## gen_params_CTs_reserves
ns10min_aero | ns10min_f | ns10min_j25 | ns10min_j15
Yes | No | Yes | Yes

## CTs_runtimes_scr
rt_limit_aero_scr | rt_limit_j25_scr | rt_limit_j15_scr | rt_limit_f_scr | rt_limit_ccj_scr
3066 | 3066 | 3066 | 3066 | 8760

## nox_limits
Area | NOx.Limit
C | 200000
F | 200000
G1 | 200000
G2 | 50000
J | 50000
K | 50000

## tech_params_aero
AREA | TECH_PARAMS | HR_SUM_AERO | HR_WIN_AERO | VOC_NG_AERO | VOC_OIL_AERO | CAP_SUM_AERO | CAP_WIN_AERO | MM_COST_AERO | STARTUP_FUEL_AERO | STARTUP_MM_AERO | NOX_NG_SUM_AERO | SO2_NG_SUM_AERO | CO2_NG_SUM_AERO | NOX_NG_WIN_AERO | SO2_NG_WIN_AERO | CO2_NG_WIN_AERO | NOX_OIL_SUM_AERO | SO2_OIL_SUM_AERO | CO2_OIL_SUM_AERO | NOX_OIL_WIN_AERO | SO2_OIL_WIN_AERO | CO2_OIL_WIN_AERO | EFORd_AERO
K | K - Long Island | 9690 | 9440 | 9.72 | 9.79 | 166.1 | 188.2 | 570 | 100 | 0 | 13.3 | 3.5 | 208800 | 12.9569 | 3.4097 | 203413.0031 | 41.7 | 2.6 | 278400 | 40.6241 | 2.5329 | 271217.3375 | 0.8997
J | J - NYC | 9690 | 9450 | 10.17 | 10.21 | 166.4 | 188.2 | 570 | 100 | 0 | 13.3 | 3.5 | 208800 | 12.9706 | 3.4133 | 203628.483 | 41.7 | 2.6 | 278400 | 40.6672 | 2.5356 | 271504.644 | 0.8997
G1 | G - LHV (Dutchess) | 9700 | 9430 | 9.85 | 9.9 | 165.9 | 188.2 | 570 | 100 | 0 | 13.3 | 3.5 | 208800 | 12.9298 | 3.4026 | 202988.0412 | 41.7 | 2.6 | 278400 | 40.5393 | 2.5276 | 270650.7216 | 0.8997
G2 | G - LHV (Rockland) | 9700 | 9440 | 9.85 | 9.9 | 165.9 | 188.2 | 570 | 100 | 0 | 13.3 | 3.5 | 208800 | 12.9435 | 3.4062 | 203203.299 | 41.7 | 2.6 | 278400 | 40.5823 | 2.5303 | 270937.732 | 0.8997
F | F - Capital | 9700 | 9430 | 9.95 | 10 | 166.3 | 188.2 | 570 | 100 | 0 | 13.3 | 3.5 | 208800 | 12.9298 | 3.4026 | 202988.0412 | 41.7 | 2.6 | 278400 | 40.5393 | 2.5276 | 270650.7216 | 0.8997
C | C - Central | 9690 | 9430 | 10.07 | 10.2 | 166.3 | 188.2 | 570 | 100 | 0 | 13.3 | 3.5 | 208800 | 12.9431 | 3.4061 | 203197.5232 | 41.7 | 2.6 | 278400 | 40.5811 | 2.5302 | 270930.031 | 0.8997

## tech_params_aero_noscr
AREA | TECH_PARAMS | HR_SUM_AERO | HR_WIN_AERO | VOC_NG_AERO | VOC_OIL_AERO | CAP_SUM_AERO | CAP_WIN_AERO | MM_COST_AERO | STARTUP_FUEL_AERO | STARTUP_MM_AERO | NOX_NG_SUM_AERO | SO2_NG_SUM_AERO | CO2_NG_SUM_AERO | NOX_NG_WIN_AERO | SO2_NG_WIN_AERO | CO2_NG_WIN_AERO | NOX_OIL_SUM_AERO | SO2_OIL_SUM_AERO | CO2_OIL_SUM_AERO | NOX_OIL_WIN_AERO | SO2_OIL_WIN_AERO | CO2_OIL_WIN_AERO | EFORd_AERO
K | K - Long Island | 9690 | 9440 | 8.89 | 8.76 | 166.1 | 188.2 | 570 | 100 | 0 | 166.8 | 3.5 | 208800 | 162.4966 | 3.4097 | 203413.0031 | 278 | 2.6 | 278400 | 270.8277 | 2.5329 | 271217.3375 | 0.8997
J | J - NYC | 9690 | 9450 | 9.34 | 9.18 | 166.4 | 188.2 | 570 | 100 | 0 | 166.8 | 3.5 | 208800 | 162.6687 | 3.4133 | 203628.483 | 278 | 2.6 | 278400 | 271.1146 | 2.5356 | 271504.644 | 0.8997
G1 | G - LHV (Dutchess) | 9700 | 9430 | 9.02 | 8.9 | 165.9 | 188.2 | 570 | 100 | 0 | 166.8 | 3.5 | 208800 | 162.1571 | 3.4026 | 202988.0412 | 278 | 2.6 | 278400 | 270.2619 | 2.5276 | 270650.7216 | 0.8997
G2 | G - LHV (Rockland) | 9700 | 9440 | 9.02 | 8.9 | 165.9 | 188.2 | 570 | 100 | 0 | 166.8 | 3.5 | 208800 | 162.3291 | 3.4062 | 203203.299 | 278 | 2.6 | 278400 | 270.5485 | 2.5303 | 270937.732 | 0.8997
F | F - Capital | 9700 | 9430 | 9.12 | 9 | 166.3 | 188.2 | 570 | 100 | 0 | 166.8 | 3.5 | 208800 | 162.1571 | 3.4026 | 202988.0412 | 278 | 2.6 | 278400 | 270.2619 | 2.5276 | 270650.7216 | 0.8997
C | C - Central | 9690 | 9430 | 9.25 | 9.2 | 166.3 | 188.2 | 570 | 100 | 0 | 166.8 | 3.5 | 208800 | 162.3245 | 3.4061 | 203197.5232 | 278 | 2.6 | 278400 | 270.5408 | 2.5302 | 270930.031 | 0.8997

## tech_params_f
AREA | TECH_PARAMS | HR_SUM_F | HR_WIN_F | VOC_NG_F | VOC_OIL_F | CAP_SUM_F | CAP_WIN_F | STARTUP_FUEL_F | STARTUP_MM_F | NOX_NG_SUM_F | SO2_NG_SUM_F | CO2_NG_SUM_F | NOX_NG_WIN_F | SO2_NG_WIN_F | CO2_NG_WIN_F | NOX_OIL_SUM_F | SO2_OIL_SUM_F | CO2_OIL_SUM_F | NOX_OIL_WIN_F | SO2_OIL_WIN_F | CO2_OIL_WIN_F | EFORd_F
K | K - Long Island | 10230 | 9880 | 1.48 | 8.79 | 216.7 | 227.7 | 325 | 9500 | 17.8 | 4.5 | 272400 | 17.191 | 4.346 | 263080.3519 | 64.5 | 3.5 | 363200 | 62.2933 | 3.3803 | 350773.8025 | 0.9566
J | J - NYC | 10220 | 9890 | 1.5 | 9.17 | 216.9 | 227.3 | 325 | 9500 | 17.8 | 4.5 | 272400 | 17.2252 | 4.3547 | 263604.3053 | 64.5 | 3.5 | 363200 | 62.4173 | 3.387 | 351472.407 | 0.9566
G1 | G - LHV (Dutchess) | 10230 | 9880 | 1.48 | 8.8 | 215.5 | 226.9 | 325 | 9500 | 17.8 | 4.5 | 270000 | 17.191 | 4.346 | 260762.4633 | 64.5 | 3.4 | 360000 | 62.2933 | 3.2837 | 347683.2845 | 0.9566
G2 | G - LHV (Rockland) | 10230 | 9880 | 1.48 | 8.8 | 215.4 | 226.8 | 325 | 9500 | 17.8 | 4.5 | 270000 | 17.191 | 4.346 | 260762.4633 | 64.5 | 3.4 | 360000 | 62.2933 | 3.2837 | 347683.2845 | 0.9566
F | F - Capital | 10220 | 9870 | 1.48 | 8.8 | 215.2 | 226.5 | 325 | 9500 | 17.8 | 4.5 | 270000 | 17.1904 | 4.3459 | 260753.4247 | 64.5 | 3.4 | 360000 | 62.2911 | 3.2836 | 347671.2329 | 0.9566
C | C - Central | 10210 | 9870 | 1.48 | 8.8 | 214.3 | 225.4 | 325 | 9500 | 17.8 | 4.5 | 271200 | 17.2072 | 4.3501 | 262168.8541 | 64.5 | 3.4 | 361600 | 62.3521 | 3.2868 | 349558.4721 | 0.9566

## tech_params_f_noscr
AREA | TECH_PARAMS | HR_SUM_F | HR_WIN_F | VOC_NG_F | VOC_OIL_F | CAP_SUM_F | CAP_WIN_F | STARTUP_FUEL_F | STARTUP_MM_F | NOX_NG_SUM_F | SO2_NG_SUM_F | CO2_NG_SUM_F | NOX_NG_WIN_F | SO2_NG_WIN_F | CO2_NG_WIN_F | NOX_OIL_SUM_F | SO2_OIL_SUM_F | CO2_OIL_SUM_F | NOX_OIL_WIN_F | SO2_OIL_WIN_F | CO2_OIL_WIN_F | EFORd_F
K | K - Long Island | 10230 | 9880 | 0.91 | 8 | 216.7 | 227.7 | 325 | 9500 | 79.9 | 4.5 | 272400 | 77.1664 | 4.346 | 263080.3519 | 430 | 3.5 | 363200 | 415.2884 | 3.3803 | 350773.8025 | 0.9566
J | J - NYC | 10220 | 9890 | 0.93 | 8.38 | 216.9 | 227.3 | 325 | 9500 | 79.9 | 4.5 | 272400 | 77.3201 | 4.3547 | 263604.3053 | 430 | 3.5 | 363200 | 416.1155 | 3.387 | 351472.407 | 0.9566
G1 | G - LHV (Dutchess) | 10230 | 9880 | 0.9 | 8 | 215.5 | 226.9 | 325 | 9500 | 79.9 | 4.5 | 270000 | 77.1664 | 4.346 | 260762.4633 | 430 | 3.4 | 360000 | 415.2884 | 3.2837 | 347683.2845 | 0.9566
G2 | G - LHV (Rockland) | 10230 | 9880 | 0.9 | 8 | 215.4 | 226.8 | 325 | 9500 | 79.9 | 4.5 | 270000 | 77.1664 | 4.346 | 260762.4633 | 430 | 3.4 | 360000 | 415.2884 | 3.2837 | 347683.2845 | 0.9566
F | F - Capital | 10220 | 9870 | 0.9 | 8 | 215.2 | 226.5 | 325 | 9500 | 79.9 | 4.5 | 270000 | 77.1637 | 4.3459 | 260753.4247 | 430 | 3.4 | 360000 | 415.274 | 3.2836 | 347671.2329 | 0.9566
C | C - Central | 10210 | 9870 | 0.9 | 8 | 214.3 | 225.4 | 325 | 9500 | 79.9 | 4.5 | 271200 | 77.2393 | 4.3501 | 262168.8541 | 430 | 3.4 | 361600 | 415.6807 | 3.2868 | 349558.4721 | 0.9566

## tech_params_j25
AREA | TECH_PARAMS | HR_SUM_J25 | HR_WIN_J25 | VOC_NG_J25 | VOC_OIL_J25 | CAP_SUM_J25 | CAP_WIN_J25 | STARTUP_FUEL_J25 | STARTUP_MM_J25 | NOX_NG_SUM_J25 | SO2_NG_SUM_J25 | CO2_NG_SUM_J25 | NOX_NG_WIN_J25 | SO2_NG_WIN_J25 | CO2_NG_WIN_J25 | NOX_OIL_SUM_J25 | SO2_OIL_SUM_J25 | CO2_OIL_SUM_J25 | NOX_OIL_WIN_J25 | SO2_OIL_WIN_J25 | CO2_OIL_WIN_J25 | EFORd_J25
K | K - Long Island | 9390 | 9290 | 1.27 | 8.8 | 357.2 | 372.2 | 490 | 16200 | 26.4 | 6.8 | 409200 | 26.1188 | 6.7276 | 404842.1725 | 96 | 5.2 | 545600 | 94.9776 | 5.1446 | 539789.5634 | 0.9566
J | J - NYC | 9380 | 9300 | 1.39 | 11.44 | 357.4 | 371.6 | 490 | 16200 | 26.4 | 6.8 | 409200 | 26.1748 | 6.742 | 405710.0213 | 96 | 5.2 | 545600 | 95.1812 | 5.1557 | 540946.6951 | 0.9566
G1 | G - LHV (Dutchess) | 9390 | 9280 | 1.27 | 8.8 | 355.1 | 370.8 | 490 | 16200 | 26.4 | 6.8 | 406800 | 26.0907 | 6.7203 | 402034.5048 | 96 | 5.2 | 542400 | 94.8754 | 5.1391 | 536046.0064 | 0.9566
G2 | G - LHV (Rockland) | 9390 | 9290 | 1.27 | 8.8 | 355 | 370.7 | 490 | 16200 | 26.4 | 6.8 | 406800 | 26.1188 | 6.7276 | 402467.7316 | 96 | 5.2 | 542400 | 94.9776 | 5.1446 | 536623.6422 | 0.9566
F | F - Capital | 9380 | 9270 | 1.27 | 8.8 | 354.3 | 369.9 | 490 | 16200 | 26.4 | 6.8 | 405600 | 26.0904 | 6.7203 | 400843.4968 | 96 | 5.1 | 540800 | 94.8742 | 5.0402 | 534457.9957 | 0.9566
C | C - Central | 9380 | 9270 | 1.37 | 8.8 | 352.8 | 368.1 | 490 | 16200 | 26.4 | 6.8 | 408000 | 26.0904 | 6.7203 | 403215.3518 | 96 | 5.2 | 544000 | 94.8742 | 5.139 | 537620.4691 | 0.9566

## tech_params_j25_noscr
AREA | TECH_PARAMS | HR_SUM_J25 | HR_WIN_J25 | VOC_NG_J25 | VOC_OIL_J25 | CAP_SUM_J25 | CAP_WIN_J25 | STARTUP_FUEL_J25 | STARTUP_MM_J25 | NOX_NG_SUM_J25 | SO2_NG_SUM_J25 | CO2_NG_SUM_J25 | NOX_NG_WIN_J25 | SO2_NG_WIN_J25 | CO2_NG_WIN_J25 | NOX_OIL_SUM_J25 | SO2_OIL_SUM_J25 | CO2_OIL_SUM_J25 | NOX_OIL_WIN_J25 | SO2_OIL_WIN_J25 | CO2_OIL_WIN_J25 | EFORd_J25
K | K - Long Island | 9390 | 9290 | 0.9 | 8 | 357.2 | 372.2 | 490 | 16200 | 330.5 | 6.8 | 409200 | 326.9803 | 6.7276 | 404842.1725 | 640 | 5.2 | 545600 | 633.1842 | 5.1446 | 539789.5634 | 0.9566
J | J - NYC | 9380 | 9300 | 0.91 | 10.74 | 357.4 | 371.6 | 490 | 16200 | 330.5 | 6.8 | 409200 | 327.6812 | 6.742 | 405710.0213 | 640 | 5.2 | 545600 | 634.5416 | 5.1557 | 540946.6951 | 0.9566
G1 | G - LHV (Dutchess) | 9390 | 9280 | 0.9 | 8 | 355.1 | 370.8 | 490 | 16200 | 330.5 | 6.8 | 406800 | 326.6283 | 6.7203 | 402034.5048 | 640 | 5.2 | 542400 | 632.5027 | 5.1391 | 536046.0064 | 0.9566
G2 | G - LHV (Rockland) | 9390 | 9290 | 0.9 | 8 | 355 | 370.7 | 490 | 16200 | 330.5 | 6.8 | 406800 | 326.9803 | 6.7276 | 402467.7316 | 640 | 5.2 | 542400 | 633.1842 | 5.1446 | 536623.6422 | 0.9566
F | F - Capital | 9380 | 9270 | 0.9 | 8 | 354.3 | 369.9 | 490 | 16200 | 330.5 | 6.8 | 405600 | 326.6242 | 6.7203 | 400843.4968 | 640 | 5.1 | 540800 | 632.4947 | 5.0402 | 534457.9957 | 0.9566
C | C - Central | 9380 | 9270 | 0.9 | 8 | 352.8 | 368.1 | 490 | 16200 | 330.5 | 6.8 | 408000 | 326.6242 | 6.7203 | 403215.3518 | 640 | 5.2 | 544000 | 632.4947 | 5.139 | 537620.4691 | 0.9566

## tech_params_j15
AREA | TECH_PARAMS | HR_SUM_J15 | HR_WIN_J15 | VOC_NG_J15 | VOC_OIL_J15 | CAP_SUM_J15 | CAP_WIN_J15 | STARTUP_FUEL_J15 | STARTUP_MM_J15 | NOX_NG_SUM_J15 | SO2_NG_SUM_J15 | CO2_NG_SUM_J15 | NOX_NG_WIN_J15 | SO2_NG_WIN_J15 | CO2_NG_WIN_J15 | NOX_OIL_SUM_J15 | SO2_OIL_SUM_J15 | CO2_OIL_SUM_J15 | NOX_OIL_WIN_J15 | SO2_OIL_WIN_J15 | CO2_OIL_WIN_J15 | EFORd_J15
G1 | G - LHV (Dutchess) | 9400 | 9310 | 0.9 | 10.2 | 337.4 | 349.2 | 490 | 16200 | 26.4 | 6.4 | 385200 | 26.1472 | 6.3387 | 381511.9149 | 96 | 4.9 | 513600 | 95.0809 | 4.8531 | 508682.5532 | 0.9566
F | F - Capital | 9270 | 9180 | 0.9 | 10.2 | 336.7 | 348.4 | 490 | 16200 | 26.4 | 6.3 | 379200 | 26.1437 | 6.2388 | 375518.4466 | 96 | 4.8 | 505600 | 95.068 | 4.7534 | 500691.2621 | 0.9566
C | C - Central | 9400 | 9310 | 0.9 | 10.2 | 335.3 | 346.7 | 490 | 16200 | 26.4 | 6.4 | 381600 | 26.1472 | 6.3387 | 377946.383 | 96 | 4.8 | 508800 | 95.0809 | 4.754 | 503928.5106 | 0.9566

## tech_params_j15_noscr
AREA | TECH_PARAMS | HR_SUM_J15 | HR_WIN_J15 | VOC_NG_J15 | VOC_OIL_J15 | CAP_SUM_J15 | CAP_WIN_J15 | STARTUP_FUEL_J15 | STARTUP_MM_J15 | NOX_NG_SUM_J15 | SO2_NG_SUM_J15 | CO2_NG_SUM_J15 | NOX_NG_WIN_J15 | SO2_NG_WIN_J15 | CO2_NG_WIN_J15 | NOX_OIL_SUM_J15 | SO2_OIL_SUM_J15 | CO2_OIL_SUM_J15 | NOX_OIL_WIN_J15 | SO2_OIL_WIN_J15 | CO2_OIL_WIN_J15 | EFORd_J15
G1 | G - LHV (Dutchess) | 9400 | 9310 | 0.9 | 10.2 | 337.4 | 349.2 | 490 | 16200 | 188.6 | 6.4 | 385200 | 186.7943 | 6.3387 | 381511.9149 | 640 | 4.9 | 513600 | 633.8723 | 4.8531 | 508682.5532 | 0.9566
F | F - Capital | 9270 | 9180 | 0.9 | 10.2 | 336.7 | 348.4 | 490 | 16200 | 188.6 | 6.3 | 379200 | 186.7689 | 6.2388 | 375518.4466 | 640 | 4.8 | 505600 | 633.7864 | 4.7534 | 500691.2621 | 0.9566
C | C - Central | 9400 | 9310 | 0.9 | 10.2 | 335.3 | 346.7 | 490 | 16200 | 188.6 | 6.4 | 381600 | 186.7943 | 6.3387 | 377946.383 | 640 | 4.8 | 508800 | 633.8723 | 4.754 | 503928.5106 | 0.9566

## tech_params_ccj
AREA | TECH_PARAMS | HR_SUM_CCJ | HR_WIN_CCJ | VOC_NG_CCJ | VOC_OIL_CCJ | CAP_SUM_CCJ | CAP_WIN_CCJ | STARTUP_FUEL_CCJ | STARTUP_MM_CCJ | NOX_NG_SUM_CCJ | SO2_NG_SUM_CCJ | CO2_NG_SUM_CCJ | NOX_NG_WIN_CCJ | SO2_NG_WIN_CCJ | CO2_NG_WIN_CCJ | NOX_OIL_SUM_CCJ | SO2_OIL_SUM_CCJ | CO2_OIL_SUM_CCJ | NOX_OIL_WIN_CCJ | SO2_OIL_WIN_CCJ | CO2_OIL_WIN_CCJ | EFORd_CCJ | HR_SUM_MIN_CCJ | HR_WIN_MIN_CCJ | CAP_SUM_MIN_CCJ | CAP_WIN_MIN_CCJ
K | K - Long Island | 6370 | 6340 | 1.54 | 1.73 | 517.9 | 547.8 | 3490 | 16200 | 26.4 | 6.8 | 406800 | 26.2757 | 6.768 | 404884.1444 | 96 | 5.2 | 545600 | 95.5479 | 5.1755 | 543030.4553 | 0.9708 | 7130 | 7540 | 235.7 | 199.5
J | J - NYC | 6370 | 6350 | 1.57 | 2.09 | 512.3 | 546.7 | 3490 | 16200 | 26.4 | 6.8 | 406800 | 26.3171 | 6.7786 | 405522.763 | 96 | 5.2 | 545600 | 95.6986 | 5.1837 | 543886.9702 | 0.9708 | 7180 | 7530 | 232.3 | 199.3
G1 | G - LHV (Dutchess) | 6360 | 6350 | 1.55 | 1.7 | 514.7 | 544.8 | 3490 | 16200 | 26.4 | 6.7 | 404400 | 26.3585 | 6.6895 | 403764.1509 | 96 | 5.2 | 542400 | 95.8491 | 5.1918 | 541547.1698 | 0.9708 | 7130 | 7550 | 234 | 198.7
G2 | G - LHV (Rockland) | 6360 | 6350 | 1.55 | 1.7 | 514.7 | 544.8 | 3490 | 16200 | 26.4 | 6.7 | 404400 | 26.3585 | 6.6895 | 403764.1509 | 96 | 5.2 | 542400 | 95.8491 | 5.1918 | 541547.1698 | 0.9708 | 7130 | 7550 | 234 | 198.7
F | F - Capital | 6360 | 6360 | 1.55 | 1.7 | 513.3 | 542.1 | 3490 | 16200 | 26.4 | 6.7 | 403200 | 26.4 | 6.7 | 403200 | 96 | 5.1 | 540800 | 96 | 5.1 | 540800 | 0.9708 | 7130 | 7560 | 233.4 | 198
C | C - Central | 6370 | 6360 | 1.55 | 1.7 | 509.9 | 539.2 | 3490 | 16200 | 26.4 | 6.6 | 393600 | 26.3586 | 6.5896 | 392982.1036 | 96 | 5.2 | 544000 | 95.8493 | 5.1918 | 543145.9969 | 0.9708 | 7130 | 7570 | 232.1 | 197

## Aero_NoSCR_Filtered
[6 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[6 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_Aeroderivative |  |  |  |  | Simple Cycle Aeroderivative Siemens 3x SGT-A65 (No SCR)
|  |  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable |  | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW |  | Summer | MW | 166.1 | 166.4 | 165.9 | 165.9 | 166.3 | 166.3
44 | 52 | Net Plant Output, kW |  | Winter | MW | 188.2 | 188.2 | 188.2 | 188.2 | 188.2 | 188.2
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Summer | Btu/kWh | 9690 | 9690 | 9700 | 9700 | 9700 | 9690
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Winter | Btu/kWh | 9440 | 9450 | 9430 | 9440 | 9430 | 9430
Natural Gas Emission Rates - Summer
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 166.8 | 166.8 | 166.8 | 166.8 | 166.8 | 166.8
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 208800 | 208800 | 208800 | 208800 | 208800 | 208800
Natural Gas Emission Rates - Winter
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 162.4966 | 162.6687 | 162.1571 | 162.3291 | 162.1571 | 162.3245
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 3.4097 | 3.4133 | 3.4026 | 3.4062 | 3.4026 | 3.4061
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 203413.0031 | 203628.483 | 202988.0412 | 203203.299 | 202988.0412 | 203197.5232
ULSD Emission Rates - Summer
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 278 | 278 | 278 | 278 | 278 | 278
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 278400 | 278400 | 278400 | 278400 | 278400 | 278400
ULSD Emission Rates - Winter
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 270.8277 | 271.1146 | 270.2619 | 270.5485 | 270.2619 | 270.5408
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 2.5329 | 2.5356 | 2.5276 | 2.5303 | 2.5276 | 2.5302
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 271217.3375 | 271504.644 | 270650.7216 | 270937.732 | 270650.7216 | 270930.031
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  |  | Fuel Required per Start (regular start - 21 min. to full load) | MMBtu/Start | 100 | 100 | 100 | 100 | 100 | 100
16 | 16 | Equivalent Forced Outage Rate Demand, % |  | EFORd outage rate | % | 10.03% | 10.03% | 10.03% | 10.03% | 10.03% | 10.03%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 8.89 | 9.34 | 9.02 | 9.02 | 9.12 | 9.25
190 | 193 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 8.76 | 9.18 | 8.9 | 8.9 | 9 | 9.2
177 | 180 | Major Maintenance Cost, 2020$/GT-hr or $/engine-hr |  | Maj. Maintenace per Hour | $/hr | 570 | 570 | 570 | 570 | 570 | 570
177 | 180 | Major Maintenance Cost, 2020$/GT-start |  | Maj. Maintenance per Start | $/Start | N/A | N/A | N/A | N/A | N/A | N/A
Updated 5/8/2020

## Aero_SCR_Filtered
[5 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[5 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_Aeroderivative |  |  |  | Simple Cycle Aeroderivative Siemens 3x SGT-A65 (with SCR)
|  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW | Summer | MW | 166.1 | 166.4 | 165.9 | 165.9 | 166.3 | 166.3
44 | 52 | Net Plant Output, kW | Winter | MW | 188.2 | 188.2 | 188.2 | 188.2 | 188.2 | 188.2
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Summer | Btu/kWh | 9690 | 9690 | 9700 | 9700 | 9700 | 9690
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Winter | Btu/kWh | 9440 | 9450 | 9430 | 9440 | 9430 | 9430
Natural Gas Emission Rates - Summer
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 13.3 | 13.3 | 13.3 | 13.3 | 13.3 | 13.3
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 208800 | 208800 | 208800 | 208800 | 208800 | 208800
Natural Gas Emission Rates - Winter
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 12.9569 | 12.9706 | 12.9298 | 12.9435 | 12.9298 | 12.9431
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 3.4097 | 3.4133 | 3.4026 | 3.4062 | 3.4026 | 3.4061
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 203413.0031 | 203628.483 | 202988.0412 | 203203.299 | 202988.0412 | 203197.5232
ULSD Emission Rates - Summer
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 41.7 | 41.7 | 41.7 | 41.7 | 41.7 | 41.7
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 278400 | 278400 | 278400 | 278400 | 278400 | 278400
ULSD Emission Rates - Winter
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 40.6241 | 40.6672 | 40.5393 | 40.5823 | 40.5393 | 40.5811
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 2.5329 | 2.5356 | 2.5276 | 2.5303 | 2.5276 | 2.5302
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 271217.3375 | 271504.644 | 270650.7216 | 270937.732 | 270650.7216 | 270930.031
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 21 min. to full load) | MMBtu/Start | 100 | 100 | 100 | 100 | 100 | 100
16 | 16 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 10.03% | 10.03% | 10.03% | 10.03% | 10.03% | 10.03%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - NG Firing | $/MWh | 9.72 | 10.17 | 9.85 | 9.85 | 9.95 | 10.07
190 | 193 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 9.79 | 10.21 | 9.9 | 9.9 | 10 | 10.2
177 | 180 | Major Maintenance Cost, 2020$/GT-hr or $/engine-hr | Maj. Maintennace per Hour | $/hr | 570 | 570 | 570 | 570 | 570 | 570
177 | 180 | Major Maintenance Cost, 2020$/GT-start | Maj. Maintenance per Start | $/Start | N/A | N/A | N/A | N/A | N/A | N/A
Updated 5/8/2020

## F-Class_NoSCR_Filtered
[6 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[6 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_F-Class |  |  |  |  | Simple Cycle Frame F-Class: GE 1x 7F.05 (No SCR)
|  |  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable 1 | Variable 2 | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW |  | Summer | MW | 216.7 | 216.9 | 215.5 | 215.4 | 215.2 | 214.3
44 | 52 | Net Plant Output, kW |  | Winter | MW | 227.7 | 227.3 | 226.9 | 226.8 | 226.5 | 225.4
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Summer | Btu/kWh | 10230 | 10220 | 10230 | 10230 | 10220 | 10210
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Winter | Btu/kWh | 9880 | 9890 | 9880 | 9880 | 9870 | 9870
Natural Gas Emission Rates - Summer
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 272400 | 272400 | 270000 | 270000 | 270000 | 271200
Natural Gas Emission Rates - Winter
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 77.1664 | 77.3201 | 77.1664 | 77.1664 | 77.1637 | 77.2393
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 4.346 | 4.3547 | 4.346 | 4.346 | 4.3459 | 4.3501
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 263080.3519 | 263604.3053 | 260762.4633 | 260762.4633 | 260753.4247 | 262168.8541
ULSD Emission Rates - Summer
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 430 | 430 | 430 | 430 | 430 | 430
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 3.5 | 3.5 | 3.4 | 3.4 | 3.4 | 3.4
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 363200 | 363200 | 360000 | 360000 | 360000 | 361600
ULSD Emission Rates - Winter
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 415.2884 | 416.1155 | 415.2884 | 415.2884 | 415.274 | 415.6807
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 3.3803 | 3.387 | 3.2837 | 3.2837 | 3.2836 | 3.2868
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 350773.8025 | 351472.407 | 347683.2845 | 347683.2845 | 347671.2329 | 349558.4721
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 325 | 325 | 325 | 325 | 325 | 325
16 | 16 | Equivalent Forced Outage Rate Demand, % |  | EFORd outage rate | % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Fixed and Variable O&M Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 0.91 | 0.93 | 0.9 | 0.9 | 0.9 | 0.9
190 | 193 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 8 | 8.38 | 8 | 8 | 8 | 8
177 | 180 | Major Maintenance Cost, 2020$/GT-start |  | Variable Cost per Start | $/Start | 9500 | 9500 | 9500 | 9500 | 9500 | 9500
Updated 4/2/2020

## F-Class_SCR_Filtered
[5 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[5 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_F-Class |  |  |  | Simple Cycle Frame F-Class: GE 1x 7F.05
|  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW | Summer | MW | 216.7 | 216.9 | 215.5 | 215.4 | 215.2 | 214.3
44 | 52 | Net Plant Output, kW | Winter | MW | 227.7 | 227.3 | 226.9 | 226.8 | 226.5 | 225.4
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Summer | Btu/kWh | 10230 | 10220 | 10230 | 10230 | 10220 | 10210
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Winter | Btu/kWh | 9880 | 9890 | 9880 | 9880 | 9870 | 9870
Natural Gas Emission Rates - Summer
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 272400 | 272400 | 270000 | 270000 | 270000 | 271200
Natural Gas Emission Rates - Winter
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 17.191 | 17.2252 | 17.191 | 17.191 | 17.1904 | 17.2072
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 4.346 | 4.3547 | 4.346 | 4.346 | 4.3459 | 4.3501
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 263080.3519 | 263604.3053 | 260762.4633 | 260762.4633 | 260753.4247 | 262168.8541
ULSD Emission Rates - Summer
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 64.5 | 64.5 | 64.5 | 64.5 | 64.5 | 64.5
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 3.5 | 3.5 | 3.4 | 3.4 | 3.4 | 3.4
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 363200 | 363200 | 360000 | 360000 | 360000 | 361600
ULSD Emission Rates - Winter
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 62.2933 | 62.4173 | 62.2933 | 62.2933 | 62.2911 | 62.3521
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 3.3803 | 3.387 | 3.2837 | 3.2837 | 3.2836 | 3.2868
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 350773.8025 | 351472.407 | 347683.2845 | 347683.2845 | 347671.2329 | 349558.4721
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 325 | 325 | 325 | 325 | 325 | 325
16 | 16 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Fixed and Variable O&M Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - NG Firing | $/MWh | 1.48 | 1.5 | 1.48 | 1.48 | 1.48 | 1.48
190 | 193 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 8.79 | 9.17 | 8.8 | 8.8 | 8.8 | 8.8
177 | 180 | Major Maintenance Cost, 2020$/GT-start | Variable Cost per Start | $/Start | 9500 | 9500 | 9500 | 9500 | 9500 | 9500
Updated 4/2/2020

## J-Class25ppm_NoSCR_Filtered
[6 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[6 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_J-Class25ppm |  |  |  |  | Simple Cycle Frame J-Class GE 1x HA.02 (25ppm) (No SCR)
|  |  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable |  | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW |  | Summer | MW | 357.2 | 357.4 | 355.1 | 355 | 354.3 | 352.8
44 | 52 | Net Plant Output, kW |  | Winter | MW | 372.2 | 371.6 | 370.8 | 370.7 | 369.9 | 368.1
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Summer | Btu/kWh | 9390 | 9380 | 9390 | 9390 | 9380 | 9380
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Winter | Btu/kWh | 9290 | 9300 | 9280 | 9290 | 9270 | 9270
Natural Gas Emission Rates - Summer
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 330.5 | 330.5 | 330.5 | 330.5 | 330.5 | 330.5
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 409200 | 409200 | 406800 | 406800 | 405600 | 408000
Natural Gas Emission Rates - Winter
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 326.9803 | 327.6812 | 326.6283 | 326.9803 | 326.6242 | 326.6242
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 6.7276 | 6.742 | 6.7203 | 6.7276 | 6.7203 | 6.7203
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 404842.1725 | 405710.0213 | 402034.5048 | 402467.7316 | 400843.4968 | 403215.3518
ULSD Emission Rates - Summer
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 640 | 640 | 640 | 640 | 640 | 640
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 5.2 | 5.2 | 5.2 | 5.2 | 5.1 | 5.2
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 545600 | 545600 | 542400 | 542400 | 540800 | 544000
ULSD Emission Rates - Winter
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 633.1842 | 634.5416 | 632.5027 | 633.1842 | 632.4947 | 632.4947
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 5.1446 | 5.1557 | 5.1391 | 5.1446 | 5.0402 | 5.139
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 539789.5634 | 540946.6951 | 536046.0064 | 536623.6422 | 534457.9957 | 537620.4691
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 490 | 490 | 490 | 490 | 490 | 490
16 | 16 | Equivalent Forced Outage Rate Demand, % |  | EFORd outage rate | % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Fixed and Variable O&M Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 0.9 | 0.91 | 0.9 | 0.9 | 0.9 | 0.9
190 | 193 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 8 | 10.74 | 8 | 8 | 8 | 8
177 | 180 | Major Maintenance Cost, 2020$/GT-start |  | Variable Cost per Start | $/Start | 16200 | 16200 | 16200 | 16200 | 16200 | 16200
Updated 4/2/2020

## J-Class25ppm_SCR_Filtered
[5 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[5 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_J-Class25ppm |  |  |  | Simple Cycle Frame J-Class GE 1x HA.02 (25 ppm)
|  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW | Summer | MW | 357.2 | 357.4 | 355.1 | 355 | 354.3 | 352.8
44 | 52 | Net Plant Output, kW | Winter | MW | 372.2 | 371.6 | 370.8 | 370.7 | 369.9 | 368.1
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Summer | Btu/kWh | 9390 | 9380 | 9390 | 9390 | 9380 | 9380
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Winter | Btu/kWh | 9290 | 9300 | 9280 | 9290 | 9270 | 9270
Natural Gas Emission Rates - Summer
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 26.4 | 26.4 | 26.4 | 26.4 | 26.4 | 26.4
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 409200 | 409200 | 406800 | 406800 | 405600 | 408000
Natural Gas Emission Rates - Winter
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 26.1188 | 26.1748 | 26.0907 | 26.1188 | 26.0904 | 26.0904
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 6.7276 | 6.742 | 6.7203 | 6.7276 | 6.7203 | 6.7203
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 404842.1725 | 405710.0213 | 402034.5048 | 402467.7316 | 400843.4968 | 403215.3518
ULSD Emission Rates - Summer
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 96 | 96 | 96 | 96 | 96 | 96
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 5.2 | 5.2 | 5.2 | 5.2 | 5.1 | 5.2
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 545600 | 545600 | 542400 | 542400 | 540800 | 544000
ULSD Emission Rates - Winter
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 94.9776 | 95.1812 | 94.8754 | 94.9776 | 94.8742 | 94.8742
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 5.1446 | 5.1557 | 5.1391 | 5.1446 | 5.0402 | 5.139
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 539789.5634 | 540946.6951 | 536046.0064 | 536623.6422 | 534457.9957 | 537620.4691
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 490 | 490 | 490 | 490 | 490 | 490
16 | 16 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Fixed and Variable O&M Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - NG Firing | $/MWh | 1.27 | 1.39 | 1.27 | 1.27 | 1.27 | 1.37
190 | 193 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 8.8 | 11.44 | 8.8 | 8.8 | 8.8 | 8.8
177 | 180 | Major Maintenance Cost, 2020$/GT-start | Variable Cost per Start | $/Start | 16200 | 16200 | 16200 | 16200 | 16200 | 16200
Updated 4/2/2020

## J-Class15ppm_NoSCR_Filtered
[6 empty] | ZONE G - Dutchess | ZONE F | ZONE C
[6 empty] | 4 | 3 | 2
Sheet | Raw_J-Class15ppm |  |  |  |  | Simple Cycle Frame J-Class GE 1x HA.02 (15 ppm) (No SCR)
|  |  |  | Item | Units | G - LHV (Dutchess) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable |  | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW |  | Summer | MW | 337.4 | 336.7 | 335.3
44 | 52 | Net Plant Output, kW |  | Winter | MW | 349.2 | 348.4 | 346.7
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Summer | Btu/kWh | 9400 | 9270 | 9400
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Winter | Btu/kWh | 9310 | 9180 | 9310
Natural Gas Emission Rates - Summer
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 188.6 | 188.6 | 188.6
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 6.4 | 6.3 | 6.4
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 385200 | 379200 | 381600
Natural Gas Emission Rates - Winter
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 186.7943 | 186.7689 | 186.7943
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 6.3387 | 6.2388 | 6.3387
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 381511.9149 | 375518.4466 | 377946.383
ULSD Emission Rates - Summer
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 640 | 640 | 640
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 4.9 | 4.8 | 4.8
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 513600 | 505600 | 508800
ULSD Emission Rates - Winter
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 633.8723 | 633.7864 | 633.8723
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 4.8531 | 4.7534 | 4.754
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 508682.5532 | 500691.2621 | 503928.5106
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 490 | 490 | 490
16 | 16 | Equivalent Forced Outage Rate Demand, % |  | EFORd outage rate | % | 4.34% | 4.34% | 4.34%
Fixed and Variable O&M Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 0.9 | 0.9 | 0.9
190 | 193 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 10.2 | 10.2 | 10.2
177 | 180 | Major Maintenance Cost, 2020$/GT-start |  | Variable Cost per Start | $/Start | 16200 | 16200 | 16200
Updated 4/2/2020

## J-Class15ppm_SCR_Filtered
[5 empty] | ZONE G - Dutchess | ZONE F | ZONE C
[5 empty] | 4 | 3 | 2
Sheet | Raw_J-Class15ppm |  |  |  | Simple Cycle Frame J-Class GE 1x HA.02 (15 ppm)
|  |  | Item | Units | G - LHV (Dutchess) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW | Summer | MW | 337.4 | 336.7 | 335.3
44 | 52 | Net Plant Output, kW | Winter | MW | 349.2 | 348.4 | 346.7
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Summer | Btu/kWh | 9400 | 9270 | 9400
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Winter | Btu/kWh | 9310 | 9180 | 9310
Natural Gas Emission Rates - Summer
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 26.4 | 26.4 | 26.4
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 6.4 | 6.3 | 6.4
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 385200 | 379200 | 381600
Natural Gas Emission Rates - Winter
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 26.1472 | 26.1437 | 26.1472
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 6.3387 | 6.2388 | 6.3387
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 381511.9149 | 375518.4466 | 377946.383
ULSD Emission Rates - Summer
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 96 | 96 | 96
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 4.9 | 4.8 | 4.8
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 513600 | 505600 | 508800
ULSD Emission Rates - Winter
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 95.0809 | 95.068 | 95.0809
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 4.8531 | 4.7534 | 4.754
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 508682.5532 | 500691.2621 | 503928.5106
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 490 | 490 | 490
16 | 16 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 4.34% | 4.34% | 4.34%
Fixed and Variable O&M Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - NG Firing | $/MWh | 0.9 | 0.9 | 0.9
190 | 193 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 10.2 | 10.2 | 10.2
177 | 180 | Major Maintenance Cost, 2020$/GT-start | Variable Cost per Start | $/Start | 16200 | 16200 | 16200
Updated 4/2/2020

## J-Class_CC_Filtered
[5 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[5 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_J-Class_CC |  |  |  | Combined Cycle J-Class Frame 1x1 GE HA.02
|  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
102 | 105 | Net Plant Output, kW | Summer | MW | 517.9 | 512.3 | 514.7 | 514.7 | 513.3 | 509.9
68 | 71 | Net Plant Output, kW | Winter | MW | 547.8 | 546.7 | 544.8 | 544.8 | 542.1 | 539.2
Net Plant Output (MECL)
112 | 115 | Net Plant Output, kW | Summer | MW | 235.7 | 232.3 | 234 | 234 | 233.4 | 232.1
78 | 81 | Net Plant Output, kW | Winter | MW | 199.5 | 199.3 | 198.7 | 198.7 | 198 | 197
Net Plant Heat Rate (HHV)
102 | 105 | Net Plant Heat Rate, Btu/kWh (HHV) | Summer | Btu/kWh | 6370 | 6370 | 6360 | 6360 | 6360 | 6370
68 | 71 | Net Plant Heat Rate, Btu/kWh (HHV) | Winter | Btu/kWh | 6340 | 6350 | 6350 | 6350 | 6360 | 6360
Net Plant Heat Rate (HHV) (MECL)
112 | 115 | Net Plant Heat Rate, Btu/kWh (HHV) | Summer | Btu/kWh | 7130 | 7180 | 7130 | 7130 | 7130 | 7130
78 | 81 | Net Plant Heat Rate, Btu/kWh (HHV) | Winter | Btu/kWh | 7540 | 7530 | 7550 | 7550 | 7560 | 7570
Natural Gas Emission Rates - Summer
240 | 243 | NOX | NOX Emissions Rate | lb/hr | 26.4 | 26.4 | 26.4 | 26.4 | 26.4 | 26.4
240 | 243 | SO2 | SO2 Emissions Rate | lb/hr | 6.8 | 6.8 | 6.7 | 6.7 | 6.7 | 6.6
240 | 243 | CO2 | CO2 Emissions Rate | lb/hr | 406800 | 406800 | 404400 | 404400 | 403200 | 393600
Natural Gas Emission Rates - Winter
240 | 243 | NOX | NOX Emissions Rate | lb/hr | 26.2757 | 26.3171 | 26.3585 | 26.3585 | 26.4 | 26.3586
240 | 243 | SO2 | SO2 Emissions Rate | lb/hr | 6.768 | 6.7786 | 6.6895 | 6.6895 | 6.7 | 6.5896
240 | 243 | CO2 | CO2 Emissions Rate | lb/hr | 404884.1444 | 405522.763 | 403764.1509 | 403764.1509 | 403200 | 392982.1036
ULSD Emission Rates - Summer
247 | 250 | NOX | NOX Emissions Rate | lb/hr | 96 | 96 | 96 | 96 | 96 | 96
247 | 250 | SO2 | SO2 Emissions Rate | lb/hr | 5.2 | 5.2 | 5.2 | 5.2 | 5.1 | 5.2
247 | 250 | CO2 | CO2 Emissions Rate | lb/hr | 545600 | 545600 | 542400 | 542400 | 540800 | 544000
ULSD Emission Rates - Winter
247 | 250 | NOX | NOX Emissions Rate | lb/hr | 95.5479 | 95.6986 | 95.8491 | 95.8491 | 96 | 95.8493
247 | 250 | SO2 | SO2 Emissions Rate | lb/hr | 5.1755 | 5.1837 | 5.1918 | 5.1918 | 5.1 | 5.1918
247 | 250 | CO2 | CO2 Emissions Rate | lb/hr | 543030.4553 | 543886.9702 | 541547.1698 | 541547.1698 | 540800 | 543145.9969
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 3490 | 3490 | 3490 | 3490 | 3490 | 3490
23 | 23 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 2.92% | 2.92% | 2.92% | 2.92% | 2.92% | 2.92%
Fixed and Variable O&M Costs (per unit)
213 | 216 | Total Variable O&M Cost, 2020 $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 1.54 | 1.57 | 1.55 | 1.55 | 1.55 | 1.55
224 | 227 | Total Variable O&M Cost, 2020 $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 1.73 | 2.09 | 1.7 | 1.7 | 1.7 | 1.7
206 | 209 | Major Maintenance Cost, 2020$/GT-start | Variable Cost per Start | $/Start | 16200 | 16200 | 16200 | 16200 | 16200 | 16200
Updated 4/2/2020

## Raw_Aeroderivative
NYISO DCR TECHNOLOGY ASSESSMENT
SIMPLE CYCLE AERODERIVATIVE SIEMENS SGT-A65
PRELIMINARY AND CONFIDENTIAL - NOT FOR CONSTRUCTION
Mar 2020 - DRAFT REV 2
PROJECT TYPE | ZONE C | ZONE F | ZONE G - Dutchess | ZONE G - Rockland | ZONE J | ZONE K
BASE PLANT DESCRIPTION
Number of Gas Turbines | 3 | 3 | 3 | 3 | 3 | 3
Representative Class Gas Turbine | Siemens SGT-A65 WLE | Siemens SGT-A65 WLE | Siemens SGT-A65 WLE | Siemens SGT-A65 WLE | Siemens SGT-A65 WLE | Siemens SGT-A65 WLE
Startup Time to Base Load, min | 5 | 5 | 5 | 5 | 5 | 5
Startup Time to MECL, min | 4 | 4 | 4 | 4 | 4 | 4
Cold Startup Time to SCR Compliance, min | 45 | 45 | 45 | 45 | 45 | 45
Equivalent Forced Outage Rate Demand, % | 10.03% | 10.03% | 10.03% | 10.03% | 10.03% | 10.03%
Assumed Land Use During Operation, Acres (Not Construction Land Use) | 15 | 15 | 15 | 15 | 15 | 15
Fuel Design | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil)
Inlet Conditioning | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler
Heat Rejection | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger
NOx Control | Water Injection and SCR | Water Injection and SCR | Water Injection and SCR | Water Injection and SCR | Water Injection and SCR | Water Injection and SCR
CO Control | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst
Particulate Control | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice
Interconnection Voltage, kV | 345 | 345 | 345 | 345 | 345 | 138
Technology Rating | Mature | Mature | Mature | Mature | Mature | Mature
Permitting & Construction Schedule (Years from FNTP) | 3 | 3 | 3 | 3 | 3 | 3
ESTIMATED PERFORMANCE (All BASED ON NATURAL GAS OPERATION)
Summer Performance
Ambient Temperature, °F | 77.7 | 78.1 | 78.9 | 79.9 | 81.1 | 78
Relative Humidity, % | 46.9% | 48% | 51% | 48.2% | 41.2% | 52.7%
Net Plant Output, kW | 166300 | 166300 | 165900 | 165900 | 166400 | 166100
Net Plant Heat Rate, Btu/kWh (HHV) | 9690 | 9700 | 9700 | 9700 | 9690 | 9690
Heat Input, MMBtu/h (HHV) | 1610 | 1610 | 1610 | 1610 | 1610 | 1610
Min Load Plant Output, kW | 22100 | 22100 | 22000 | 21900 | 21900 | 22100
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12040 | 12040 | 12050 | 12070 | 12090 | 12030
Min LoadHeat Input, MMBtu/h (HHV) | 270 | 270 | 270 | 260 | 260 | 270
Winter Performance
Ambient Temperature, °F | 28.4 | 29.2 | 32.6 | 33.2 | 38.1 | 35.9
Relative Humidity, % | 72.8% | 68.3% | 66.9% | 65.4% | 55% | 62.2%
Net Plant Output, kW | 188200 | 188200 | 188200 | 188200 | 188200 | 188200
Net Plant Heat Rate, Btu/kWh (HHV) | 9430 | 9430 | 9430 | 9440 | 9450 | 9440
Heat Input, MMBtu/h (HHV) | 1770 | 1770 | 1770 | 1780 | 1780 | 1780
Min Load Plant Output, kW | 25700 | 25700 | 25700 | 25700 | 25700 | 25700
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 11540 | 11540 | 11540 | 11540 | 11550 | 11550
Min LoadHeat Input, MMBtu/h (HHV) | 300 | 300 | 300 | 300 | 300 | 300
Spring-Fall (ISO) Performance
Ambient Temperature, °F | 59 | 59 | 59 | 59 | 59 | 59
Relative Humidity, % | 60% | 60% | 60% | 60% | 60% | 60%
Net Plant Output, kW | 184700 | 184700 | 184800 | 184800 | 184900 | 184900
Net Plant Heat Rate, Btu/kWh (HHV) | 9430 | 9430 | 9430 | 9430 | 9420 | 9420
Heat Input, MMBtu/h (HHV) | 1740 | 1740 | 1740 | 1740 | 1740 | 1740
Min Load Plant Output, kW | 25300 | 25300 | 25300 | 25300 | 25300 | 25300
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 11630 | 11620 | 11620 | 11620 | 11620 | 11620
Min LoadHeat Input, MMBtu/h (HHV) | 290 | 290 | 290 | 290 | 290 | 290
Summer DMNC Performance
Ambient Temperature, °F | 91.6 | 92.3 | 91.2 | 93.7 | 95.1 | 88.6
Relative Humidity, % | 34.2% | 35.8% | 36% | 29.2% | 25.4% | 50.2%
Net Plant Output, kW | 163600 | 163100 | 163500 | 163900 | 164200 | 162300
Net Plant Heat Rate, Btu/kWh (HHV) | 9720 | 9720 | 9710 | 9710 | 9710 | 9710
Heat Input, MMBtu/h (HHV) | 1590 | 1590 | 1590 | 1590 | 1590 | 1580
Min Load Plant Output, kW | 21100 | 21100 | 21200 | 21000 | 20900 | 21300
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12290 | 12300 | 12270 | 12320 | 12350 | 12210
Min LoadHeat Input, MMBtu/h (HHV) | 260 | 260 | 260 | 260 | 260 | 260
Winter DMNC Performance
Ambient Temperature, °F | 11.4 | 10.9 | 13.1 | 14.5 | 22.2 | 17.5
Relative Humidity, % | 73.3% | 61.7% | 69.85% | 65.9% | 46.7% | 46.9%
Net Plant Output, kW | 188200 | 188200 | 188200 | 188200 | 188200 | 188200
Net Plant Heat Rate, Btu/kWh (HHV) | 9380 | 9380 | 9380 | 9390 | 9400 | 9390
Heat Input, MMBtu/h (HHV) | 1770 | 1770 | 1770 | 1770 | 1770 | 1770
Min Load Plant Output, kW | 25700 | 25700 | 25700 | 25700 | 25700 | 25700
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 11500 | 11500 | 11500 | 11500 | 11520 | 11500
Min LoadHeat Input, MMBtu/h (HHV) | 300 | 300 | 300 | 300 | 300 | 300
ICAP Performance
Ambient Temperature, °F | 90 | 90 | 90 | 90 | 90 | 90
Relative Humidity, % | 70% | 70% | 70% | 70% | 70% | 70%
Net Plant Output, kW | 158600 | 158600 | 158700 | 158700 | 158700 | 158700
Net Plant Heat Rate, Btu/kWh (HHV) | 9730 | 9730 | 9730 | 9730 | 9720 | 9720
Heat Input, MMBtu/h (HHV) | 1540 | 1540 | 1540 | 1540 | 1540 | 1540
Min Load Plant Output, kW | 21200 | 21200 | 21200 | 21200 | 21200 | 21200
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12240 | 12240 | 12230 | 12230 | 12230 | 12230
Min LoadHeat Input, MMBtu/h (HHV) | 260 | 260 | 260 | 260 | 260 | 260
ESTIMATED STARTUP FUEL USAGE
Start to Base Load, MMBtu (includes all GTs) | 100 | 100 | 100 | 100 | 100 | 100
ESTIMATED CAPITAL AND O&M COSTS
EPC Project Capital Costs, 2020 MM$ (w/o Owner's Costs) | 224.62 | 226.97 | 230.83 | 239.16 | 259.57 | 256.57
Labor | 45.8532 | 46.3329 | 47.1209 | 48.8213 | 52.9878 | 52.3754
Materials | 59.2992 | 59.9196 | 60.9386 | 63.1377 | 68.5259 | 67.734
Turbines or Batteries | 68.8584 | 69.5788 | 70.7621 | 73.3157 | 79.5725 | 78.6528
Other | 50.6092 | 51.1387 | 52.0084 | 53.8852 | 58.4838 | 57.8079
Owner's Cost Allowances, 2020 MM$ | 74.4 | 74.53 | 74.74 | 75.3 | 116.35 | 64.09
Owner's Project Development | 0.37 | 0.37 | 0.37 | 0.37 | 0.48 | 0.41
Owner's Operational Personnel Prior to COD | 0.44 | 0.44 | 0.44 | 0.44 | 0.57 | 0.48
Owner's Engineer | 1.02 | 1.02 | 1.02 | 1.02 | 1.33 | 1.12
Owner's Project Management | 1.13 | 1.13 | 1.13 | 1.13 | 1.47 | 1.24
Owner's Legal Costs | 1 | 1 | 1 | 1 | 1.3 | 1.1
Owner's Start-up Engineering and Commissioning | 0.27 | 0.27 | 0.27 | 0.27 | 0.35 | 0.3
Sales Tax | 0 | 0 | 0 | 0 | 0 | 0
Construction Power and Water | 0.51 | 0.51 | 0.51 | 0.51 | 0.66 | 0.56
Permitting and Licensing Fees | 1 | 1 | 1 | 1 | 1.3 | 1.1
Switchyard | 17.08 | 17.08 | 17.08 | 17.08 | 53.07 | 9.32
Electrical Interconnection and Deliverability | 11 | 11 | 11 | 11 | 11 | 6.5
Gas Interconnection and Reinforcement | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3
System Deliverability Upgrade Costs
Emission Reduction Credits | 0.4 | 0.4 | 0.4 | 2.5 | 2.5 | 2.5
Political Concessions & Area Development Fees | 0.5 | 0.5 | 0.5 | 0.5 | 0.65 | 0.55
Startup/Testing (Fuel & Consumables) | 2.64 | 2.64 | 2.64 | 2.64 | 2.64 | 2.64
Initial Fuel Inventory | 4.18 | 4.18 | 4.18 | 4.18 | 4.18 | 4.18
Site Security | 0.58 | 0.58 | 0.58 | 0.58 | 0.75 | 0.64
Operating Spare Parts | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11
Builders Risk Insurance (0.45% of Construction Costs) | 1.01 | 1.02 | 1.04 | 1.08 | 1.17 | 1.15
Owner's Contingency (5% for Screening Purposes) | 14.26 | 14.38 | 14.57 | 15.09 | 18.02 | 15.39
AFUDC, 2020 MM$ | 20.9314 | 21.105 | 21.3899 | 22.0122 | 26.3144 | 22.4462
EPC Portion | 15.7234 | 15.8879 | 16.1581 | 16.7412 | 18.1699 | 17.9599
Non-EPC Portion | 5.208 | 5.2171 | 5.2318 | 5.271 | 8.1445 | 4.4863
Total Project Costs, 2020 MM$ | 319.9514 | 322.605 | 326.9599 | 336.4722 | 402.2344 | 343.1062
EPC Cost Per kW, 2020 $/kW (Based on ICAP kW) | 1420 | 1430 | 1450 | 1510 | 1640 | 1620
Total Cost Per kW, 2020 $/kW (Based on ICAP kW) | 2020 | 2030 | 2060 | 2120 | 2530 | 2160
FIXED O&M COSTS - NATURAL GAS ONLY
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3 | 1.3 | 1.7 | 1.5
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Site Leasing Allowance, 2020$MM/Yr | 0.33 | 0.33 | 0.33 | 0.33 | 4.05 | 0.39
Property Insurance Allowance, 2020$MM/Yr | 1.3477 | 1.3618 | 1.385 | 1.435 | 1.5574 | 1.5394
FIXED O&M COSTS - DUAL FUEL
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3 | 1.3 | 1.7 | 1.5
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Site Leasing Allowance, 2020$MM/Yr | 0.33 | 0.33 | 0.33 | 0.33 | 4.05 | 0.39
Property Insurance Allowance, 2020$MM/Yr | 1.3477 | 1.3618 | 1.385 | 1.435 | 1.5574 | 1.5394
LEVELIZED MAJOR MAINTENANCE COSTS
Major Maintenance Cost, 2020$/GT-hr or $/engine-hr | 190 | 190 | 190 | 190 | 190 | 190
Major Maintenance Cost, 2020$/GT-start | N/A | N/A | N/A | N/A | N/A | N/A
Major Maintenance Cost, 2020$/MWh | 3 | 3 | 3 | 3 | 3 | 3
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - GAS OPERATION
Total Variable O&M Cost, 2020$/MWh | 10.07 | 9.95 | 9.85 | 9.85 | 10.17 | 9.72
Water Related O&M, $/MWh | 8.35 | 8.22 | 8.12 | 8.12 | 8.44 | 7.99
SCR Related Costs, $/MWh | 0.82 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - FUEL OIL OPERATION
Total Variable O&M Cost, 2020$/MWh | 10.2 | 10 | 9.9 | 9.9 | 10.21 | 9.79
Water Related O&M, $/MWh | 8.2 | 8.1 | 8 | 8 | 8.28 | 7.86
SCR Related Costs, $/MWh | 1 | 1 | 1 | 1 | 1.03 | 1.03
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
CAPITAL COST DEDUCT FOR GAS ONLY
Capital Costs, 2020 MM$ | -11.3 | -11.3 | -11.3 | -11.3 | -12.3 | -12.3
Owner's Costs, 2020 MM$ | -4.8 | -4.8 | -4.8 | -4.8 | -4.9 | -4.9
CAPITAL COST DEDUCT TO REMOVE SCR/CO
Capital Costs, 2020 MM$ | -17.1 | -17.1 | -17.1 | -17.1 | -20.4 | -20.4
Owner's Costs, 2020 MM$ | -0.9 | -0.9 | -0.9 | -0.9 | -1.1 | -1.1
ESTIMATED BASE LOAD OPERATING EMISSIONS: NATURAL GAS
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 166.8 | 166.8 | 166.8 | 166.8 | 166.8 | 166.8
SO2 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
CO | 302.4 | 302.4 | 302.4 | 302.4 | 302.4 | 302.4
CO2 | 208800 | 208800 | 208800 | 208800 | 208800 | 208800
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 13.3 | 13.3 | 13.3 | 13.3 | 13.3 | 13.3
SO2 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
CO | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
CO2 | 208800 | 208800 | 208800 | 208800 | 208800 | 208800
ESTIMATED BASE LOAD OPERATING EMISSIONS: ULTRA-LOW SULFUR FUEL OIL
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 278 | 278 | 278 | 278 | 278 | 278
SO2 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
CO | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4
CO2 | 278400 | 278400 | 278400 | 278400 | 278400 | 278400
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 41.7 | 41.7 | 41.7 | 41.7 | 41.7 | 41.7
SO2 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
CO | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2
CO2 | 278400 | 278400 | 278400 | 278400 | 278400 | 278400
Notes
Note 1: Capital cost assumes EPC full wrap methodology. Electrical scope ends at the high side of the GSU. Assumes gas, water, sewer, communications are available at plant fenceline.
Note 2: Simple cycle GT starts are not affected by hot, warm or cold conditions. Simple cycle starts assume purge credits are available.
Note 3: MECL start time assumes the min load at which the GT achieves the steady state NOx emissions ppm rate. The SCR compliance start time assumes a cold start, ending at the time when the catalysts are heated and the NOx levels meet the desired SCR emissions.
Note 4: Outage and availability statistics are collected using the NERC Generating Availability Data System. Simple cycle data is based on North American units that came online in 2010 or later. Reporting period is 2012-2019.
Note 5: Degraded performance assumed for all scenarios. For Siemens A65, 2.5% average degradation is assumed. All performance ratings based on NATURAL GAS operation. Minimum loads are based on OEM information at requested ambient conditions.
Note 6: Assumes incoming gas pressure of 250 psig. Compression included in EPC scope. Owner's costs include 5 miles pipeline for all zones except Zone J, which assumes 1 mile. 12" pipeline for aero and F class. 16" pipeline for J class.
Note 7: Capital and fixed O&M costs are presented in 2020 USD $MM.
Note 8: FOM costs assume 7 full time personnel. FOM costs do not include engine lease fees that may be available with LTSA, depending on OEM.
Note 9: Major maintenance $/hr holds for all aero gas turbines. Major maintenance $/hr holds for frame gas turbines where hours per start is >27.
Note 10: VOM assumes the use of temporarily trailers for demineralized water treatment.
Note 11: Emissions estimates are shown for steady state operation at annual average conditions.
Note 12: Fuel Oil emissions based on ultra low sulfur diesel. Per the US EPA, this fuel must meet 15 ppm sulfur.
Note 13: Estimated Costs exclude decommisioning costs and salvage values.

## Raw_F-Class
NYISO DCR TECHNOLOGY ASSESSMENT
SIMPLE CYCLE FRAME F-CLASS
PRELIMINARY AND CONFIDENTIAL - NOT FOR CONSTRUCTION
Mar 2020 - DRAFT REV 2
PROJECT TYPE | ZONE C | ZONE F | ZONE G - Dutchess | ZONE G - Rockland | ZONE J | ZONE K
BASE PLANT DESCRIPTION
Number of Gas Turbines | 1 | 1 | 1 | 1 | 1 | 1
Representative Class Gas Turbine | GE 7F.05 | GE 7F.05 | GE 7F.05 | GE 7F.05 | GE 7F.05 | GE 7F.05
Startup Time to Base Load, min | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional
Startup Time to MECL, min | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional
Cold Startup Time to SCR Compliance, min | 45 | 45 | 45 | 45 | 45 | 45
Equivalent Forced Outage Rate Demand, % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Assumed Land Use During Operation, Acres (Not Construction Land Use) | 15 | 15 | 15 | 15 | 15 | 15
Fuel Design | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil)
Inlet Conditioning | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler
Heat Rejection | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger
NOx Control | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR
CO Control | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst
Particulate Control | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice
Interconnection Voltage, kV | 345 | 345 | 345 | 345 | 345 | 138
Technology Rating | Mature | Mature | Mature | Mature | Mature | Mature
Permitting & Construction Schedule (Years from FNTP) | 3 | 3 | 3 | 3 | 3 | 3
ESTIMATED PERFORMANCE (All BASED ON NATURAL GAS OPERATION)
Summer Performance
Ambient Temperature, °F | 77.7 | 78.1 | 78.9 | 79.9 | 81.1 | 78
Relative Humidity, % | 46.9% | 48% | 51% | 48.2% | 41.2% | 52.7%
Net Plant Output, kW | 214300 | 215200 | 215500 | 215400 | 216900 | 216700
Net Plant Heat Rate, Btu/kWh (HHV) | 10210 | 10220 | 10230 | 10230 | 10220 | 10230
Heat Input, MMBtu/h (HHV) | 2220 | 2200 | 2200 | 2200 | 2220 | 2220
Min Load Plant Output, kW | 90700 | 91100 | 91300 | 91100 | 91300 | 92000
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13520 | 13530 | 13560 | 13580 | 13580 | 13530
Min LoadHeat Input, MMBtu/h (HHV) | 1240 | 1230 | 1240 | 1240 | 1240 | 1240
Winter Performance
Ambient Temperature, °F | 28.4 | 29.2 | 32.6 | 33.2 | 38.1 | 35.9
Relative Humidity, % | 72.8% | 68.3% | 66.9% | 65.4% | 55% | 62.2%
Net Plant Output, kW | 225400 | 226500 | 226900 | 226800 | 227300 | 227700
Net Plant Heat Rate, Btu/kWh (HHV) | 9870 | 9870 | 9880 | 9880 | 9890 | 9880
Heat Input, MMBtu/h (HHV) | 2250 | 2230 | 2240 | 2240 | 2250 | 2250
Min Load Plant Output, kW | 93500 | 94000 | 94200 | 94100 | 94300 | 94500
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13630 | 13630 | 13620 | 13620 | 13620 | 13620
Min LoadHeat Input, MMBtu/h (HHV) | 1290 | 1280 | 1280 | 1280 | 1280 | 1290
Spring-Fall (ISO) Performance
Ambient Temperature, °F | 59 | 59 | 59 | 59 | 59 | 59
Relative Humidity, % | 60% | 60% | 60% | 60% | 60% | 60%
Net Plant Output, kW | 219800 | 221000 | 221900 | 221900 | 223000 | 223100
Net Plant Heat Rate, Btu/kWh (HHV) | 10160 | 10160 | 10160 | 10160 | 10160 | 10160
Heat Input, MMBtu/h (HHV) | 2260 | 2250 | 2250 | 2250 | 2270 | 2270
Min Load Plant Output, kW | 91900 | 91100 | 91400 | 91400 | 91900 | 91900
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13630 | 13640 | 13630 | 13630 | 13630 | 13630
Min LoadHeat Input, MMBtu/h (HHV) | 1270 | 1240 | 1250 | 1250 | 1250 | 1250
Summer DMNC Performance
Ambient Temperature, °F | 91.6 | 92.3 | 91.2 | 92.3 | 95.1 | 88.6
Relative Humidity, % | 34.2% | 35.8% | 36% | 35.8% | 25.4% | 50.2%
Net Plant Output, kW | 211300 | 211900 | 213100 | 211900 | 214700 | 213000
Net Plant Heat Rate, Btu/kWh (HHV) | 10290 | 10300 | 10290 | 10300 | 10280 | 10330
Heat Input, MMBtu/h (HHV) | 2200 | 2180 | 2190 | 2180 | 2210 | 2200
Min Load Plant Output, kW | 87600 | 87900 | 88500 | 87800 | 87700 | 89800
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13720 | 13740 | 13710 | 13760 | 13780 | 13680
Min LoadHeat Input, MMBtu/h (HHV) | 1220 | 1210 | 1210 | 1210 | 1210 | 1230
Winter DMNC Performance
Ambient Temperature, °F | 11.4 | 10.9 | 13.1 | 14.5 | 22.2 | 17.5
Relative Humidity, % | 73.3% | 61.7% | 69.85% | 65.9% | 46.7% | 46.9%
Net Plant Output, kW | 225900 | 227100 | 228000 | 228000 | 229200 | 229200
Net Plant Heat Rate, Btu/kWh (HHV) | 9830 | 9830 | 9830 | 9840 | 9850 | 9840
Heat Input, MMBtu/h (HHV) | 2250 | 2230 | 2240 | 2240 | 2260 | 2260
Min Load Plant Output, kW | 93800 | 94200 | 94600 | 94600 | 95100 | 95100
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13680 | 13680 | 13680 | 13670 | 13640 | 13660
Min LoadHeat Input, MMBtu/h (HHV) | 1300 | 1290 | 1290 | 1290 | 1300 | 1300
ICAP Performance
Ambient Temperature, °F | 90 | 90 | 90 | 90 | 90 | 90
Relative Humidity, % | 70% | 70% | 70% | 70% | 70% | 70%
Net Plant Output, kW | 207100 | 208200 | 209100 | 209100 | 210200 | 210200
Net Plant Heat Rate, Btu/kWh (HHV) | 10360 | 10360 | 10360 | 10360 | 10360 | 10360
Heat Input, MMBtu/h (HHV) | 2170 | 2160 | 2170 | 2170 | 2180 | 2180
Min Load Plant Output, kW | 87600 | 88700 | 89100 | 89100 | 89500 | 89500
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13720 | 13720 | 13720 | 13720 | 13720 | 13720
Min LoadHeat Input, MMBtu/h (HHV) | 1220 | 1220 | 1220 | 1220 | 1230 | 1230
ESTIMATED STARTUP FUEL USAGE
Start to Base Load, MMBtu | 140 (fast) / 325 (typ) | 140 (fast) / 325 (typ) | 140 (fast) / 325 (typ) | 140 (fast) / 325 (typ) | 140 (fast) / 325 (typ) | 140 (fast) / 325 (typ)
ESTIMATED CAPITAL AND O&M COSTS
EPC Project Capital Costs, 2020 MM$ (w/o Owner's Costs) | 180.96 | 183.9 | 187.65 | 198.84 | 226.42 | 223.42
Labor | 54.1606 | 55.0405 | 56.1629 | 59.512 | 67.7666 | 66.8687
Materials | 32.9305 | 33.4655 | 34.1479 | 36.1843 | 41.2032 | 40.6573
Turbines or Batteries | 44.4809 | 45.2035 | 46.1253 | 48.8758 | 55.6551 | 54.9177
Other | 49.388 | 50.1904 | 51.2139 | 54.2679 | 61.7951 | 60.9763
Owner's Cost Allowances, 2020 MM$ | 68.65 | 68.81 | 69.01 | 69.83 | 116.02 | 62.29
Owner's Project Development | 0.37 | 0.37 | 0.37 | 0.37 | 0.48 | 0.41
Owner's Operational Personnel Prior to COD | 0.44 | 0.44 | 0.44 | 0.44 | 0.57 | 0.48
Owner's Engineer | 1.02 | 1.02 | 1.02 | 1.02 | 1.33 | 1.12
Owner's Project Management | 1.13 | 1.13 | 1.13 | 1.13 | 1.47 | 1.24
Owner's Legal Costs | 1 | 1 | 1 | 1 | 1.3 | 1.1
Owner's Start-up Engineering and Commissioning | 0.27 | 0.27 | 0.27 | 0.27 | 0.35 | 0.3
Sales Tax | 0 | 0 | 0 | 0 | 0 | 0
Construction Power and Water | 0.51 | 0.51 | 0.51 | 0.51 | 0.66 | 0.56
Permitting and Licensing Fees | 1 | 1 | 1 | 1 | 1.3 | 1.1
Switchyard | 10.25 | 10.25 | 10.25 | 10.25 | 50.75 | 5.59
Electrical Interconnection and Deliverability | 11 | 11 | 11 | 11 | 11 | 6.5
Gas Interconnection and Reinforcement | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3
System Deliverability Upgrade Costs
Emission Reduction Credits | 0.1 | 0.1 | 0.1 | 0.3 | 0.3 | 0.3
Political Concessions & Area Development Fees | 0.5 | 0.5 | 0.5 | 0.5 | 0.65 | 0.55
Startup/Testing (Fuel & Consumables) | 3.1 | 3.1 | 3.1 | 3.1 | 3.1 | 3.1
Initial Fuel Inventory | 4.88 | 4.88 | 4.88 | 4.88 | 4.88 | 4.88
Site Security | 0.58 | 0.58 | 0.58 | 0.58 | 0.75 | 0.64
Operating Spare Parts | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Builders Risk Insurance (0.45% of Construction Costs) | 0.81 | 0.83 | 0.84 | 0.89 | 1.02 | 1.01
Owner's Contingency (5% for Screening Purposes) | 11.89 | 12.03 | 12.22 | 12.79 | 16.31 | 13.61
AFUDC, 2020 MM$ | 17.4727 | 17.6897 | 17.9662 | 18.8069 | 23.9708 | 19.9997
EPC Portion | 12.6672 | 12.873 | 13.1355 | 13.9188 | 15.8494 | 15.6394
Non-EPC Portion | 4.8055 | 4.8167 | 4.8307 | 4.8881 | 8.1214 | 4.3603
Total Project Costs, 2020 MM$ | 267.0827 | 270.3997 | 274.6262 | 287.4769 | 366.4108 | 305.7097
EPC Cost Per kW, 2020 $/kW (Based on ICAP kW) | 870 | 880 | 900 | 950 | 1080 | 1060
Total Cost Per kW, 2020 $/kW (Based on ICAP kW) | 1290 | 1300 | 1310 | 1370 | 1740 | 1450
FIXED O&M COSTS
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3 | 1.3 | 1.7 | 1.5
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Site Leasing Allowance, 2020$/MM/Yr | 0.33 | 0.33 | 0.33 | 0.33 | 4.05 | 0.39
Property Insurance Allowance, 2020$MM/Yr | 1.0858 | 1.1034 | 1.1259 | 1.193 | 1.3585 | 1.3405
FIXED O&M COSTS - DUAL FUEL
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3 | 1.3 | 1.7 | 1.5
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Site Leasing Allowance, 2020$MM/Yr | 0.33 | 0.33 | 0.33 | 0.33 | 4.05 | 0.39
Property Insurance Allowance, 2020$MM/Yr | 1.0858 | 1.1034 | 1.1259 | 1.193 | 1.3585 | 1.3405
LEVELIZED MAJOR MAINTENANCE COSTS
Major Maintenance Cost, 2020$/GT-hr or $/engine-hr | 350 | 350 | 350 | 350 | 350 | 350
Major Maintenance Cost, 2020$/GT-start | 9500 | 9500 | 9500 | 9500 | 9500 | 9500
Major Maintenance Cost, 2020$/MWh | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - GAS OPERATION
Total Variable O&M Cost, 2020$/MWh | 1.48 | 1.48 | 1.48 | 1.48 | 1.5 | 1.48
Water Related O&M, $/MWh | 0 | 0 | 0 | 0 | 0.02 | 0
SCR Related Costs, $/MWh | 0.58 | 0.58 | 0.58 | 0.58 | 0.57 | 0.57
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9 | 0.9 | 0.91 | 0.91
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - FUEL OIL OPERATION
Total Variable O&M Cost, 2020$/MWh | 8.8 | 8.8 | 8.8 | 8.8 | 9.17 | 8.79
Water Related O&M, $/MWh | 7.1 | 7.1 | 7.1 | 7.1 | 7.48 | 7.11
SCR Related Costs, $/MWh | 0.8 | 0.8 | 0.8 | 0.8 | 0.79 | 0.79
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.89
CAPITAL COST DEDUCT FOR GAS ONLY
Capital Costs, 2020 MM$ | -16.9 | -16.9 | -16.9 | -16.9 | -20.1 | -20.1
Owner's Costs, 2020 MM$ | -5.8 | -5.8 | -5.8 | -5.8 | -6 | -6
CAPITAL COST DEDUCT TO REMOVE SCR/CO
Capital Costs, 2020 MM$ | -20.6 | -20.6 | -20.6 | -20.6 | -24 | -24
Owner's Costs, 2020 MM$ | -1.1 | -1.1 | -1.1 | -1.1 | -1.3 | -1.3
ESTIMATED BASE LOAD OPERATING EMISSIONS: NATURAL GAS
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9
SO2 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
CO | 48.6 | 48.6 | 48.6 | 48.6 | 48.6 | 48.6
CO2 | 271200 | 270000 | 270000 | 270000 | 272400 | 272400
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8
SO2 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
CO | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
CO2 | 271200 | 270000 | 270000 | 270000 | 272400 | 272400
ESTIMATED BASE LOAD OPERATING EMISSIONS: ULTRA-LOW SULFUR FUEL OIL
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 430 | 430 | 430 | 430 | 430 | 430
SO2 | 3.4 | 3.4 | 3.4 | 3.4 | 3.5 | 3.5
CO | 84.3 | 84.3 | 84.3 | 84.3 | 84.3 | 84.3
CO2 | 361600 | 360000 | 360000 | 360000 | 363200 | 363200
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 64.5 | 64.5 | 64.5 | 64.5 | 64.5 | 64.5
SO2 | 3.4 | 3.4 | 3.4 | 3.4 | 3.5 | 3.5
CO | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3
CO2 | 361600 | 360000 | 360000 | 360000 | 363200 | 363200
Notes
Note 1: Capital cost assumes EPC full wrap methodology. Electrical scope ends at the high side of the GSU. Assumes gas, water, sewer, communications are available at plant fenceline.
Note 2: Simple cycle GT starts are not affected by hot, warm or cold conditions. Simple cycle starts assume purge credits are available.
Note 3: MECL start time assumes the min load at which the GT achieves the steady state NOx emissions ppm rate. The SCR compliance start time assumes a cold start, ending at the time when the catalysts are heated and the NOx levels meet the desired SCR emissions.
Note 4: Outage and availability statistics are collected using the NERC Generating Availability Data System. Simple cycle data is based on North American units that came online in 2010 or later. Reporting period is 2012-2019.
Note 5: Degraded performance assumed for all scenarios. For frame units, 3% average degradation is assumed. All performance ratings based on NATURAL GAS operation. Minimum loads are based on OEM information at requested ambient conditions.
Note 6: Assumes incoming gas pressure of 250 psig. Compression included in EPC scope. Owner's costs include 5 miles pipeline for all zones except Zone J, which assumes 1 mile. 12" pipeline for aero and F class. 16" pipeline for J class.
Note 7: Capital and fixed O&M costs are presented in 2020 USD $MM.
Note 8: FOM costs assume 7 full time personnel. FOM costs do not include engine lease fees that may be available with LTSA, depending on OEM.
Note 9: Major maintenance $/hr holds for all aero gas turbines. Major maintenance $/hr holds for frame gas turbines where hours per start is >27.
Note 10: VOM assumes the use of temporarily trailers for demineralized water treatment.
Note 11: Emissions estimates are shown for steady state operation at annual average conditions.
Note 12: Fuel Oil emissions based on ultra low sulfur diesel. Per the US EPA, this fuel must meet 15 ppm sulfur.
Note 13: Estimated Costs exclude decommisioning costs and salvage values.

## Raw_J-Class25ppm
NYISO DCR TECHNOLOGY ASSESSMENT
SIMPLE CYCLE FRAME J-CLASS (GE HA.02)
PRELIMINARY AND CONFIDENTIAL - NOT FOR CONSTRUCTION
Mar 2020 - DRAFT REV 2
PROJECT TYPE | ZONE C | ZONE F | ZONE G - Dutchess | ZONE G - Rockland | ZONE J | ZONE K
BASE PLANT DESCRIPTION
Number of Gas Turbines | 1 | 1 | 1 | 1 | 1 | 1
Representative Class Gas Turbine | GE 7HA.02 | GE 7HA.02 | GE 7HA.02 | GE 7HA.02 | GE 7HA.02 | GE 7HA.02
Startup Time to Base Load, min | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional
Startup Time to MECL, min | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional
Cold Startup Time to SCR Compliance, min | 45 | 45 | 45 | 45 | 45 | 45
Equivalent Forced Outage Rate Demand, % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Assumed Land Use During Operation, Acres (Not Construction Land Use) | 15 | 15 | 15 | 15 | 15 | 15
Fuel Design | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil)
Inlet Conditioning | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler
Heat Rejection | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger
NOx Control | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR
CO Control | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst
Particulate Control | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice
Interconnection Voltage, kV | 345 | 345 | 345 | 345 | 345 | 138
Technology Rating | Mature | Mature | Mature | Mature | Mature | Mature
Permitting & Construction Schedule (Years from FNTP) | 3 | 3 | 3 | 3 | 3 | 3
ESTIMATED PERFORMANCE (All BASED ON NATURAL GAS OPERATION)
Summer Performance
Ambient Temperature, °F | 77.7 | 78.1 | 78.9 | 79.9 | 81.1 | 78
Relative Humidity, % | 46.9% | 48% | 51% | 48.2% | 41.2% | 52.7%
Net Plant Output, kW | 352800 | 354300 | 355100 | 355000 | 357400 | 357200
Net Plant Heat Rate, Btu/kWh (HHV) | 9380 | 9380 | 9390 | 9390 | 9380 | 9390
Heat Input, MMBtu/h (HHV) | 3350 | 3320 | 3330 | 3330 | 3350 | 3350
Min Load Plant Output, kW | 137400 | 138000 | 138400 | 138000 | 138100 | 139500
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12000 | 12000 | 12010 | 12010 | 12020 | 12000
Min LoadHeat Input, MMBtu/h (HHV) | 1670 | 1660 | 1660 | 1660 | 1660 | 1670
Winter Performance
Ambient Temperature, °F | 28.4 | 29.2 | 32.6 | 33.2 | 38.1 | 35.9
Relative Humidity, % | 72.8% | 68.3% | 66.9% | 65.4% | 55% | 62.2%
Net Plant Output, kW | 368100 | 369900 | 370800 | 370700 | 371600 | 372200
Net Plant Heat Rate, Btu/kWh (HHV) | 9270 | 9270 | 9280 | 9290 | 9300 | 9290
Heat Input, MMBtu/h (HHV) | 3460 | 3430 | 3440 | 3440 | 3460 | 3460
Min Load Plant Output, kW | 110400 | 111000 | 111200 | 111200 | 111500 | 111600
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13440 | 13440 | 13420 | 13420 | 13410 | 13410
Min LoadHeat Input, MMBtu/h (HHV) | 1500 | 1490 | 1490 | 1490 | 1490 | 1500
Spring-Fall (ISO) Performance
Ambient Temperature, °F | 59 | 59 | 59 | 59 | 59 | 59
Relative Humidity, % | 60% | 60% | 60% | 60% | 60% | 60%
Net Plant Output, kW | 359500 | 361400 | 362900 | 362900 | 364800 | 364900
Net Plant Heat Rate, Btu/kWh (HHV) | 9340 | 9340 | 9340 | 9340 | 9340 | 9340
Heat Input, MMBtu/h (HHV) | 3400 | 3380 | 3390 | 3390 | 3410 | 3410
Min Load Plant Output, kW | 108400 | 107400 | 107800 | 107800 | 108400 | 108400
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13440 | 13450 | 13450 | 13450 | 13440 | 13440
Min LoadHeat Input, MMBtu/h (HHV) | 1480 | 1440 | 1450 | 1450 | 1460 | 1460
Summer DMNC Performance
Ambient Temperature, °F | 91.6 | 92.3 | 91.2 | 92.3 | 95.1 | 88.6
Relative Humidity, % | 34.2% | 35.8% | 36% | 35.8% | 25.4% | 50.2%
Net Plant Output, kW | 348900 | 350200 | 352000 | 350200 | 354500 | 352600
Net Plant Heat Rate, Btu/kWh (HHV) | 9430 | 9430 | 9430 | 9430 | 9420 | 9440
Heat Input, MMBtu/h (HHV) | 3330 | 3300 | 3320 | 3300 | 3340 | 3330
Min Load Plant Output, kW | 131200 | 131700 | 132700 | 131300 | 131100 | 135200
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12130 | 12140 | 12130 | 12150 | 12160 | 12110
Min LoadHeat Input, MMBtu/h (HHV) | 1610 | 1600 | 1610 | 1590 | 1590 | 1640
Winter DMNC Performance
Ambient Temperature, °F | 11.4 | 10.9 | 13.1 | 14.5 | 22.2 | 17.5
Relative Humidity, % | 73.3% | 61.7% | 69.85% | 65.9% | 46.7% | 46.9%
Net Plant Output, kW | 366000 | 367900 | 370100 | 370500 | 374300 | 373300
Net Plant Heat Rate, Btu/kWh (HHV) | 9210 | 9210 | 9210 | 9220 | 9250 | 9230
Heat Input, MMBtu/h (HHV) | 3410 | 3390 | 3410 | 3420 | 3460 | 3450
Min Load Plant Output, kW | 109800 | 110400 | 111000 | 111100 | 112300 | 112000
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13590 | 13590 | 13590 | 13580 | 13480 | 13540
Min LoadHeat Input, MMBtu/h (HHV) | 1510 | 1500 | 1510 | 1510 | 1510 | 1520
ICAP Performance
Ambient Temperature, °F | 90 | 90 | 90 | 90 | 90 | 90
Relative Humidity, % | 70% | 70% | 70% | 70% | 70% | 70%
Net Plant Output, kW | 343700 | 345600 | 347000 | 347000 | 348800 | 348800
Net Plant Heat Rate, Btu/kWh (HHV) | 9460 | 9460 | 9460 | 9460 | 9460 | 9460
Heat Input, MMBtu/h (HHV) | 3290 | 3270 | 3280 | 3280 | 3300 | 3300
Min Load Plant Output, kW | 131200 | 134000 | 134500 | 134500 | 135200 | 135200
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12130 | 12160 | 12160 | 12160 | 12150 | 12150
Min LoadHeat Input, MMBtu/h (HHV) | 1610 | 1630 | 1630 | 1630 | 1640 | 1640
ESTIMATED STARTUP FUEL USAGE
Start to Base Load, MMBtu | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ)
ESTIMATED CAPITAL AND O&M COSTS
EPC Project Capital Costs, 2020 MM$ (w/o Owner's Costs) | 249.58 | 252.64 | 256.49 | 266.81 | 300.58 | 297.58
Labor | 62.4426 | 63.2082 | 64.1715 | 66.7534 | 75.2024 | 74.4518
Materials | 40.1745 | 40.6671 | 41.2868 | 42.948 | 48.3839 | 47.901
Turbines or Batteries | 88.5041 | 89.5892 | 90.9544 | 94.614 | 106.5893 | 105.5254
Other | 58.4587 | 59.1755 | 60.0773 | 62.4945 | 70.4044 | 69.7017
Owner's Cost Allowances, 2020 MM$ | 81.22 | 81.4 | 81.6 | 82.48 | 129.02 | 75.27
Owner's Project Development | 0.37 | 0.37 | 0.37 | 0.37 | 0.48 | 0.41
Owner's Operational Personnel Prior to COD | 0.44 | 0.44 | 0.44 | 0.44 | 0.57 | 0.48
Owner's Engineer | 1.02 | 1.02 | 1.02 | 1.02 | 1.33 | 1.12
Owner's Project Management | 1.13 | 1.13 | 1.13 | 1.13 | 1.47 | 1.24
Owner's Legal Costs | 1 | 1 | 1 | 1 | 1.3 | 1.1
Owner's Start-up Engineering and Commissioning | 0.27 | 0.27 | 0.27 | 0.27 | 0.35 | 0.3
Sales Tax | 0 | 0 | 0 | 0 | 0 | 0
Construction Power and Water | 0.55 | 0.55 | 0.55 | 0.55 | 0.72 | 0.61
Permitting and Licensing Fees | 1 | 1 | 1 | 1 | 1.3 | 1.1
Switchyard | 10.25 | 10.25 | 10.25 | 10.25 | 50.75 | 5.59
Electrical Interconnection and Deliverability | 11 | 11 | 11 | 11 | 11 | 6.5
Gas Interconnection and Reinforcement | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | 17.9
System Deliverability Upgrade Costs
Emission Reduction Credits | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4
Political Concessions & Area Development Fees | 0.5 | 0.5 | 0.5 | 0.5 | 0.65 | 0.55
Startup/Testing (Fuel & Consumables) | 4.5 | 4.5 | 4.5 | 4.5 | 4.5 | 4.5
Initial Fuel Inventory | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24
Site Security | 0.58 | 0.58 | 0.58 | 0.58 | 0.75 | 0.64
Operating Spare Parts | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Builders Risk Insurance (0.45% of Construction Costs) | 1.12 | 1.14 | 1.15 | 1.2 | 1.35 | 1.34
Owner's Contingency (5% for Screening Purposes) | 15.75 | 15.91 | 16.1 | 16.63 | 20.46 | 17.75
AFUDC, 2020 MM$ | 23.156 | 23.3828 | 23.6663 | 24.4503 | 30.072 | 26.0995
EPC Portion | 17.4706 | 17.6848 | 17.9543 | 18.6767 | 21.0406 | 20.8306
Non-EPC Portion | 5.6854 | 5.698 | 5.712 | 5.7736 | 9.0314 | 5.2689
Total Project Costs, 2020 MM$ | 353.956 | 357.4228 | 361.7563 | 373.7403 | 459.672 | 398.9495
EPC Cost Per kW, 2020 $/kW (Based on ICAP kW) | 730 | 730 | 740 | 770 | 860 | 850
Total Cost Per kW, 2020 $/kW (Based on ICAP kW) | 1030 | 1030 | 1040 | 1080 | 1320 | 1140
FIXED O&M COSTS
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3 | 1.3 | 1.7 | 1.5
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Site Leasing Allowance, 2020$/MM/Yr | 0.33 | 0.33 | 0.33 | 0.33 | 4.05 | 0.39
Property Insurance Allowance, 2020$MM/Yr | 1.4975 | 1.5158 | 1.5389 | 1.6009 | 1.8035 | 1.7855
FIXED O&M COSTS - DUAL FUEL
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3 | 1.3 | 1.7 | 1.5
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Site Leasing Allowance, 2020$MM/Yr | 0.33 | 0.33 | 0.33 | 0.33 | 4.05 | 0.39
Property Insurance Allowance, 2020$MM/Yr | 1.4975 | 1.5158 | 1.5389 | 1.6009 | 1.8035 | 1.7855
LEVELIZED MAJOR MAINTENANCE COSTS
Major Maintenance Cost, 2020$/GT-hr or $/engine-hr | 600 | 600 | 600 | 600 | 600 | 600
Major Maintenance Cost, 2020$/GT-start | 16200 | 16200 | 16200 | 16200 | 16200 | 16200
Major Maintenance Cost, 2020$/MWh | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - GAS OPERATION
Total Variable O&M Cost, 2020$/MWh | 1.37 | 1.27 | 1.27 | 1.27 | 1.39 | 1.27
Water Related O&M, $/MWh | 0 | 0 | 0 | 0 | 0.02 | 0
SCR Related Costs, $/MWh | 0.47 | 0.37 | 0.37 | 0.37 | 0.48 | 0.37
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - FUEL OIL OPERATION
Total Variable O&M Cost, 2020$/MWh | 8.8 | 8.8 | 8.8 | 8.8 | 11.44 | 8.8
Water Related O&M, $/MWh | 7.1 | 7.1 | 7.1 | 7.1 | 9.83 | 7.1
SCR Related Costs, $/MWh | 0.8 | 0.8 | 0.8 | 0.8 | 0.7 | 0.8
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
CAPITAL COST DEDUCT FOR GAS ONLY
Capital Costs, 2020 MM$ | -25.4 | -25.4 | -25.4 | -25.4 | -30.2 | -30.2
Owner's Costs, 2020 MM$ | -8.6 | -8.6 | -8.6 | -8.6 | -8.9 | -8.9
CAPITAL COST DEDUCT TO REMOVE SCR/CO
Capital Costs, 2020 MM$ | N/A | N/A | N/A | N/A | N/A | N/A
Owner's Costs, 2020 MM$ | N/A | N/A | N/A | N/A | N/A | N/A
ESTIMATED BASE LOAD OPERATING EMISSIONS: NATURAL GAS
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 330.5 | 330.5 | 330.5 | 330.5 | 330.5 | 330.5
SO2 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
CO | 72.4 | 72.4 | 72.4 | 72.4 | 72.4 | 72.4
CO2 | 408000 | 405600 | 406800 | 406800 | 409200 | 409200
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 26.4 | 26.4 | 26.4 | 26.4 | 26.4 | 26.4
SO2 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8 | 6.8
CO | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1
CO2 | 408000 | 405600 | 406800 | 406800 | 409200 | 409200
ESTIMATED BASE LOAD OPERATING EMISSIONS: ULTRA-LOW SULFUR FUEL OIL
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 640 | 640 | 640 | 640 | 640 | 640
SO2 | 5.2 | 5.1 | 5.2 | 5.2 | 5.2 | 5.2
CO | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4
CO2 | 544000 | 540800 | 542400 | 542400 | 545600 | 545600
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 96 | 96 | 96 | 96 | 96 | 96
SO2 | 5.2 | 5.1 | 5.2 | 5.2 | 5.2 | 5.2
CO | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6
CO2 | 544000 | 540800 | 542400 | 542400 | 545600 | 545600
Notes
Note 1: Capital cost assumes EPC full wrap methodology. Electrical scope ends at the high side of the GSU. Assumes gas, water, sewer, communications are available at plant fenceline.
Note 2: Simple cycle GT starts are not affected by hot, warm or cold conditions. Simple cycle starts assume purge credits are available.
Note 3: MECL start time assumes the min load at which the GT achieves the steady state NOx emissions ppm rate. The SCR compliance start time assumes a cold start, ending at the time when the catalysts are heated and the NOx levels meet the desired SCR emissions.
Note 4: Outage and availability statistics are collected using the NERC Generating Availability Data System. Simple cycle data is based on North American units that came online in 2010 or later. Reporting period is 2012-2019.
Note 5: Degraded performance assumed for all scenarios. For frame units, 3% average degradation is assumed. All performance ratings based on NATURAL GAS operation. Minimum loads are based on OEM information at requested ambient conditions.
Note 6: Assumes incoming gas pressure of 250 psig. Compression included in EPC scope. Owner's costs include 5 miles pipeline for all zones except Zone J, which assumes 1 mile. 12" pipeline for aero and F class. 16" pipeline for J class.
Note 7: Capital and fixed O&M costs are presented in 2020 USD $MM.
Note 8: FOM costs assume 7 full time personnel. FOM costs do not include engine lease fees that may be available with LTSA, depending on OEM.
Note 9: Major maintenance $/hr holds for all aero gas turbines. Major maintenance $/hr holds for frame gas turbines where hours per start is >27.
Note 10: VOM assumes the use of temporarily trailers for demineralized water treatment.
Note 11: Emissions estimates are shown for steady state operation at annual average conditions.
Note 12: Fuel Oil emissions based on ultra low sulfur diesel. Per the US EPA, this fuel must meet 15 ppm sulfur.
Note 13: Estimated Costs exclude decommisioning costs and salvage values.

## Raw_J-Class15ppm
NYISO DCR TECHNOLOGY ASSESSMENT
SIMPLE CYCLE FRAME J-CLASS (GE HA.02)
PRELIMINARY AND CONFIDENTIAL - NOT FOR CONSTRUCTION
Mar 2020 - DRAFT REV 2
PROJECT TYPE | ZONE C | ZONE F | ZONE G - Dutchess
BASE PLANT DESCRIPTION
Number of Gas Turbines | 1 | 1 | 1
Representative Class Gas Turbine | GE 7HA.02 | GE 7HA.02 | GE 7HA.02
Startup Time to Base Load, min | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional
Startup Time to MECL, min | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional
Cold Startup Time to SCR Compliance, min | 45 | 45 | 45
Equivalent Forced Outage Rate Demand, % | 4.34% | 4.34% | 4.34%
Assumed Land Use During Operation, Acres (Not Construction Land Use) | 15 | 15 | 15
Fuel Design | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil)
Inlet Conditioning | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler
Heat Rejection | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger
NOx Control | DLN (Gas), Water Injection (Fuel Oil) | DLN (Gas), Water Injection (Fuel Oil) | DLN (Gas), Water Injection (Fuel Oil)
CO Control | CO Catalyst | CO Catalyst | CO Catalyst
Particulate Control | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice
Interconnection Voltage, kV | 345 | 345 | 345
Technology Rating | Mature | Mature | Mature
Permitting & Construction Schedule (Years from FNTP) | 3 | 3 | 3
ESTIMATED PERFORMANCE (All BASED ON NATURAL GAS OPERATION)
Summer Performance
Ambient Temperature, °F | 77.7 | 78.1 | 78.9
Relative Humidity, % | 46.9% | 48% | 51%
Net Plant Output, kW | 335300 | 336700 | 337400
Net Plant Heat Rate, Btu/kWh (HHV) | 9400 | 9270 | 9400
Heat Input, MMBtu/h (HHV) | 3150 | 3120 | 3170
Min Load Plant Output, kW | 130600 | 131200 | 131600
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12030 | 11890 | 12080
Min LoadHeat Input, MMBtu/h (HHV) | 1570 | 1560 | 1590
Winter Performance
Ambient Temperature, °F | 28.4 | 29.2 | 32.6
Relative Humidity, % | 72.8% | 68.3% | 66.9%
Net Plant Output, kW | 346700 | 348400 | 349200
Net Plant Heat Rate, Btu/kWh (HHV) | 9310 | 9180 | 9310
Heat Input, MMBtu/h (HHV) | 3230 | 3200 | 3250
Min Load Plant Output, kW | 104000 | 104600 | 104800
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13500 | 13290 | 13450
Min LoadHeat Input, MMBtu/h (HHV) | 1400 | 1390 | 1410
Spring-Fall (ISO) Performance
Ambient Temperature, °F | 59 | 59 | 59
Relative Humidity, % | 60% | 60% | 60%
Net Plant Output, kW | 340400 | 342200 | 343500
Net Plant Heat Rate, Btu/kWh (HHV) | 9340 | 9230 | 9340
Heat Input, MMBtu/h (HHV) | 3180 | 3160 | 3210
Min Load Plant Output, kW | 101100 | 100200 | 102000
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13470 | 13170 | 13430
Min LoadHeat Input, MMBtu/h (HHV) | 1360 | 1320 | 1370
Summer DMNC Performance
Ambient Temperature, °F | 91.6 | 92.3 | 91.2
Relative Humidity, % | 34.2% | 35.8% | 36%
Net Plant Output, kW | 332000 | 333200 | 334900
Net Plant Heat Rate, Btu/kWh (HHV) | 9440 | 9300 | 9440
Heat Input, MMBtu/h (HHV) | 3130 | 3100 | 3160
Min Load Plant Output, kW | 124700 | 125200 | 126200
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12160 | 12060 | 12120
Min LoadHeat Input, MMBtu/h (HHV) | 1520 | 1510 | 1530
Winter DMNC Performance
Ambient Temperature, °F | 11.4 | 10.9 | 13.1
Relative Humidity, % | 73.3% | 61.7% | 69.85%
Net Plant Output, kW | 344800 | 346600 | 348600
Net Plant Heat Rate, Btu/kWh (HHV) | 9250 | 9150 | 9240
Heat Input, MMBtu/h (HHV) | 3190 | 3170 | 3220
Min Load Plant Output, kW | 103400 | 104000 | 104600
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13650 | 13460 | 13580
Min LoadHeat Input, MMBtu/h (HHV) | 1410 | 1400 | 1420
ICAP Performance
Ambient Temperature, °F | 90 | 90 | 90
Relative Humidity, % | 70% | 70% | 70%
Net Plant Output, kW | 326700 | 328500 | 329900
Net Plant Heat Rate, Btu/kWh (HHV) | 9490 | 9380 | 9490
Heat Input, MMBtu/h (HHV) | 3100 | 3080 | 3130
Min Load Plant Output, kW | 126700 | 129400 | 127900
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12190 | 12060 | 12200
Min LoadHeat Input, MMBtu/h (HHV) | 1540 | 1560 | 1560
ESTIMATED STARTUP FUEL USAGE
Start to Base Load, MMBtu | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ)
ESTIMATED CAPITAL AND O&M COSTS
EPC Project Capital Costs, 2020 MM$ (w/o Owner's Costs) | 206.1416 | 209.2078 | 213.0583
Labor | 51.5747 | 52.3419 | 53.3053
Materials | 33.1823 | 33.6759 | 34.2957
Turbines or Batteries | 73.1003 | 74.1876 | 75.553
Other | 48.2842 | 49.0024 | 49.9043
Owner's Cost Allowances, 2020 MM$ | 78.8486 | 79.0164 | 79.2271
Owner's Project Development | 0.37 | 0.37 | 0.37
Owner's Operational Personnel Prior to COD | 0.44 | 0.44 | 0.44
Owner's Engineer | 1.02 | 1.02 | 1.02
Owner's Project Management | 1.13 | 1.13 | 1.13
Owner's Legal Costs | 1 | 1 | 1
Owner's Start-up Engineering and Commissioning | 0.27 | 0.27 | 0.27
Sales Tax | 0 | 0 | 0
Construction Power and Water | 0.55 | 0.55 | 0.55
Permitting and Licensing Fees | 1 | 1 | 1
Switchyard | 10.25 | 10.25 | 10.25
Electrical Interconnection and Deliverability | 11 | 11 | 11
Gas Interconnection and Reinforcement | 17.9 | 17.9 | 17.9
System Deliverability Upgrade Costs
Emission Reduction Credits | 0.1 | 0.1 | 0.1
Political Concessions & Area Development Fees | 0.5 | 0.5 | 0.5
Startup/Testing (Fuel & Consumables) | 4.5 | 4.5 | 4.5
Initial Fuel Inventory | 7.24 | 7.24 | 7.24
Site Security | 0.58 | 0.58 | 0.58
Operating Spare Parts | 6.5 | 6.5 | 6.5
Builders Risk Insurance (0.45% of Construction Costs) | 0.92764 | 0.94144 | 0.95876
Owner's Contingency (5% for Screening Purposes) | 13.571 | 13.725 | 13.9184
AFUDC, 2020 MM$ | 19.9493 | 20.1757 | 20.46
EPC Portion | 14.4299 | 14.6445 | 14.9141
Non-EPC Portion | 5.5194 | 5.5311 | 5.5459
Total Project Costs, 2020 MM$ | 304.9395 | 308.3999 | 312.7454
EPC Cost Per kW, 2020 $/kW (Based on ICAP kW) | 630 | 640 | 650
Total Cost Per kW, 2020 $/kW (Based on ICAP kW) | 930 | 940 | 950
FIXED O&M COSTS
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.5 | 1.5 | 1.5
Site Leasing Allowance, 2020$/MM/Yr | 0.33 | 0.33 | 0.33
Property Insurance Allowance, 2020$MM/Yr | 1.2368 | 1.2552 | 1.2783
FIXED O&M COSTS - DUAL FUEL
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.5 | 1.5 | 1.5
Site Leasing Allowance, 2020$MM/Yr | 0.33 | 0.33 | 0.33
Property Insurance Allowance, 2020$MM/Yr | 1.2368 | 1.2552 | 1.2783
LEVELIZED MAJOR MAINTENANCE COSTS
Major Maintenance Cost, 2020$/GT-hr or $/engine-hr | 600 | 600 | 600
Major Maintenance Cost, 2020$/GT-start | 16200 | 16200 | 16200
Major Maintenance Cost, 2020$/MWh | 1.6 | 1.6 | 1.6
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - GAS OPERATION
Total Variable O&M Cost, 2020$/MWh | 0.9 | 0.9 | 0.9
Water Related O&M, $/MWh | 0 | 0 | 0
SCR Related Costs, $/MWh | 0 | 0 | 0
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - FUEL OIL OPERATION
Total Variable O&M Cost, 2020$/MWh | 10.2 | 10.2 | 10.2
Water Related O&M, $/MWh | 9.3 | 9.3 | 9.3
SCR Related Costs, $/MWh | 0 | 0 | 0
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9
CAPITAL COST DEDUCT FOR GAS ONLY
Capital Costs, 2020 MM$ | -25.4 | -25.4 | -25.4
Owner's Costs, 2020 MM$ | -8.6 | -8.6 | -8.6
CAPITAL COST DEDUCT TO REMOVE SCR/CO
Capital Costs, 2020 MM$ | N/A | N/A | N/A
Owner's Costs, 2020 MM$ | N/A | N/A | N/A
ESTIMATED BASE LOAD OPERATING EMISSIONS: NATURAL GAS
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 188.6 | 188.6 | 188.6
SO2 | 6.4 | 6.3 | 6.4
CO | 68.9 | 68.9 | 68.9
CO2 | 381600 | 379200 | 385200
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 26.4 | 26.4 | 26.4
SO2 | 6.4 | 6.3 | 6.4
CO | 16.1 | 16.1 | 16.1
CO2 | 381600 | 379200 | 385200
ESTIMATED BASE LOAD OPERATING EMISSIONS: ULTRA-LOW SULFUR FUEL OIL
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 640 | 640 | 640
SO2 | 4.8 | 4.8 | 4.9
CO | 109.4 | 109.4 | 109.4
CO2 | 508800 | 505600 | 513600
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 96 | 96 | 96
SO2 | 4.8 | 4.8 | 4.9
CO | 18.6 | 18.6 | 18.6
CO2 | 508800 | 505600 | 513600
Notes
Note 1: Capital cost assumes EPC full wrap methodology. Electrical scope ends at the high side of the GSU. Assumes gas, water, sewer, communications are available at plant fenceline.
Note 2: Simple cycle GT starts are not affected by hot, warm or cold conditions. Simple cycle starts assume purge credits are available.
Note 3: MECL start time assumes the min load at which the GT achieves the steady state NOx emissions ppm rate. The SCR compliance start time assumes a cold start, ending at the time when the catalysts are heated and the NOx levels meet the desired SCR emissions.
Note 4: Outage and availability statistics are collected using the NERC Generating Availability Data System. Simple cycle data is based on North American units that came online in 2010 or later. Reporting period is 2012-2019.
Note 5: Degraded performance assumed for all scenarios. For frame units, 3% average degradation is assumed. All performance ratings based on NATURAL GAS operation. Minimum loads are based on OEM information at requested ambient conditions.
Note 6: Assumes incoming gas pressure of 250 psig. Compression included in EPC scope. Owner's costs include 5 miles pipeline for all zones except Zone J, which assumes 1 mile. 12" pipeline for aero and F class. 16" pipeline for J class.
Note 7: Capital and fixed O&M costs are presented in 2020 USD $MM.
Note 8: FOM costs assume 7 full time personnel. FOM costs do not include engine lease fees that may be available with LTSA, depending on OEM.
Note 9: Major maintenance $/hr holds for all aero gas turbines. Major maintenance $/hr holds for frame gas turbines where hours per start is >27.
Note 10: VOM assumes the use of temporarily trailers for demineralized water treatment.
Note 11: Emissions estimates are shown for steady state operation at annual average conditions.
Note 12: Fuel Oil emissions based on ultra low sulfur diesel. Per the US EPA, this fuel must meet 15 ppm sulfur.
Note 13: Estimated Costs exclude decommisioning costs and salvage values.

## Raw_J-Class_CC
NYISO DCR TECHNOLOGY ASSESSMENT
COMBINED CYCLE 1x1 GE HA.02
PRELIMINARY AND CONFIDENTIAL - NOT FOR CONSTRUCTION
Mar 2020 - DRAFT REV 2
PROJECT ZONE: | ZONE C | ZONE F | ZONE G - Dutchess | ZONE G - Rockland | ZONE J | ZONE K
BASE PLANT DESCRIPTION | 1x1 GE HA.02 | 1x1 GE HA.02 | 1x1 GE HA.02 | 1x1 GE HA.02 | 1x1 GE HA.02 | 1x1 GE HA.02
Number of Gas Turbines | 1 | 1 | 1 | 1 | 1 | 1
Number of Steam Turbines | 1 | 1 | 1 | 1 | 1 | 1
Representative Class Gas Turbine | GE 7HA.02 | GE 7HA.02 | GE 7HA.02 | GE 7HA.02 | GE 7HA.02 | GE 7HA.02
Steam Conditions (Main Steam / Reheat) | 1,085°F / 1,085°F | 1,085°F / 1,085°F | 1,085°F / 1,085°F | 1,085°F / 1,085°F | 1,085°F / 1,085°F | 1,085°F / 1,085°F
Main Steam Pressure | 2330 | 2330 | 2330 | 2330 | 2330 | 2330
Steam Cycle Type | Subcritical | Subcritical | Subcritical | Subcritical | Subcritical | Subcritical
Startup Time, Minutes (Cold Start to Unfired Base Load) | 180 | 180 | 180 | 180 | 180 | 180
Startup Time, Minutes (Warm Start to Unfired Base Load) | 120 | 120 | 120 | 120 | 120 | 120
Startup Time, Minutes (Hot Start to Unfired Base Load) | 80 | 80 | 80 | 80 | 80 | 80
Startup Time, Minutes (Cold Start to Stack Emissions Compliance) | 60 | 60 | 60 | 60 | 60 | 60
Equivalent Forced Outage Rate Demand, % | 2.92% | 2.92% | 2.92% | 2.92% | 2.92% | 2.92%
Assumed Land Use During Operation, Acres (Not Construction Land Use) | 30 | 30 | 30 | 30 | 30 | 30
Fuel Design | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil)
Inlet Conditioning | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler
Heat Rejection | Air Cooled Condenser (ACC) | Air Cooled Condenser (ACC) | Air Cooled Condenser (ACC) | Air Cooled Condenser (ACC) | Air Cooled Condenser (ACC) | Air Cooled Condenser (ACC)
NOx Control | DLN/SCR | DLN/SCR | DLN/SCR | DLN/SCR | DLN/SCR | DLN/SCR
CO Control | Oxidation Catalyst | Oxidation Catalyst | Oxidation Catalyst | Oxidation Catalyst | Oxidation Catalyst | Oxidation Catalyst
Particulate Control | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice
Interconnection Voltage, kV | 345 | 345 | 345 | 345 | 345 | 345
Technology Rating | Mature | Mature | Mature | Mature | Mature | Mature
Permitting & Construction Schedule (Years from FNTP) | 4 | 4 | 4 | 4 | 4 | 4
ESTIMATED PERFORMANCE
Base Load Performance @ ICAP: 90 °F ¦ 70% RH (Nominal)
Net Plant Output, kW | 495100 | 498500 | 500600 | 500600 | 502200 | 502500
Net Plant Heat Rate, Btu/kWh (HHV) | 6410 | 6400 | 6400 | 6400 | 6410 | 6410
Heat Input, MMBtu/h (HHV) | 3170 | 3190 | 3200 | 3200 | 3220 | 3220
Incremental Duct Fired Performance @ ICAP: 90 °F ¦ 70% RH (Nominal)
Incremental Duct Fired Output, kW | 103800 | 104200 | 103200 | 103200 | 102900 | 107700
Incremental Heat Rate, Btu/kWh (HHV) | 8530 | 8540 | 8550 | 8550 | 8600 | 8530
Incremental Heat Input, MMBtu/h (HHV) | 890 | 890 | 880 | 880 | 880 | 920
Minimum Load (Single Turbine at MECL) @ ICAP: 90 °F ¦ 70% RH (Nominal)
Net Plant Output, kW | 221500 | 223400 | 224400 | 224400 | 225300 | 224900
Net Plant Heat Rate, Btu/kWh (HHV) | 7340 | 7320 | 7320 | 7320 | 7320 | 7340
Heat Input, MMBtu/h (HHV) | 1630 | 1640 | 1640 | 1640 | 1650 | 1650
Base Load Performance @ Winter DMNC
Net Plant Output, kW | 530000 | 532500 | 536300 | 536300 | 544900 | 542600
Net Plant Heat Rate, Btu/kWh (HHV) | 6390 | 6390 | 6390 | 6390 | 6380 | 6380
Heat Input, MMBtu/h (HHV) | 3390 | 3400 | 3430 | 3430 | 3480 | 3460
Incremental Duct Fired Performance @ Winter DMNC
Incremental Duct Fired Output, kW | 110400 | 110900 | 108800 | 108800 | 105600 | 111900
Incremental Heat Rate, Btu/kWh (HHV) | 8740 | 8740 | 8740 | 8740 | 8700 | 8730
Incremental Heat Input, MMBtu/h (HHV) | 960 | 970 | 950 | 950 | 920 | 980
Minimum Load (Single Turbine at MECL) @ Winter DMNC
Net Plant Output, kW | 196100 | 197100 | 198400 | 198400 | 200400 | 200000
Net Plant Heat Rate, Btu/kWh (HHV) | 7650 | 7650 | 7630 | 7630 | 7590 | 7620
Heat Input, MMBtu/h (HHV) | 1500 | 1510 | 1510 | 1510 | 1520 | 1520
Base Load Performance @ Winter
Net Plant Output, kW | 539200 | 542100 | 544800 | 544800 | 546700 | 547800
Net Plant Heat Rate, Btu/kWh (HHV) | 6360 | 6360 | 6350 | 6350 | 6350 | 6340
Heat Input, MMBtu/h (HHV) | 3430 | 3450 | 3460 | 3460 | 3470 | 3470
Incremental Duct Fired Performance @ Winter
Incremental Duct Fired Output, kW | 104100 | 104200 | 102700 | 102700 | 101600 | 106700
Incremental Heat Rate, Btu/kWh (HHV) | 8720 | 8720 | 8730 | 8730 | 8710 | 8730
Incremental Heat Input, MMBtu/h (HHV) | 910 | 910 | 900 | 900 | 880 | 930
Minimum Load (Single Turbine at MECL) @ Winter
Net Plant Output, kW | 197000 | 198000 | 198700 | 198700 | 199300 | 199500
Net Plant Heat Rate, Btu/kWh (HHV) | 7570 | 7560 | 7550 | 7550 | 7530 | 7540
Heat Input, MMBtu/h (HHV) | 1490 | 1500 | 1500 | 1500 | 1500 | 1500
Base Load Performance @ Spring / Fall
Net Plant Output, kW | 520400 | 532900 | 535000 | 535000 | 536800 | 537600
Net Plant Heat Rate, Btu/kWh (HHV) | 6300 | 6300 | 6300 | 6300 | 6310 | 6300
Heat Input, MMBtu/h (HHV) | 3280 | 3360 | 3370 | 3370 | 3390 | 3390
Incremental Unfired Performance with Evaporative Coolers @ Spring / Fall
Incremental Output with Evap Coolers, kW | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
Net Plant Heat Rate with Evap Coolers, Btu/kWh (HHV) | 8590 | 8580 | 8590 | 8590 | 8600 | 8580
Incremental Duct Fired Performance with Evaporative Coolers @ Spring / Fall
Incremental Duct Fired Output, kW | 99900 | 100400 | 99400 | 99400 | 99800 | 104400
Incremental Heat Rate, Btu/kWh (HHV) | 8850 | 8830 | 8830 | 8830 | 8810 | 8860
Incremental Heat Input, MMBtu/h (HHV) | 880 | 890 | 880 | 880 | 880 | 920
Minimum Load (Single Turbine at MECL) @ Spring / Fall
Net Plant Output, kW | 191500 | 192600 | 193400 | 193400 | 194500 | 194300
Net Plant Heat Rate, Btu/kWh (HHV) | 7540 | 7540 | 7530 | 7530 | 7530 | 7540
Heat Input, MMBtu/h (HHV) | 1440 | 1450 | 1460 | 1460 | 1460 | 1470
Base Load Performance @ Summer
Net Plant Output, kW | 509900 | 513300 | 514700 | 514700 | 512300 | 517900
Net Plant Heat Rate, Btu/kWh (HHV) | 6370 | 6360 | 6360 | 6360 | 6370 | 6370
Heat Input, MMBtu/h (HHV) | 3250 | 3260 | 3270 | 3270 | 3260 | 3300
Incremental Duct Fired Performance @ Summer
Incremental Duct Fired Output, kW | 103100 | 103000 | 102200 | 102200 | 103600 | 107200
Incremental Heat Rate, Btu/kWh (HHV) | 8580 | 8610 | 8590 | 8590 | 8600 | 8590
Incremental Heat Input, MMBtu/h (HHV) | 880 | 890 | 880 | 880 | 890 | 920
Minimum Load (Single Turbine at MECL) @ Summer
Net Plant Output, kW | 232100 | 233400 | 234000 | 234000 | 232300 | 235700
Net Plant Heat Rate, Btu/kWh (HHV) | 7130 | 7130 | 7130 | 7130 | 7180 | 7130
Heat Input, MMBtu/h (HHV) | 1650 | 1660 | 1670 | 1670 | 1670 | 1680
Base Load Performance @ Summer DMNC
Net Plant Output, kW | 486000 | 488300 | 486500 | 486500 | 484700 | 501600
Net Plant Heat Rate, Btu/kWh (HHV) | 6410 | 6410 | 6410 | 6410 | 6440 | 6400
Heat Input, MMBtu/h (HHV) | 3120 | 3130 | 3120 | 3120 | 3120 | 3210
Incremental Unfired Performance with Evaporative Coolers @ Summer DMNC
Incremental Output with Evap Coolers, kW | 28200 | 28200 | 33000 | 33000 | 35300 | 19100
Incremental Heat Rate with Evap Coolers, Btu/kWh (HHV) | 6590 | 6640 | 6400 | 6400 | 6600 | 6420
Incremental Fired Performance with Evaporative Coolers @ Summer DMNC
Incremental Output with Evap Coolers, kW | 100400 | 100300 | 99700 | 99700 | 98900 | 104600
Incremental Heat Rate with Evap Coolers, Btu/kWh (HHV) | 8660 | 8650 | 8640 | 8640 | 8770 | 8590
Incremental Heat Input, MMBtu/h (HHV) | 870 | 870 | 860 | 860 | 870 | 900
Minimum Load (Single Turbine at MECL) @ Summer DMNC
Net Plant Output, kW | 216900 | 218300 | 217400 | 217400 | 216500 | 224300
Net Plant Heat Rate, Btu/kWh (HHV) | 7370 | 7350 | 7370 | 7370 | 7400 | 7330
Heat Input, MMBtu/h (HHV) | 1600 | 1600 | 1600 | 1600 | 1600 | 1640
ESTIMATED STARTUP FUEL USAGE
Start to Unfired Base Load, MMBtu (WARM Start) | 3940 | 3940 | 3940 | 3940 | 3940 | 3940
ESTIMATED CAPITAL AND O&M COSTS
EPC Project Capital Costs, 2020 MM$ (w/o Owner's Costs) | 537.01 | 549.56 | 567.61 | 610.14 | 692.83 | 686.83
Labor | 201.088 | 205.7875 | 212.5465 | 228.4722 | 259.4362 | 257.1894
Materials | 117.7157 | 120.4668 | 124.4234 | 133.7463 | 151.8724 | 150.5572
Turbines or Batteries | 94.2391 | 96.4415 | 99.6091 | 107.0726 | 121.5838 | 120.5308
Other | 123.9671 | 126.8642 | 131.031 | 140.8489 | 159.9377 | 158.5526
Owner's Cost Allowances, 2020 MM$ | 119.91 | 120.59 | 121.58 | 124.86 | 180.14 | 131.04
Owner's Project Development | 3.5 | 3.5 | 3.5 | 3.5 | 4.55 | 3.85
Owner's Operational Personnel Prior to COD | 2.4 | 2.4 | 2.4 | 2.4 | 3.12 | 2.64
Owner's Engineer | 2.6 | 2.6 | 2.6 | 2.6 | 3.38 | 2.86
Owner's Project Management | 4.8 | 4.8 | 4.8 | 4.8 | 6.24 | 5.28
Owner's Legal Costs | 1 | 1 | 1 | 1 | 1.3 | 1.1
Owner's Start-up Engineering and Commissioning | 0.54 | 0.54 | 0.54 | 0.54 | 0.7 | 0.59
Sales Tax | 0 | 0 | 0 | 0 | 0 | 0
Construction Power and Water | 1.54 | 1.54 | 1.54 | 1.54 | 2 | 1.69
Permitting and Licensing Fees | 1 | 1 | 1 | 1 | 1.3 | 1.1
Switchyard | 18.94 | 18.94 | 18.94 | 18.94 | 61.59 | 18.94
Electrical Interconnection and Deliverability | 11 | 11 | 11 | 11 | 11 | 11
Gas Interconnection and Reinforcement | 17.9 | 17.9 | 17.9 | 17.9 | 17.9 | 17.9
System Deliverability Upgrade Costs
Emission Reduction Credits | 0.2 | 0.2 | 0.2 | 1.1 | 1.1 | 1.1
Political Concessions & Area Development Fees | 0.5 | 0.5 | 0.5 | 0.5 | 0.65 | 0.55
Startup/Testing (Fuel & Consumables) | 5.45 | 5.45 | 5.45 | 5.45 | 5.45 | 5.45
Initial Fuel Inventory | 7.24 | 7.24 | 7.24 | 7.24 | 7.24 | 7.24
Site Security | 1.1 | 1.1 | 1.1 | 1.1 | 1.43 | 1.21
Operating Spare Parts | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Builders Risk Insurance (0.45% of Construction Costs) | 2.42 | 2.47 | 2.55 | 2.75 | 3.12 | 3.09
Owner's Contingency (5% for Screening Purposes) | 31.28 | 31.91 | 32.82 | 35 | 41.57 | 38.95
AFUDC, 2020 MM$ | 45.9844 | 46.9105 | 48.2433 | 51.45 | 61.1079 | 57.2509
EPC Portion | 37.5907 | 38.4692 | 39.7327 | 42.7098 | 48.4981 | 48.0781
Non-EPC Portion | 8.3937 | 8.4413 | 8.5106 | 8.7402 | 12.6098 | 9.1728
Total Project Costs, 2020 MM$ | 702.9044 | 717.0605 | 737.4333 | 786.45 | 934.0779 | 875.1209
EPC Cost Per UNFIRED kW, 2020 $/kW (Based on ICAP kW) | 1080 | 1100 | 1130 | 1220 | 1380 | 1370
Total Cost Per UNFIRED kW, 2020 $/kW (Based on ICAP kW) | 1420 | 1440 | 1470 | 1570 | 1860 | 1740
EPC Cost Per FIRED kW, 2020 $/kW (Based on ICAP kW) | 900 | 910 | 940 | 1010 | 1140 | 1130
Total Cost Per FIRED kW, 2020 $/kW (Based on ICAP kW) | 1170 | 1190 | 1220 | 1300 | 1540 | 1430
FIXED O&M COSTS
Fixed O&M Cost - LABOR, 2020$MM/Yr | 2.8286 | 3.1429 | 4.0857 | 4.0857 | 5.3429 | 4.7143
Fixed O&M Cost - OTHER, 2020$MM/Yr | 2.14 | 2.14 | 2.14 | 2.14 | 2.14 | 2.14
Site Leasing Allowance, 2020$/MM/Yr | 0.66 | 0.66 | 0.66 | 0.66 | 8.1 | 0.78
Property Insurance Allowance, 2020$MM/Yr | 3.2221 | 3.2974 | 3.4057 | 3.6608 | 4.157 | 4.121
FIXED O&M COSTS - DUAL FUEL
Fixed O&M Cost - LABOR, 2020$MM/Yr | 2.8286 | 3.1429 | 4.0857 | 4.0857 | 5.3429 | 4.7143
Fixed O&M Cost - OTHER, 2020$MM/Yr | 2.14 | 2.14 | 2.14 | 2.14 | 2.14 | 2.14
Site Leasing Allowance, 2020$MM/Yr | 0.66 | 0.66 | 0.66 | 0.66 | 8.1 | 0.78
Property Insurance Allowance, 2020$MM/Yr | 3.2221 | 3.2974 | 3.4057 | 3.6608 | 4.157 | 4.121
LEVELIZED CAPITAL MAINTENANCE COSTS
Major Maintenance Cost, 2020 $/GT-hr | 600 | 600 | 600 | 600 | 600 | 600
Major Maintenance Cost, 2020$/GT-start | 16200 | 16200 | 16200 | 16200 | 16200 | 16200
Major Maintenance Cost, 2020 $/MWh | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - GAS OPERATION
Total Variable O&M Cost, 2020 $/MWh | 1.55 | 1.55 | 1.55 | 1.55 | 1.57 | 1.54
Water Related O&M ($/MWh) | 0.01 | 0.01 | 0.01 | 0.01 | 0.03 | 0.01
SCR Related Costs, $/MWh | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
Other Consumables and Variable O&M ($/MWh) | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.21
Incremental Duct Fired Variable O&M, 2020 $/MWh (excl. GT major maint.) | 0.6 | 0.6 | 0.6 | 0.6 | 0.6 | 0.6
Water Related O&M ($/MWh) | 0.03 | 0.03 | 0.03 | 0.03 | 0.06 | 0.03
SCR Reagent, $/MWh | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13
Other Consumables and Variable O&M ($/MWh) | 0.44 | 0.44 | 0.44 | 0.44 | 0.41 | 0.44
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - FUEL OIL OPERATION
Total Variable O&M Cost, 2020 $/MWh | 1.7 | 1.7 | 1.7 | 1.7 | 2.09 | 1.73
Water Related O&M ($/MWh) | 0 | 0 | 0 | 0 | 0.4 | 0.03
SCR Related Costs, $/MWh | 0.5 | 0.5 | 0.5 | 0.5 | 0.46 | 0.48
Other Consumables and Variable O&M ($/MWh) | 1.2 | 1.2 | 1.2 | 1.2 | 1.23 | 1.22
Incremental Duct Fired Variable O&M, 2020 $/MWh (excl. GT major maint.) | N/A | N/A | N/A | N/A | N/A | N/A
Water Related O&M ($/MWh) | N/A | N/A | N/A | N/A | N/A | N/A
SCR Reagent, $/MWh | N/A | N/A | N/A | N/A | N/A | N/A
Other Consumables and Variable O&M ($/MWh) | N/A | N/A | N/A | N/A | N/A | N/A
CAPITAL COST DEDUCT FOR GAS ONLY
Capital Costs, 2020 MM$ | -25.4 | -25.4 | -25.4 | -25.4 | -30.2 | -30.2
Owner's Costs, 2020 MM$ | -3.8 | -3.9 | -3.9 | -4.1 | -4.8 | -4.7
ESTIMATED BASE LOAD OPERATING EMISSIONS, lb/MMBtu (HHV)
NOX | 26.4 | 26.4 | 26.4 | 26.4 | 26.4 | 26.4
SO2 | 6.6 | 6.7 | 6.7 | 6.7 | 6.8 | 6.8
CO | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1
CO2 | 393600 | 403200 | 404400 | 404400 | 406800 | 406800
ESTIMATED BASE LOAD OPERATING EMISSIONS: ULTRA-LOW SULFUR FUEL OIL
NOX | 96 | 96 | 96 | 96 | 96 | 96
SO2 | 5.2 | 5.1 | 5.2 | 5.2 | 5.2 | 5.2
CO | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6
CO2 | 544000 | 540800 | 542400 | 542400 | 545600 | 545600
Notes
Note 1: Capital cost assumes EPC full wrap methodology. Electrical scope ends at the high side of the GSU. Assumes gas, water, sewer, communications are available at plant fenceline. CCGT unit includes duct firing capability.
Note 2: Performance ratings were determined using heat balance modeling software. Performance is based on 1.8% average degradation for capacity and 1.1% average degradation for heat rate. All performance is based on NATURAL GAS operation. Min load ratings are based on OEM performance information at specified ambient conditions.
Note 3: Variable O&M costs are based on performance at annual average conditions.
Note 4: Capital and fixed O&M costs are presented in 2020 USD $MM.
Note 5: Major maintenance $/hr holds for frame gas turbines where hours per start is >27.
Note 6: The duct firing incremental values note incremental performance output. The incremental heat rate reflects the effective heat rate of the additional output due to the duct burners.
Note 7: Startup time to stack emissions compliance is not the same as the start time for gas turbine MECL. Stack emissions compliance is expected to be limited by the temperature of the CO catalyst, which impacts VOC emissions.
Note 8: Outage and availability statistics are collected using the NERC Generating Availability Data System. Combined cycle data is based on North American units that came online in 2010 or later. Reporting period is 2012-2019.
Note 9: Cold start is >72 hours after shutdown. Hot start is <8 hours after shutdown.
Note 10: Startup times reflect unrestricted, conventional starts for all gas turbines. These start times assume the inclusion of terminal point desuperheaters, full bypass, and associated controls. Fast start packages are not included in CCGT plants.
Note 14: Fixed O&M assumes 22 FTE for a 1x1 configuration.
Note 15: Variable O&M costs assume onsite demineralized water treatment system (included in EPC cost).
Note 16: Emissions estimates are shown for steady state operation at annual average conditions. Estimates account for the impacts of SCR and CO catalysts.
Note 17: Estimated costs exclude decommisioning costs and salvage values.

## SCR_Limits
Greenfield Site Control Requirements in New York ISO
Technology | Load Zone
| K |  | G |  |  |  | F |  | C
| Severe |  | Severe |  | Moderate |  | Moderate |  | Moderate
| SCR Needed? | Oxidation Catalyst Needed? | SCR Needed? | Oxidation Catalyst Needed? | SCR Needed? | Oxidation Catalyst Needed? | SCR Needed? | Oxidation Catalyst Needed? | SCR Needed? | Oxidation Catalyst Needed?
Siemens SGT-A65 (Trent) | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
GE 7F.05 | Yes | No | Yes | No | Yes | No | Yes | No | Yes | No
GE 7HA.02 15 ppm NOx | Yes | No | Yes | No | Yes | No | Yes | No | Yes | No
GE 7HA.02 25 ppm NOx | Yes | No | Yes | No | Yes | No | Yes | No | Yes | No
1x1 7HA.02 | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes
Values shown are for maximum annual hours of operation (3,066 hours for SCGT technologies and 8,760 for CCGT technology). For dual fuel SCGT, the evaluation considers 720 hours operating on ultra-low sulfur fuel oil and the remaining 2,346 hours on gas. For dual fuel CCGT, evaluation considers 720 hours operating on ultra-low sulfur fuel oil and the remaining 8,040 hours on gas.
For gas only operation, the SCR and oxidation catalyst results above do not change.
**Ox Cat based on BACT for CO
Existing Major Source Site Control Requirements in New York ISO
Technology | Load Zone
J
Severe
| SCR Needed? | Oxidation Catalyst Needed?
Siemens SGT-A65 (Trent) | Yes | Yes
GE 7F.05 | Yes | No
GE 7HA.02 15 ppm NOx | Yes | No
GE 7HA.02 25 ppm NOx | Yes | No
1x1 7HA.02 | Yes | Yes
Values listed here are for maximum annual hours of operation on natural gas (2,346 hours/year for SCGT technologies, 8,040 hours/year for CCGT techology) and ultra low sulfur diesel (720 hrs/year for all technologies )
SCR and CO requirements are not expected to change if there are zero fuel oil hours.
**Ox Cat based on BACT for CO
Operating Limits Needed to Not Require SCR Using Natural Gas Only at Greenfield Site
Technology | Load Zone
| K | J | G |  | F | C
| Severe | Severe | Severe | Moderate | Moderate | Moderate
Hours Limit to not need SCR
Siemens SGT-A65 (Trent) | 295 | 295 | 295 | 1195 | 1195 | 1195
GE 7F.05 | 620 | 620 | 620 | 2500 | 2500 | 2500
GE 7HA.02 15 ppm NOx | 260 | 260 | 260 | 1055 | 1055 | 1055
GE 7HA.02 25 ppm NOx | N/A2 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2
1x1 7HA.02 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2
(1) These values are for the analyzed project (i.e., the SGT-A65 limit is for all three engines combined, each year)
(2) SCR is required for these units per the NSPS KKKK rule
Operating Limits Needed to Not Require SCR Using ULSD Only at Greenfield Site
Technology | Load Zone
| K | J | G |  | F | C
| Severe | Severe | Severe | Moderate | Moderate | Moderate
Hours Limit to not need SCR
Siemens SGT-A65 (Trent) | 176.6667 | 176.6667 | 176.6667 | 716.6667 | 716.6667 | 716.6667
GE 7F.05 | 115 | 115 | 115 | 465 | 465 | 465
GE 7HA.02 15 ppm NOx | 78 | 78 | 78 | 312 | 312 | 312
GE 7HA.02 25 ppm NOx | N/A2 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2
1x1 7HA.02 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2 | N/A2
(1) These values are for the analyzed project (i.e., the SGT-A65 limit is for all three engines combined, each year)
(2) SCR is required for these units per the NSPS KKKK rule