## gen_params_CTs_reserves
ns10min_aero | ns10min_f | ns10min_j25 | ns10min_j15
Yes | No | Yes | Yes

## CTs_runtimes_scr
rt_limit_aero_scr | rt_limit_j25_scr | rt_limit_j15_scr | rt_limit_f_scr | rt_limit_ccj_scr
3066 | 3066 | 3066 | 3066 | 8760

## nox_limits
Area | NOx.Limit
C | 200000
F | 200000
G1 | 200000
G2 | 50000
J | 50000
K | 50000

## tech_params_aero
AREA | TECH_PARAMS | HR_SUM_AERO | HR_WIN_AERO | VOC_NG_AERO | VOC_OIL_AERO | CAP_SUM_AERO | CAP_WIN_AERO | MM_COST_AERO | STARTUP_FUEL_AERO | STARTUP_MM_AERO | NOX_NG_SUM_AERO | SO2_NG_SUM_AERO | CO2_NG_SUM_AERO | NOX_NG_WIN_AERO | SO2_NG_WIN_AERO | CO2_NG_WIN_AERO | NOX_OIL_SUM_AERO | SO2_OIL_SUM_AERO | CO2_OIL_SUM_AERO | NOX_OIL_WIN_AERO | SO2_OIL_WIN_AERO | CO2_OIL_WIN_AERO | EFORd_AERO
K | K - Long Island | 9670 | 9450 | 9.74 | 9.81 | 166.6 | 188.2 | 570 | 100 | 0 | 13.653 | 3.5929 | 214341.4013 | 13.3424 | 3.5111 | 209464.9682 | 42.8067 | 2.669 | 285788.535 | 41.8328 | 2.6083 | 279286.6242 | 0.8997
J | J - NYC | 9670 | 9460 | 10.19 | 10.23 | 166.5 | 188.2 | 570 | 100 | 0 | 13.653 | 3.5929 | 214341.4013 | 13.3565 | 3.5149 | 209686.6242 | 42.8067 | 2.669 | 285788.535 | 41.8771 | 2.611 | 279582.1656 | 0.8997
G1 | G - LHV (Dutchess) | 9670 | 9440 | 9.87 | 9.92 | 166.5 | 188.2 | 570 | 100 | 0 | 13.6385 | 3.5891 | 214114.1039 | 13.3141 | 3.5037 | 209021.421 | 42.7613 | 2.6662 | 285485.4719 | 41.7442 | 2.6028 | 278695.228 | 0.8997
G2 | G - LHV (Rockland) | 9670 | 9440 | 9.87 | 9.92 | 166.5 | 188.2 | 570 | 100 | 0 | 13.6385 | 3.5891 | 214114.1039 | 13.3141 | 3.5037 | 209021.421 | 42.7613 | 2.6662 | 285485.4719 | 41.7442 | 2.6028 | 278695.228 | 0.8997
F | F - Capital | 9660 | 9440 | 9.97 | 10.02 | 166.7 | 188.2 | 570 | 100 | 0 | 13.6244 | 3.5854 | 213892.6829 | 13.3141 | 3.5037 | 209021.421 | 42.7171 | 2.6634 | 285190.2439 | 41.7442 | 2.6028 | 278695.228 | 0.8997
C | C - Central | 9670 | 9440 | 10.09 | 10.12 | 166.7 | 188.2 | 570 | 100 | 0 | 13.6385 | 3.5891 | 214114.1039 | 13.3141 | 3.5037 | 209021.421 | 42.7613 | 2.6662 | 285485.4719 | 41.7442 | 2.6028 | 278695.228 | 0.8997

## tech_params_aero_noscr
AREA | TECH_PARAMS | HR_SUM_AERO | HR_WIN_AERO | VOC_NG_AERO | VOC_OIL_AERO | CAP_SUM_AERO | CAP_WIN_AERO | MM_COST_AERO | STARTUP_FUEL_AERO | STARTUP_MM_AERO | NOX_NG_SUM_AERO | SO2_NG_SUM_AERO | CO2_NG_SUM_AERO | NOX_NG_WIN_AERO | SO2_NG_WIN_AERO | CO2_NG_WIN_AERO | NOX_OIL_SUM_AERO | SO2_OIL_SUM_AERO | CO2_OIL_SUM_AERO | NOX_OIL_WIN_AERO | SO2_OIL_WIN_AERO | CO2_OIL_WIN_AERO | EFORd_AERO
K | K - Long Island | 9670 | 9450 | 8.91 | 8.78 | 166.6 | 188.2 | 570 | 100 | 0 | 171.2268 | 3.5929 | 214341.4013 | 167.3312 | 3.5111 | 209464.9682 | 285.3779 | 2.669 | 285788.535 | 278.8854 | 2.6083 | 279286.6242 | 0.8997
J | J - NYC | 9670 | 9460 | 9.36 | 9.2 | 166.5 | 188.2 | 570 | 100 | 0 | 171.2268 | 3.5929 | 214341.4013 | 167.5083 | 3.5149 | 209686.6242 | 285.3779 | 2.669 | 285788.535 | 279.1805 | 2.611 | 279582.1656 | 0.8997
G1 | G - LHV (Dutchess) | 9670 | 9440 | 9.04 | 8.92 | 166.5 | 188.2 | 570 | 100 | 0 | 171.0452 | 3.5891 | 214114.1039 | 166.9769 | 3.5037 | 209021.421 | 285.0753 | 2.6662 | 285485.4719 | 278.2948 | 2.6028 | 278695.228 | 0.8997
G2 | G - LHV (Rockland) | 9670 | 9440 | 9.04 | 8.92 | 166.5 | 188.2 | 570 | 100 | 0 | 171.0452 | 3.5891 | 214114.1039 | 166.9769 | 3.5037 | 209021.421 | 285.0753 | 2.6662 | 285485.4719 | 278.2948 | 2.6028 | 278695.228 | 0.8997
F | F - Capital | 9660 | 9440 | 9.14 | 9.02 | 166.7 | 188.2 | 570 | 100 | 0 | 170.8683 | 3.5854 | 213892.6829 | 166.9769 | 3.5037 | 209021.421 | 284.7805 | 2.6634 | 285190.2439 | 278.2948 | 2.6028 | 278695.228 | 0.8997
C | C - Central | 9670 | 9440 | 9.27 | 9.12 | 166.7 | 188.2 | 570 | 100 | 0 | 171.0452 | 3.5891 | 214114.1039 | 166.9769 | 3.5037 | 209021.421 | 285.0753 | 2.6662 | 285485.4719 | 278.2948 | 2.6028 | 278695.228 | 0.8997

## tech_params_f
AREA | TECH_PARAMS | HR_SUM_F | HR_WIN_F | VOC_NG_F | VOC_OIL_F | CAP_SUM_F | CAP_WIN_F | STARTUP_FUEL_F | STARTUP_MM_F | NOX_NG_SUM_F | SO2_NG_SUM_F | CO2_NG_SUM_F | NOX_NG_WIN_F | SO2_NG_WIN_F | CO2_NG_WIN_F | NOX_OIL_SUM_F | SO2_OIL_SUM_F | CO2_OIL_SUM_F | NOX_OIL_WIN_F | SO2_OIL_WIN_F | CO2_OIL_WIN_F | EFORd_F
K | K - Long Island | 10200 | 9890 | 1.52 | 8.83 | 218 | 227.2 | 325 | 9500 | 17.8701 | 4.6181 | 277086.6142 | 17.327 | 4.4778 | 268665.3543 | 64.7539 | 3.5138 | 369448.8189 | 62.7859 | 3.407 | 358220.4724 | 0.9566
J | J - NYC | 10210 | 9900 | 1.54 | 9.21 | 217.8 | 226.9 | 325 | 9500 | 17.8876 | 4.6226 | 277358.2677 | 17.3445 | 4.4823 | 268937.0079 | 64.8174 | 3.5172 | 369811.0236 | 62.8494 | 3.4104 | 358582.6772 | 0.9566
G1 | G - LHV (Dutchess) | 10200 | 9890 | 1.52 | 8.84 | 217 | 226.5 | 325 | 9500 | 17.8701 | 4.6181 | 274677.1654 | 17.327 | 4.4778 | 266329.1339 | 64.7539 | 3.5138 | 366236.2205 | 62.7859 | 3.407 | 355105.5118 | 0.9566
G2 | G - LHV (Rockland) | 10200 | 9890 | 1.52 | 8.84 | 217 | 226.5 | 325 | 9500 | 17.8701 | 4.6181 | 274677.1654 | 17.327 | 4.4778 | 266329.1339 | 64.7539 | 3.5138 | 366236.2205 | 62.7859 | 3.407 | 355105.5118 | 0.9566
F | F - Capital | 10180 | 9880 | 1.52 | 8.84 | 217 | 225.9 | 325 | 9500 | 17.835 | 4.5089 | 272936.2205 | 17.3094 | 4.376 | 264892.9134 | 64.627 | 3.5069 | 363914.9606 | 62.7224 | 3.4035 | 353190.5512 | 0.9566
C | C - Central | 10180 | 9880 | 1.52 | 8.84 | 215.8 | 224.9 | 325 | 9500 | 17.835 | 4.5089 | 271733.8583 | 17.3094 | 4.376 | 263725.9843 | 64.627 | 3.4067 | 362311.811 | 62.7224 | 3.3063 | 351634.6457 | 0.9566

## tech_params_f_noscr
AREA | TECH_PARAMS | HR_SUM_F | HR_WIN_F | VOC_NG_F | VOC_OIL_F | CAP_SUM_F | CAP_WIN_F | STARTUP_FUEL_F | STARTUP_MM_F | NOX_NG_SUM_F | SO2_NG_SUM_F | CO2_NG_SUM_F | NOX_NG_WIN_F | SO2_NG_WIN_F | CO2_NG_WIN_F | NOX_OIL_SUM_F | SO2_OIL_SUM_F | CO2_OIL_SUM_F | NOX_OIL_WIN_F | SO2_OIL_WIN_F | CO2_OIL_WIN_F | EFORd_F
K | K - Long Island | 10200 | 9890 | 0.95 | 8.04 | 218 | 227.2 | 325 | 9500 | 80.2146 | 4.6181 | 277086.6142 | 77.7767 | 4.4778 | 268665.3543 | 431.6929 | 3.5138 | 369448.8189 | 418.5728 | 3.407 | 358220.4724 | 0.9566
J | J - NYC | 10210 | 9900 | 0.97 | 8.42 | 217.8 | 226.9 | 325 | 9500 | 80.2932 | 4.6226 | 277358.2677 | 77.8553 | 4.4823 | 268937.0079 | 432.1161 | 3.5172 | 369811.0236 | 418.9961 | 3.4104 | 358582.6772 | 0.9566
G1 | G - LHV (Dutchess) | 10200 | 9890 | 0.94 | 8.04 | 217 | 226.5 | 325 | 9500 | 80.2146 | 4.6181 | 274677.1654 | 77.7767 | 4.4778 | 266329.1339 | 431.6929 | 3.5138 | 366236.2205 | 418.5728 | 3.407 | 355105.5118 | 0.9566
G2 | G - LHV (Rockland) | 10200 | 9890 | 0.94 | 8.04 | 217 | 226.5 | 325 | 9500 | 80.2146 | 4.6181 | 274677.1654 | 77.7767 | 4.4778 | 266329.1339 | 431.6929 | 3.5138 | 366236.2205 | 418.5728 | 3.407 | 355105.5118 | 0.9566
F | F - Capital | 10180 | 9880 | 0.94 | 8.04 | 217 | 225.9 | 325 | 9500 | 80.0573 | 4.5089 | 272936.2205 | 77.698 | 4.376 | 264892.9134 | 430.8465 | 3.5069 | 363914.9606 | 418.1496 | 3.4035 | 353190.5512 | 0.9566
C | C - Central | 10180 | 9880 | 0.94 | 8.04 | 215.8 | 224.9 | 325 | 9500 | 80.0573 | 4.5089 | 271733.8583 | 77.698 | 4.376 | 263725.9843 | 430.8465 | 3.4067 | 362311.811 | 418.1496 | 3.3063 | 351634.6457 | 0.9566

## tech_params_j25
AREA | TECH_PARAMS | HR_SUM_J25 | HR_WIN_J25 | VOC_NG_J25 | VOC_OIL_J25 | CAP_SUM_J25 | CAP_WIN_J25 | STARTUP_FUEL_J25 | STARTUP_MM_J25 | NOX_NG_SUM_J25 | SO2_NG_SUM_J25 | CO2_NG_SUM_J25 | NOX_NG_WIN_J25 | SO2_NG_WIN_J25 | CO2_NG_WIN_J25 | NOX_OIL_SUM_J25 | SO2_OIL_SUM_J25 | CO2_OIL_SUM_J25 | NOX_OIL_WIN_J25 | SO2_OIL_WIN_J25 | CO2_OIL_WIN_J25 | EFORd_J25
K | K - Long Island | 9370 | 9300 | 1.39 | 10.93 | 359 | 371.1 | 490 | 26600 | 26.4848 | 6.9222 | 415329.7645 | 26.2869 | 6.8704 | 412226.9807 | 96.3084 | 5.317 | 553773.0193 | 95.5889 | 5.2773 | 549635.9743 | 0.9566
J | J - NYC | 9370 | 9300 | 1.43 | 11.46 | 358.7 | 370.2 | 490 | 26600 | 26.4848 | 6.9222 | 415329.7645 | 26.2869 | 6.8704 | 412226.9807 | 96.3084 | 5.317 | 553773.0193 | 95.5889 | 5.2773 | 549635.9743 | 0.9566
G1 | G - LHV (Dutchess) | 9360 | 9300 | 1.39 | 10.93 | 357.4 | 370.2 | 490 | 26600 | 26.4565 | 6.9148 | 412481.3704 | 26.2869 | 6.8704 | 409837.2591 | 96.2056 | 5.2111 | 549975.1606 | 95.5889 | 5.1777 | 546449.6788 | 0.9566
G2 | G - LHV (Rockland) | 9360 | 9300 | 1.39 | 10.93 | 357.4 | 370.2 | 490 | 26600 | 26.4565 | 6.9148 | 412481.3704 | 26.2869 | 6.8704 | 409837.2591 | 96.2056 | 5.2111 | 549975.1606 | 95.5889 | 5.1777 | 546449.6788 | 0.9566
F | F - Capital | 9350 | 9290 | 1.39 | 10.91 | 357.7 | 369.2 | 490 | 26600 | 26.4283 | 6.8073 | 410839.4004 | 26.2587 | 6.7636 | 408202.9979 | 96.1028 | 5.2056 | 547785.8672 | 95.4861 | 5.1722 | 544270.6638 | 0.9566
C | C - Central | 9350 | 9280 | 1.4 | 10.91 | 355.6 | 367.4 | 490 | 26600 | 26.4283 | 6.8073 | 408436.8308 | 26.2304 | 6.7563 | 405379.015 | 96.1028 | 5.2056 | 544582.4411 | 95.3833 | 5.1666 | 540505.3533 | 0.9566

## tech_params_j25_noscr
AREA | TECH_PARAMS | HR_SUM_J25 | HR_WIN_J25 | VOC_NG_J25 | VOC_OIL_J25 | CAP_SUM_J25 | CAP_WIN_J25 | STARTUP_FUEL_J25 | STARTUP_MM_J25 | NOX_NG_SUM_J25 | SO2_NG_SUM_J25 | CO2_NG_SUM_J25 | NOX_NG_WIN_J25 | SO2_NG_WIN_J25 | CO2_NG_WIN_J25 | NOX_OIL_SUM_J25 | SO2_OIL_SUM_J25 | CO2_OIL_SUM_J25 | NOX_OIL_WIN_J25 | SO2_OIL_WIN_J25 | CO2_OIL_WIN_J25 | EFORd_J25
K | K - Long Island | 9370 | 9300 | 0.93 | 10.23 | 359 | 371.1 | 490 | 26600 | 331.5616 | 6.9222 | 415329.7645 | 329.0846 | 6.8704 | 412226.9807 | 642.0557 | 5.317 | 553773.0193 | 637.2591 | 5.2773 | 549635.9743 | 0.9566
J | J - NYC | 9370 | 9300 | 0.95 | 10.76 | 358.7 | 370.2 | 490 | 26600 | 331.5616 | 6.9222 | 415329.7645 | 329.0846 | 6.8704 | 412226.9807 | 642.0557 | 5.317 | 553773.0193 | 637.2591 | 5.2773 | 549635.9743 | 0.9566
G1 | G - LHV (Dutchess) | 9360 | 9300 | 0.93 | 10.23 | 357.4 | 370.2 | 490 | 26600 | 331.2077 | 6.9148 | 412481.3704 | 329.0846 | 6.8704 | 409837.2591 | 641.3704 | 5.2111 | 549975.1606 | 637.2591 | 5.1777 | 546449.6788 | 0.9566
G2 | G - LHV (Rockland) | 9360 | 9300 | 0.93 | 10.23 | 357.4 | 370.2 | 490 | 26600 | 331.2077 | 6.9148 | 412481.3704 | 329.0846 | 6.8704 | 409837.2591 | 641.3704 | 5.2111 | 549975.1606 | 637.2591 | 5.1777 | 546449.6788 | 0.9566
F | F - Capital | 9350 | 9290 | 0.93 | 10.21 | 357.7 | 369.2 | 490 | 26600 | 330.8539 | 6.8073 | 410839.4004 | 328.7307 | 6.7636 | 408202.9979 | 640.6852 | 5.2056 | 547785.8672 | 636.5739 | 5.1722 | 544270.6638 | 0.9566
C | C - Central | 9350 | 9280 | 0.93 | 10.21 | 355.6 | 367.4 | 490 | 26600 | 330.8539 | 6.8073 | 408436.8308 | 328.3769 | 6.7563 | 405379.015 | 640.6852 | 5.2056 | 544582.4411 | 635.8887 | 5.1666 | 540505.3533 | 0.9566

## tech_params_j15_noscr
AREA | TECH_PARAMS | HR_SUM_J15 | HR_WIN_J15 | VOC_NG_J15 | VOC_OIL_J15 | CAP_SUM_J15 | CAP_WIN_J15 | STARTUP_FUEL_J15 | STARTUP_MM_J15 | NOX_NG_SUM_J15 | SO2_NG_SUM_J15 | CO2_NG_SUM_J15 | NOX_NG_WIN_J15 | SO2_NG_WIN_J15 | CO2_NG_WIN_J15 | NOX_OIL_SUM_J15 | SO2_OIL_SUM_J15 | CO2_OIL_SUM_J15 | NOX_OIL_WIN_J15 | SO2_OIL_WIN_J15 | CO2_OIL_WIN_J15 | EFORd_J15
G1 | G - LHV (Dutchess) | 9390 | 9340 | 0.93 | 10.21 | 340.9 | 350.5 | 490 | 26600 | 189.6096 | 6.4343 | 387262.0985 | 188.6 | 6.4 | 385200 | 643.4261 | 4.9262 | 516349.4647 | 640 | 4.9 | 513600 | 0.9566
F | F - Capital | 9390 | 9320 | 0.93 | 10.21 | 341.2 | 351 | 490 | 26600 | 189.4068 | 6.4274 | 385642.7807 | 187.9949 | 6.3795 | 382767.9144 | 642.738 | 4.921 | 514190.3743 | 637.9465 | 4.8843 | 510357.2193 | 0.9566
C | C - Central | 9370 | 9320 | 0.93 | 10.21 | 338 | 346.1 | 490 | 26600 | 189.2058 | 6.4206 | 382825.6959 | 188.1961 | 6.3863 | 380782.8694 | 642.0557 | 4.8154 | 510434.2612 | 638.6296 | 4.7897 | 507710.4925 | 0.9566

## tech_params_ccj
AREA | TECH_PARAMS | HR_SUM_CCJ | HR_WIN_CCJ | VOC_NG_CCJ | VOC_OIL_CCJ | CAP_SUM_CCJ | CAP_WIN_CCJ | MM_COST_CCJ | STARTUP_FUEL_CCJ | STARTUP_MM_CCJ | NOX_NG_SUM_CCJ | SO2_NG_SUM_CCJ | CO2_NG_SUM_CCJ | NOX_NG_WIN_CCJ | SO2_NG_WIN_CCJ | CO2_NG_WIN_CCJ | NOX_OIL_SUM_CCJ | SO2_OIL_SUM_CCJ | CO2_OIL_SUM_CCJ | NOX_OIL_WIN_CCJ | SO2_OIL_WIN_CCJ | CO2_OIL_WIN_CCJ | EFORd_CCJ | HR_SUM_MIN_CCJ | HR_WIN_MIN_CCJ | NOX_NG_SUM_MIN_CCJ | SO2_NG_SUM_MIN_CCJ | CO2_NG_SUM_MIN_CCJ | NOX_NG_WIN_MIN_CCJ | SO2_NG_WIN_MIN_CCJ | CO2_NG_WIN_MIN_CCJ | NOX_OIL_SUM_MIN_CCJ | SO2_OIL_SUM_MIN_CCJ | CO2_OIL_SUM_MIN_CCJ | NOX_OIL_WIN_MIN_CCJ | SO2_OIL_WIN_MIN_CCJ | CO2_OIL_WIN_MIN_CCJ | CAP_SUM_MIN_CCJ | CAP_WIN_MIN_CCJ
K | K - Long Island | 6370 | 6340 | 1.58 | 2.48 | 517.9 | 547.8 | 600 | 3490 | 26600 | 26.6933 | 6.8756 | 411320 | 26.5676 | 6.8432 | 409382.8571 | 97.0667 | 5.3589 | 558133.3333 | 96.6095 | 5.3337 | 555504.7619 | 0.9708 | 7130 | 7540 | 29.8781 | 7.6959 | 460394.2857 | 31.5962 | 8.1384 | 486868.5714 | 108.6476 | 5.9983 | 624723.8095 | 114.8952 | 6.3432 | 660647.619 | 235.7 | 199.5
J | J - NYC | 6370 | 6350 | 1.61 | 2.84 | 512.3 | 546.7 | 600 | 3490 | 26600 | 26.651 | 6.8647 | 410668.1458 | 26.5674 | 6.8431 | 409378.7639 | 96.9128 | 5.3504 | 557248.8114 | 96.6086 | 5.3336 | 555499.2076 | 0.9708 | 7180 | 7530 | 30.0399 | 7.7376 | 462888.1141 | 31.5043 | 8.1147 | 485452.2979 | 109.2361 | 6.0307 | 628107.7655 | 114.561 | 6.3247 | 658725.832 | 232.3 | 199.3
G1 | G - LHV (Dutchess) | 6360 | 6350 | 1.59 | 2.45 | 514.7 | 544.8 | 600 | 3490 | 26600 | 26.6514 | 6.7638 | 408251.4286 | 26.6095 | 6.7532 | 407609.5238 | 96.9143 | 5.2495 | 554026.6667 | 96.7619 | 5.2413 | 553155.5556 | 0.9708 | 7130 | 7550 | 29.8781 | 7.5827 | 457678.0952 | 31.6381 | 8.0294 | 484638.0952 | 108.6476 | 5.8851 | 621102.2222 | 115.0476 | 6.2317 | 657688.8889 | 234 | 198.7
G2 | G - LHV (Rockland) | 6360 | 6350 | 1.59 | 2.45 | 514.7 | 544.8 | 600 | 3490 | 26600 | 26.6514 | 6.7638 | 408251.4286 | 26.6095 | 6.7532 | 407609.5238 | 96.9143 | 5.2495 | 554026.6667 | 96.7619 | 5.2413 | 553155.5556 | 0.9708 | 7130 | 7550 | 29.8781 | 7.5827 | 457678.0952 | 31.6381 | 8.0294 | 484638.0952 | 108.6476 | 5.8851 | 621102.2222 | 115.0476 | 6.2317 | 657688.8889 | 234 | 198.7
F | F - Capital | 6360 | 6360 | 1.59 | 2.45 | 513.3 | 542.1 | 600 | 3490 | 26600 | 26.6514 | 6.7638 | 407040 | 26.6514 | 6.7638 | 407040 | 96.9143 | 5.2495 | 552411.4286 | 96.9143 | 5.2495 | 552411.4286 | 0.9708 | 7130 | 7560 | 29.8781 | 7.5827 | 456320 | 31.68 | 8.04 | 483840 | 108.6476 | 5.8851 | 619291.4286 | 115.2 | 6.24 | 656640 | 233.4 | 198
C | C - Central | 6370 | 6360 | 1.59 | 2.45 | 509.9 | 539.2 | 600 | 3490 | 26600 | 26.6933 | 6.6733 | 397973.3333 | 26.6514 | 6.6629 | 397348.5714 | 97.0667 | 5.2578 | 550044.4444 | 96.9143 | 5.2495 | 549180.9524 | 0.9708 | 7130 | 7570 | 29.8781 | 7.4695 | 445455.2381 | 31.7219 | 7.9305 | 472944.7619 | 108.6476 | 5.8851 | 615669.8413 | 115.3524 | 6.2483 | 653663.4921 | 232.1 | 197

## Aero_NoSCR_Filtered
[6 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[6 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_Aeroderivative |  |  |  |  | Simple Cycle Aeroderivative Siemens 3x SGT-A65 (No SCR)
|  |  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable |  | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW |  | Summer | MW | 166.6 | 166.5 | 166.5 | 166.5 | 166.7 | 166.7
44 | 52 | Net Plant Output, kW |  | Winter | MW | 188.2 | 188.2 | 188.2 | 188.2 | 188.2 | 188.2
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Summer | Btu/kWh | 9670 | 9670 | 9670 | 9670 | 9660 | 9670
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Winter | Btu/kWh | 9450 | 9460 | 9440 | 9440 | 9440 | 9440
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Heat Rate - ISO Conditions | Btu/kWh | 9420 | 9420 | 9430 | 9430 | 9430 | 9430 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 171.2268 | 171.2268 | 171.0452 | 171.0452 | 170.8683 | 171.0452
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 3.5929 | 3.5929 | 3.5891 | 3.5891 | 3.5854 | 3.5891
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 214341.4013 | 214341.4013 | 214114.1039 | 214114.1039 | 213892.6829 | 214114.1039
Natural Gas Emission Rates - Winter
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 167.3312 | 167.5083 | 166.9769 | 166.9769 | 166.9769 | 166.9769
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 3.5111 | 3.5149 | 3.5037 | 3.5037 | 3.5037 | 3.5037
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 209464.9682 | 209686.6242 | 209021.421 | 209021.421 | 209021.421 | 209021.421
ULSD Emission Rates - Summer
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 285.3779 | 285.3779 | 285.0753 | 285.0753 | 284.7805 | 285.0753
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 2.669 | 2.669 | 2.6662 | 2.6662 | 2.6634 | 2.6662
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 285788.535 | 285788.535 | 285485.4719 | 285485.4719 | 285190.2439 | 285485.4719
ULSD Emission Rates - Winter
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 278.8854 | 279.1805 | 278.2948 | 278.2948 | 278.2948 | 278.2948
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 2.6083 | 2.611 | 2.6028 | 2.6028 | 2.6028 | 2.6028
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 279286.6242 | 279582.1656 | 278695.228 | 278695.228 | 278695.228 | 278695.228
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  |  | Fuel Required per Start (regular start - 21 min. to full load) | MMBtu/Start | 100 | 100 | 100 | 100 | 100 | 100
16 | 16 | Equivalent Forced Outage Rate Demand, % |  | EFORd outage rate | % | 10.03% | 10.03% | 10.03% | 10.03% | 10.03% | 10.03%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 8.91 | 9.36 | 9.04 | 9.04 | 9.14 | 9.27
190 | 193 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 8.78 | 9.2 | 8.92 | 8.92 | 9.02 | 9.12
177 | 180 | Major Maintenance Cost, 2020$/GT-hr or $/engine-hr |  | Maj. Maintenance per Hour | $/hr | 570 | 570 | 570 | 570 | 570 | 570
177 | 180 | Major Maintenance Cost, 2020$/GT-start |  | Maj. Maintenance per Start | $/Start | N/A | N/A | N/A | N/A | N/A | N/A
Updated 5/27/2020

## Aero_SCR_Filtered
[5 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[5 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_Aeroderivative |  |  |  | Simple Cycle Aeroderivative Siemens 3x SGT-A65 (with SCR)
|  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW | Summer | MW | 166.6 | 166.5 | 166.5 | 166.5 | 166.7 | 166.7
44 | 52 | Net Plant Output, kW | Winter | MW | 188.2 | 188.2 | 188.2 | 188.2 | 188.2 | 188.2
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Summer | Btu/kWh | 9670 | 9670 | 9670 | 9670 | 9660 | 9670
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Winter | Btu/kWh | 9450 | 9460 | 9440 | 9440 | 9440 | 9440
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Heat Rate - ISO Conditions | Btu/kWh | 9420 | 9420 | 9430 | 9430 | 9430 | 9430 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 13.653 | 13.653 | 13.6385 | 13.6385 | 13.6244 | 13.6385
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 3.5929 | 3.5929 | 3.5891 | 3.5891 | 3.5854 | 3.5891
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 214341.4013 | 214341.4013 | 214114.1039 | 214114.1039 | 213892.6829 | 214114.1039
Natural Gas Emission Rates - Winter
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 13.3424 | 13.3565 | 13.3141 | 13.3141 | 13.3141 | 13.3141
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 3.5111 | 3.5149 | 3.5037 | 3.5037 | 3.5037 | 3.5037
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 209464.9682 | 209686.6242 | 209021.421 | 209021.421 | 209021.421 | 209021.421
ULSD Emission Rates - Summer
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 42.8067 | 42.8067 | 42.7613 | 42.7613 | 42.7171 | 42.7613
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 2.669 | 2.669 | 2.6662 | 2.6662 | 2.6634 | 2.6662
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 285788.535 | 285788.535 | 285485.4719 | 285485.4719 | 285190.2439 | 285485.4719
ULSD Emission Rates - Winter
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 41.8328 | 41.8771 | 41.7442 | 41.7442 | 41.7442 | 41.7442
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 2.6083 | 2.611 | 2.6028 | 2.6028 | 2.6028 | 2.6028
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 279286.6242 | 279582.1656 | 278695.228 | 278695.228 | 278695.228 | 278695.228
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 21 min. to full load) | MMBtu/Start | 100 | 100 | 100 | 100 | 100 | 100
16 | 16 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 10.03% | 10.03% | 10.03% | 10.03% | 10.03% | 10.03%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - NG Firing | $/MWh | 9.74 | 10.19 | 9.87 | 9.87 | 9.97 | 10.09
190 | 193 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 9.81 | 10.23 | 9.92 | 9.92 | 10.02 | 10.12
177 | 180 | Major Maintenance Cost, 2020$/GT-hr or $/engine-hr | Maj. Maintenance per Hour | $/hr | 570 | 570 | 570 | 570 | 570 | 570
177 | 180 | Major Maintenance Cost, 2020$/GT-start | Maj. Maintenance per Start | $/Start | N/A | N/A | N/A | N/A | N/A | N/A
Updated 5/27/2020

## F-Class_NoSCR_Filtered
[6 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[6 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_F-Class |  |  |  |  | Simple Cycle Frame F-Class: GE 1x 7F.05 (No SCR)
|  |  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable 1 | Variable 2 | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW |  | Summer | MW | 218 | 217.8 | 217 | 217 | 217 | 215.8
44 | 52 | Net Plant Output, kW |  | Winter | MW | 227.2 | 226.9 | 226.5 | 226.5 | 225.9 | 224.9
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Summer | Btu/kWh | 10200 | 10210 | 10200 | 10200 | 10180 | 10180
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Winter | Btu/kWh | 9890 | 9900 | 9890 | 9890 | 9880 | 9880
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Heat Rate - ISO Conditions | Btu/kWh | 10160 | 10160 | 10160 | 10160 | 10160 | 10160 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 80.2146 | 80.2932 | 80.2146 | 80.2146 | 80.0573 | 80.0573
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 4.6181 | 4.6226 | 4.6181 | 4.6181 | 4.5089 | 4.5089
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 277086.6142 | 277358.2677 | 274677.1654 | 274677.1654 | 272936.2205 | 271733.8583
Natural Gas Emission Rates - Winter
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 77.7767 | 77.8553 | 77.7767 | 77.7767 | 77.698 | 77.698
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 4.4778 | 4.4823 | 4.4778 | 4.4778 | 4.376 | 4.376
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 268665.3543 | 268937.0079 | 266329.1339 | 266329.1339 | 264892.9134 | 263725.9843
ULSD Emission Rates - Summer
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 431.6929 | 432.1161 | 431.6929 | 431.6929 | 430.8465 | 430.8465
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 3.5138 | 3.5172 | 3.5138 | 3.5138 | 3.5069 | 3.4067
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 369448.8189 | 369811.0236 | 366236.2205 | 366236.2205 | 363914.9606 | 362311.811
ULSD Emission Rates - Winter
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 418.5728 | 418.9961 | 418.5728 | 418.5728 | 418.1496 | 418.1496
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 3.407 | 3.4104 | 3.407 | 3.407 | 3.4035 | 3.3063
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 358220.4724 | 358582.6772 | 355105.5118 | 355105.5118 | 353190.5512 | 351634.6457
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 325 | 325 | 325 | 325 | 325 | 325
16 | 16 | Equivalent Forced Outage Rate Demand, % |  | EFORd outage rate | % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 0.95 | 0.97 | 0.94 | 0.94 | 0.94 | 0.94
190 | 193 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 8.04 | 8.42 | 8.04 | 8.04 | 8.04 | 8.04
177 | 180 | Major Maintenance Cost, 2020$/GT-start |  | Maj. Maintenance per Start | $/Start | 9500 | 9500 | 9500 | 9500 | 9500 | 9500
Updated 5/27/2020

## F-Class_SCR_Filtered
[5 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[5 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_F-Class |  |  |  | Simple Cycle Frame F-Class: GE 1x 7F.05
|  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW | Summer | MW | 218 | 217.8 | 217 | 217 | 217 | 215.8
44 | 52 | Net Plant Output, kW | Winter | MW | 227.2 | 226.9 | 226.5 | 226.5 | 225.9 | 224.9
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Summer | Btu/kWh | 10200 | 10210 | 10200 | 10200 | 10180 | 10180
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Winter | Btu/kWh | 9890 | 9900 | 9890 | 9890 | 9880 | 9880
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Heat Rate - ISO Conditions | Btu/kWh | 10160 | 10160 | 10160 | 10160 | 10160 | 10160 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 17.8701 | 17.8876 | 17.8701 | 17.8701 | 17.835 | 17.835
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 4.6181 | 4.6226 | 4.6181 | 4.6181 | 4.5089 | 4.5089
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 277086.6142 | 277358.2677 | 274677.1654 | 274677.1654 | 272936.2205 | 271733.8583
Natural Gas Emission Rates - Winter
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 17.327 | 17.3445 | 17.327 | 17.327 | 17.3094 | 17.3094
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 4.4778 | 4.4823 | 4.4778 | 4.4778 | 4.376 | 4.376
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 268665.3543 | 268937.0079 | 266329.1339 | 266329.1339 | 264892.9134 | 263725.9843
ULSD Emission Rates - Summer
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 64.7539 | 64.8174 | 64.7539 | 64.7539 | 64.627 | 64.627
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 3.5138 | 3.5172 | 3.5138 | 3.5138 | 3.5069 | 3.4067
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 369448.8189 | 369811.0236 | 366236.2205 | 366236.2205 | 363914.9606 | 362311.811
ULSD Emission Rates - Winter
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 62.7859 | 62.8494 | 62.7859 | 62.7859 | 62.7224 | 62.7224
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 3.407 | 3.4104 | 3.407 | 3.407 | 3.4035 | 3.3063
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 358220.4724 | 358582.6772 | 355105.5118 | 355105.5118 | 353190.5512 | 351634.6457
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 325 | 325 | 325 | 325 | 325 | 325
16 | 16 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - NG Firing | $/MWh | 1.52 | 1.54 | 1.52 | 1.52 | 1.52 | 1.52
190 | 193 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 8.83 | 9.21 | 8.84 | 8.84 | 8.84 | 8.84
177 | 180 | Major Maintenance Cost, 2020$/GT-start | Maj. Maintenance per Start | $/Start | 9500 | 9500 | 9500 | 9500 | 9500 | 9500
Updated 5/27/2020

## J-Class25ppm_NoSCR_Filtered
[6 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[6 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_J-Class25ppm |  |  |  |  | Simple Cycle Frame J-Class GE 1x HA.02 (25ppm) (No SCR)
|  |  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable |  | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW |  | Summer | MW | 359 | 358.7 | 357.4 | 357.4 | 357.7 | 355.6
44 | 52 | Net Plant Output, kW |  | Winter | MW | 371.1 | 370.2 | 370.2 | 370.2 | 369.2 | 367.4
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Summer | Btu/kWh | 9370 | 9370 | 9360 | 9360 | 9350 | 9350
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Winter | Btu/kWh | 9300 | 9300 | 9300 | 9300 | 9290 | 9280
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Heat Rate - ISO Conditions | Btu/kWh | 9340 | 9340 | 9340 | 9340 | 9340 | 9340 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 331.5616 | 331.5616 | 331.2077 | 331.2077 | 330.8539 | 330.8539
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 6.9222 | 6.9222 | 6.9148 | 6.9148 | 6.8073 | 6.8073
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 415329.7645 | 415329.7645 | 412481.3704 | 412481.3704 | 410839.4004 | 408436.8308
Natural Gas Emission Rates - Winter
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 329.0846 | 329.0846 | 329.0846 | 329.0846 | 328.7307 | 328.3769
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 6.8704 | 6.8704 | 6.8704 | 6.8704 | 6.7636 | 6.7563
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 412226.9807 | 412226.9807 | 409837.2591 | 409837.2591 | 408202.9979 | 405379.015
ULSD Emission Rates - Summer
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 642.0557 | 642.0557 | 641.3704 | 641.3704 | 640.6852 | 640.6852
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 5.317 | 5.317 | 5.2111 | 5.2111 | 5.2056 | 5.2056
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 553773.0193 | 553773.0193 | 549975.1606 | 549975.1606 | 547785.8672 | 544582.4411
ULSD Emission Rates - Winter
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 637.2591 | 637.2591 | 637.2591 | 637.2591 | 636.5739 | 635.8887
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 5.2773 | 5.2773 | 5.1777 | 5.1777 | 5.1722 | 5.1666
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 549635.9743 | 549635.9743 | 546449.6788 | 546449.6788 | 544270.6638 | 540505.3533
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 490 | 490 | 490 | 490 | 490 | 490
16 | 16 | Equivalent Forced Outage Rate Demand, % |  | EFORd outage rate | % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 0.93 | 0.95 | 0.93 | 0.93 | 0.93 | 0.93
190 | 193 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 10.23 | 10.76 | 10.23 | 10.23 | 10.21 | 10.21
177 | 180 | Major Maintenance Cost, 2020$/GT-start |  | Maj. Maintenance per Start | $/Start | 26600 | 26600 | 26600 | 26600 | 26600 | 26600
Updated 5/27/2020

## J-Class25ppm_SCR_Filtered
[5 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[5 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_J-Class25ppm |  |  |  | Simple Cycle Frame J-Class GE 1x HA.02 (25 ppm)
|  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW | Summer | MW | 359 | 358.7 | 357.4 | 357.4 | 357.7 | 355.6
44 | 52 | Net Plant Output, kW | Winter | MW | 371.1 | 370.2 | 370.2 | 370.2 | 369.2 | 367.4
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Summer | Btu/kWh | 9370 | 9370 | 9360 | 9360 | 9350 | 9350
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Winter | Btu/kWh | 9300 | 9300 | 9300 | 9300 | 9290 | 9280
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Heat Rate - ISO Conditions | Btu/kWh | 9340 | 9340 | 9340 | 9340 | 9340 | 9340 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 26.4848 | 26.4848 | 26.4565 | 26.4565 | 26.4283 | 26.4283
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 6.9222 | 6.9222 | 6.9148 | 6.9148 | 6.8073 | 6.8073
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 415329.7645 | 415329.7645 | 412481.3704 | 412481.3704 | 410839.4004 | 408436.8308
Natural Gas Emission Rates - Winter
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 26.2869 | 26.2869 | 26.2869 | 26.2869 | 26.2587 | 26.2304
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 6.8704 | 6.8704 | 6.8704 | 6.8704 | 6.7636 | 6.7563
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 412226.9807 | 412226.9807 | 409837.2591 | 409837.2591 | 408202.9979 | 405379.015
ULSD Emission Rates - Summer
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 96.3084 | 96.3084 | 96.2056 | 96.2056 | 96.1028 | 96.1028
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 5.317 | 5.317 | 5.2111 | 5.2111 | 5.2056 | 5.2056
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 553773.0193 | 553773.0193 | 549975.1606 | 549975.1606 | 547785.8672 | 544582.4411
ULSD Emission Rates - Winter
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 95.5889 | 95.5889 | 95.5889 | 95.5889 | 95.4861 | 95.3833
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 5.2773 | 5.2773 | 5.1777 | 5.1777 | 5.1722 | 5.1666
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 549635.9743 | 549635.9743 | 546449.6788 | 546449.6788 | 544270.6638 | 540505.3533
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 490 | 490 | 490 | 490 | 490 | 490
16 | 16 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - NG Firing | $/MWh | 1.39 | 1.43 | 1.39 | 1.39 | 1.39 | 1.4
190 | 193 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 10.93 | 11.46 | 10.93 | 10.93 | 10.91 | 10.91
177 | 180 | Major Maintenance Cost, 2020$/GT-start | Maj. Maintenance per Start | $/Start | 26600 | 26600 | 26600 | 26600 | 26600 | 26600
Updated 5/27/2020

## J-Class15ppm_NoSCR_Filtered
[6 empty] | ZONE G - Dutchess | ZONE F | ZONE C
[6 empty] | 4 | 3 | 2
Sheet | Raw_J-Class15ppm |  |  |  |  | Simple Cycle Frame J-Class GE 1x HA.02 (15 ppm) (No SCR)
|  |  |  | Item | Units | G - LHV (Dutchess) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable |  | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW |  | Summer | MW | 340.9 | 341.2 | 338
44 | 52 | Net Plant Output, kW |  | Winter | MW | 350.5 | 351 | 346.1
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Summer | Btu/kWh | 9390 | 9390 | 9370
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Winter | Btu/kWh | 9340 | 9320 | 9320
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Heat Rate - ISO Conditions | Btu/kWh | 9340 | 9350 | 9340 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 189.6096 | 189.4068 | 189.2058
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 6.4343 | 6.4274 | 6.4206
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 387262.0985 | 385642.7807 | 382825.6959
Natural Gas Emission Rates - Winter
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 188.6 | 187.9949 | 188.1961
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 6.4 | 6.3795 | 6.3863
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 385200 | 382767.9144 | 380782.8694
ULSD Emission Rates - Summer
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 643.4261 | 642.738 | 642.0557
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 4.9262 | 4.921 | 4.8154
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 516349.4647 | 514190.3743 | 510434.2612
ULSD Emission Rates - Winter
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 640 | 637.9465 | 638.6296
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 4.9 | 4.8843 | 4.7897
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 513600 | 510357.2193 | 507710.4925
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 490 | 490 | 490
16 | 16 | Equivalent Forced Outage Rate Demand, % |  | EFORd outage rate | % | 4.34% | 4.34% | 4.34%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 0.93 | 0.93 | 0.93
190 | 193 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 10.21 | 10.21 | 10.21
177 | 180 | Major Maintenance Cost, 2020$/GT-start |  | Maj. Maintenance per Start | $/Start | 26600 | 26600 | 26600
Updated 5/27/2020

## J-Class_CC_Filtered
[5 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[5 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_J-Class_CC |  |  |  | Combined Cycle J-Class Frame 1x1 GE HA.02
|  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
101 | 104 | Net Plant Output, kW | Summer | MW | 517.9 | 512.3 | 514.7 | 514.7 | 513.3 | 509.9
67 | 70 | Net Plant Output, kW | Winter | MW | 547.8 | 546.7 | 544.8 | 544.8 | 542.1 | 539.2
Net Plant Output (MECL)
111 | 114 | Net Plant Output, kW | Summer | MW | 235.7 | 232.3 | 234 | 234 | 233.4 | 232.1
77 | 80 | Net Plant Output, kW | Winter | MW | 199.5 | 199.3 | 198.7 | 198.7 | 198 | 197
Net Plant Heat Rate (HHV)
101 | 104 | Net Plant Heat Rate, Btu/kWh (HHV) | Summer | Btu/kWh | 6370 | 6370 | 6360 | 6360 | 6360 | 6370
67 | 70 | Net Plant Heat Rate, Btu/kWh (HHV) | Winter | Btu/kWh | 6340 | 6350 | 6350 | 6350 | 6360 | 6360
82 | 85 | Net Plant Heat Rate, Btu/kWh (HHV) | ISO Conditions | Btu/kWh | 6300 | 6310 | 6300 | 6300 | 6300 | 6300
Net Plant Heat Rate (HHV) (MECL)
111 | 114 | Net Plant Heat Rate, Btu/kWh (HHV) | Summer | Btu/kWh | 7130 | 7180 | 7130 | 7130 | 7130 | 7130
77 | 80 | Net Plant Heat Rate, Btu/kWh (HHV) | Winter | Btu/kWh | 7540 | 7530 | 7550 | 7550 | 7560 | 7570
Natural Gas Emission Rates - Summer
239 | 242 | NOX | NOX Emissions Rate | lb/hr | 26.6933 | 26.651 | 26.6514 | 26.6514 | 26.6514 | 26.6933
239 | 242 | SO2 | SO2 Emissions Rate | lb/hr | 6.8756 | 6.8647 | 6.7638 | 6.7638 | 6.7638 | 6.6733
239 | 242 | CO2 | CO2 Emissions Rate | lb/hr | 411320 | 410668.1458 | 408251.4286 | 408251.4286 | 407040 | 397973.3333
Natural Gas Emission Rates - Winter
239 | 242 | NOX | NOX Emissions Rate | lb/hr | 26.5676 | 26.5674 | 26.6095 | 26.6095 | 26.6514 | 26.6514
239 | 242 | SO2 | SO2 Emissions Rate | lb/hr | 6.8432 | 6.8431 | 6.7532 | 6.7532 | 6.7638 | 6.6629
239 | 242 | CO2 | CO2 Emissions Rate | lb/hr | 409382.8571 | 409378.7639 | 407609.5238 | 407609.5238 | 407040 | 397348.5714
ULSD Emission Rates - Summer
246 | 249 | NOX | NOX Emissions Rate | lb/hr | 97.0667 | 96.9128 | 96.9143 | 96.9143 | 96.9143 | 97.0667
246 | 249 | SO2 | SO2 Emissions Rate | lb/hr | 5.3589 | 5.3504 | 5.2495 | 5.2495 | 5.2495 | 5.2578
246 | 249 | CO2 | CO2 Emissions Rate | lb/hr | 558133.3333 | 557248.8114 | 554026.6667 | 554026.6667 | 552411.4286 | 550044.4444
ULSD Emission Rates - Winter
246 | 249 | NOX | NOX Emissions Rate | lb/hr | 96.6095 | 96.6086 | 96.7619 | 96.7619 | 96.9143 | 96.9143
246 | 249 | SO2 | SO2 Emissions Rate | lb/hr | 5.3337 | 5.3336 | 5.2413 | 5.2413 | 5.2495 | 5.2495
246 | 249 | CO2 | CO2 Emissions Rate | lb/hr | 555504.7619 | 555499.2076 | 553155.5556 | 553155.5556 | 552411.4286 | 549180.9524
Natural Gas Emission Rates - Summer (MECL)
239 | 242 | NOX | NOX Emissions Rate | lb/hr | 29.8781 | 30.0399 | 29.8781 | 29.8781 | 29.8781 | 29.8781
239 | 242 | SO2 | SO2 Emissions Rate | lb/hr | 7.6959 | 7.7376 | 7.5827 | 7.5827 | 7.5827 | 7.4695
239 | 242 | CO2 | CO2 Emissions Rate | lb/hr | 460394.2857 | 462888.1141 | 457678.0952 | 457678.0952 | 456320 | 445455.2381
Natural Gas Emission Rates - Winter (MECL)
239 | 242 | NOX | NOX Emissions Rate | lb/hr | 31.5962 | 31.5043 | 31.6381 | 31.6381 | 31.68 | 31.7219
239 | 242 | SO2 | SO2 Emissions Rate | lb/hr | 8.1384 | 8.1147 | 8.0294 | 8.0294 | 8.04 | 7.9305
239 | 242 | CO2 | CO2 Emissions Rate | lb/hr | 486868.5714 | 485452.2979 | 484638.0952 | 484638.0952 | 483840 | 472944.7619
ULSD Emission Rates - Summer (MECL)
246 | 249 | NOX | NOX Emissions Rate | lb/hr | 108.6476 | 109.2361 | 108.6476 | 108.6476 | 108.6476 | 108.6476
246 | 249 | SO2 | SO2 Emissions Rate | lb/hr | 5.9983 | 6.0307 | 5.8851 | 5.8851 | 5.8851 | 5.8851
246 | 249 | CO2 | CO2 Emissions Rate | lb/hr | 624723.8095 | 628107.7655 | 621102.2222 | 621102.2222 | 619291.4286 | 615669.8413
ULSD Emission Rates - Winter (MECL)
246 | 249 | NOX | NOX Emissions Rate | lb/hr | 114.8952 | 114.561 | 115.0476 | 115.0476 | 115.2 | 115.3524
246 | 249 | SO2 | SO2 Emissions Rate | lb/hr | 6.3432 | 6.3247 | 6.2317 | 6.2317 | 6.24 | 6.2483
246 | 249 | CO2 | CO2 Emissions Rate | lb/hr | 660647.619 | 658725.832 | 657688.8889 | 657688.8889 | 656640 | 653663.4921
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 3490 | 3490 | 3490 | 3490 | 3490 | 3490
22 | 22 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 2.92% | 2.92% | 2.92% | 2.92% | 2.92% | 2.92%
Variable O&M & Maj. Maintenance Costs (per unit)
212 | 215 | Total Variable O&M Cost, 2020 $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 1.58 | 1.61 | 1.59 | 1.59 | 1.59 | 1.59
223 | 226 | Total Variable O&M Cost, 2020 $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 2.48 | 2.84 | 2.45 | 2.45 | 2.45 | 2.45
205 | 208 | Major Maintenance Cost, 2020 $/GT-hr | Maj. Maintenance per Hour | $/GT-hr | 600 | 600 | 600 | 600 | 600 | 600
205 | 208 | Major Maintenance Cost, 2020$/GT-start | Maj. Maintenance per Start | $/Start | 26600 | 26600 | 26600 | 26600 | 26600 | 26600
Updated 5/27/2020

## Raw_Aeroderivative
NYISO DCR TECHNOLOGY ASSESSMENT
SIMPLE CYCLE AERODERIVATIVE SIEMENS SGT-A65
PRELIMINARY AND CONFIDENTIAL - NOT FOR CONSTRUCTION
May 2020 - DRAFT REV 4.1 [AG UPDATED 7.27.2020]
PROJECT TYPE | ZONE C | ZONE F | ZONE G - Dutchess | ZONE G - Rockland | ZONE J | ZONE K
BASE PLANT DESCRIPTION
Number of Gas Turbines | 3 | 3 | 3 | 3 | 3 | 3
Representative Class Gas Turbine | Siemens SGT-A65 WLE | Siemens SGT-A65 WLE | Siemens SGT-A65 WLE | Siemens SGT-A65 WLE | Siemens SGT-A65 WLE | Siemens SGT-A65 WLE
Startup Time to Base Load, min | 5 | 5 | 5 | 5 | 5 | 5
Startup Time to MECL, min | 4 | 4 | 4 | 4 | 4 | 4
Cold Startup Time to SCR Compliance, min | 45 | 45 | 45 | 45 | 45 | 45
Equivalent Forced Outage Rate Demand, % | 10.03% | 10.03% | 10.03% | 10.03% | 10.03% | 10.03%
Assumed Land Use During Operation, Acres (Not Construction Land Use) | 15 | 15 | 15 | 15 | 12 | 15
Fuel Design | Natural Gas Only | Natural Gas Only | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil)
Inlet Conditioning | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler
Heat Rejection | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger
NOx Control | Water Injection and SCR | Water Injection and SCR | Water Injection and SCR | Water Injection and SCR | Water Injection and SCR | Water Injection and SCR
CO Control | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst
Particulate Control | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice
Interconnection Voltage, kV | 345 | 345 | 345 | 345 | 345 | 138
Technology Rating | Mature | Mature | Mature | Mature | Mature | Mature
Permitting & Construction Schedule (Years from FNTP) | 3 | 3 | 3 | 3 | 3 | 3
ESTIMATED PERFORMANCE (All BASED ON NATURAL GAS OPERATION)
Summer Performance
Ambient Temperature, °F | 64.39 | 65.46 | 67.14 | 67.14 | 70.71 | 67.8
Relative Humidity, % | 76.02% | 69.1% | 77.21% | 77.21% | 66.44% | 77.3%
Net Plant Output, kW | 166700 | 166700 | 166500 | 166500 | 166500 | 166600
Net Plant Heat Rate, Btu/kWh (HHV) | 9670 | 9660 | 9670 | 9670 | 9670 | 9670
Heat Input, MMBtu/h (HHV) | 1610 | 1610 | 1610 | 1610 | 1610 | 1610
Min Load Plant Output, kW | 22800 | 22800 | 22700 | 22700 | 22600 | 22700
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 11860 | 11870 | 11880 | 11880 | 11910 | 11870
Min LoadHeat Input, MMBtu/h (HHV) | 270 | 270 | 270 | 270 | 270 | 270
Winter Performance
Ambient Temperature, °F | 31.96 | 33.13 | 36.05 | 36.05 | 41.19 | 39.5
Relative Humidity, % | 74.44% | 65.62% | 75.54% | 75.54% | 60.9% | 69.2%
Net Plant Output, kW | 188200 | 188200 | 188200 | 188200 | 188200 | 188200
Net Plant Heat Rate, Btu/kWh (HHV) | 9440 | 9440 | 9440 | 9440 | 9460 | 9450
Heat Input, MMBtu/h (HHV) | 1780 | 1780 | 1780 | 1780 | 1780 | 1780
Min Load Plant Output, kW | 25700 | 25700 | 25700 | 25700 | 25700 | 25700
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 11550 | 11550 | 11550 | 11550 | 11560 | 11550
Min LoadHeat Input, MMBtu/h (HHV) | 300 | 300 | 300 | 300 | 300 | 300
Spring-Fall (ISO) Performance
Ambient Temperature, °F | 59 | 59 | 59 | 59 | 59 | 59
Relative Humidity, % | 60% | 60% | 60% | 60% | 60% | 60%
Net Plant Output, kW | 184700 | 184700 | 184800 | 184800 | 184900 | 184900
Net Plant Heat Rate, Btu/kWh (HHV) | 9430 | 9430 | 9430 | 9430 | 9420 | 9420
Heat Input, MMBtu/h (HHV) | 1740 | 1740 | 1740 | 1740 | 1740 | 1740
Min Load Plant Output, kW | 25300 | 25300 | 25300 | 25300 | 25300 | 25300
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 11630 | 11620 | 11620 | 11620 | 11620 | 11620
Min LoadHeat Input, MMBtu/h (HHV) | 290 | 290 | 290 | 290 | 290 | 290
Summer DMNC Performance
Ambient Temperature, °F | 88.86 | 89.43 | 92.85 | 92.85 | 93.25 | 88.8
Relative Humidity, % | 57.7% | 54.65% | 51.49% | 51.49% | 58.8% | 59%
Net Plant Output, kW | 160900 | 161200 | 160200 | 160200 | 158800 | 160800
Net Plant Heat Rate, Btu/kWh (HHV) | 9730 | 9720 | 9730 | 9730 | 9730 | 9720
Heat Input, MMBtu/h (HHV) | 1570 | 1570 | 1560 | 1560 | 1550 | 1560
Min Load Plant Output, kW | 21300 | 21200 | 21000 | 21000 | 21000 | 21300
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12230 | 12240 | 12290 | 12290 | 12290 | 12210
Min LoadHeat Input, MMBtu/h (HHV) | 260 | 260 | 260 | 260 | 260 | 260
Winter DMNC Performance
Ambient Temperature, °F | 10.84 | 13.23 | 12.48 | 12.48 | 21.15 | 16.5
Relative Humidity, % | 55.67% | 59.08% | 57.55% | 57.55% | 46.44% | 50.2%
Net Plant Output, kW | 188200 | 188200 | 188200 | 188200 | 188200 | 188200
Net Plant Heat Rate, Btu/kWh (HHV) | 9380 | 9390 | 9380 | 9380 | 9400 | 9390
Heat Input, MMBtu/h (HHV) | 1770 | 1770 | 1770 | 1770 | 1770 | 1770
Min Load Plant Output, kW | 25700 | 25700 | 25700 | 25700 | 25700 | 25700
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 11500 | 11500 | 11500 | 11500 | 11510 | 11500
Min LoadHeat Input, MMBtu/h (HHV) | 300 | 300 | 300 | 300 | 300 | 300
ICAP Performance
Ambient Temperature, °F | 90 | 90 | 90 | 90 | 90 | 90
Relative Humidity, % | 70% | 70% | 70% | 70% | 70% | 70%
Net Plant Output, kW | 158600 | 158600 | 158700 | 158700 | 158700 | 158700
Net Plant Heat Rate, Btu/kWh (HHV) | 9730 | 9730 | 9730 | 9730 | 9720 | 9720
Heat Input, MMBtu/h (HHV) | 1540 | 1540 | 1540 | 1540 | 1540 | 1540
Min Load Plant Output, kW | 21200 | 21200 | 21200 | 21200 | 21200 | 21200
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12240 | 12240 | 12230 | 12230 | 12230 | 12230
Min LoadHeat Input, MMBtu/h (HHV) | 260 | 260 | 260 | 260 | 260 | 260
ESTIMATED STARTUP FUEL USAGE
Start to Base Load, MMBtu (includes all GTs) | 100 | 100 | 100 | 100 | 100 | 100
ESTIMATED CAPITAL AND O&M COSTS
EPC Project Capital Costs, 2020 MM$ (w/o Owner's Costs) | 213.3 | 215.65 | 231.47 | 239.8 | 261.48 | 258.42
Labor | 37.6906 | 39.3088 | 45.625 | 53.7947 | 72.3703 | 69.9186
Materials | 63.5541 | 63.7416 | 66.6077 | 66.7704 | 66.8885 | 66.945
Turbines or Batteries | 63 | 63 | 66 | 66 | 66 | 66
Other | 49.0601 | 49.5995 | 53.2383 | 53.2358 | 56.2174 | 55.5614
Owner's Cost Allowances, 2020 MM$ | 67.46 | 67.59 | 74.86 | 75.63 | 123.75 | 64.49
Owner's Project Development | 0.37 | 0.37 | 0.37 | 0.37 | 0.48 | 0.41
Owner's Operational Personnel Prior to COD | 0.44 | 0.44 | 0.44 | 0.44 | 0.57 | 0.48
Owner's Engineer | 1.02 | 1.02 | 1.02 | 1.02 | 1.33 | 1.12
Owner's Project Management | 1.13 | 1.13 | 1.13 | 1.13 | 1.47 | 1.24
Owner's Legal Costs | 1 | 1 | 1 | 1 | 1.3 | 1.1
Owner's Start-up Engineering and Commissioning | 0.27 | 0.27 | 0.27 | 0.27 | 0.35 | 0.3
Sales Tax | 0 | 0 | 0 | 0 | 0 | 0
Construction Power and Water | 0.51 | 0.51 | 0.51 | 0.51 | 0.66 | 0.56
Permitting and Licensing Fees | 1 | 1 | 1 | 1 | 1.3 | 1.1
Switchyard | 17.08 | 17.08 | 17.08 | 17.08 | 52.03 | 9.32
Electrical Interconnection and Deliverability | 11 | 11 | 11 | 11 | 13.01 | 6.5
Gas Interconnection and Reinforcement | 14.3 | 14.3 | 14.3 | 14.3 | 20 | 14.3
System Deliverability Upgrade Costs | 0 | 0 | 0 | 0 | 0 | 0
Emission Reduction Credits | 0.1 | 0.1 | 0.1 | 0.4 | 0.4 | 0.4
Political Concessions & Area Development | 0.5 | 0.5 | 0.5 | 0.5 | 0.65 | 0.55
Startup/Testing (Fuel & Consumables) | 0.72 | 0.72 | 2.64 | 2.64 | 2.64 | 2.64
Initial Fuel Inventory | 0 | 0 | 4.18 | 4.18 | 4.18 | 4.18
Site Security | 0.58 | 0.58 | 0.58 | 0.58 | 0.75 | 0.64
Operating Spare Parts | 3.11 | 3.11 | 3.11 | 3.11 | 3.11 | 3.11
Builders Risk Insurance (0.45% of Construction Costs) | 0.96 | 0.97 | 1.04 | 1.08 | 1.18 | 1.16
Owner's Contingency (5% for Screening Purposes) | 13.37 | 13.49 | 14.59 | 15.02 | 18.34 | 15.38
AFUDC, 2020 MM$ | 19.6532 | 19.8268 | 21.4431 | 22.0801 | 26.9661 | 22.6037
EPC Portion | 14.931 | 15.0955 | 16.2029 | 16.786 | 18.3036 | 18.0894
Non-EPC Portion | 4.7222 | 4.7313 | 5.2402 | 5.2941 | 8.6625 | 4.5143
Total Project Costs, 2020 MM$ | 300.4132 | 303.0668 | 327.7731 | 337.5101 | 412.1961 | 345.5137
EPC Cost Per kW, 2020 $/kW (Based on ICAP kW) | 1340 | 1360 | 1460 | 1510 | 1650 | 1630
Total Cost Per kW, 2020 $/kW (Based on ICAP kW) | 1890 | 1910 | 2070 | 2130 | 2600 | 2180
FIXED O&M COSTS - NATURAL GAS ONLY
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3 | 1.3 | 1.7 | 1.5
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Site Leasing Allowance, 2020$MM/Yr | 0.33 | 0.33 | 0.33 | 0.33 | 3.24 | 0.39
Property Insurance Allowance, 2020$MM/Yr | 1.2798 | 1.2939 | 1.3888 | 1.4388 | 1.5689 | 1.5505
FIXED O&M COSTS - DUAL FUEL
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3 | 1.3 | 1.7 | 1.5
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Site Leasing Allowance, 2020$MM/Yr | 0.33 | 0.33 | 0.33 | 0.33 | 3.24 | 0.39
Property Insurance Allowance, 2020$MM/Yr | 1.2798 | 1.2939 | 1.3888 | 1.4388 | 1.5689 | 1.5505
LEVELIZED MAJOR MAINTENANCE COSTS
Major Maintenance Cost, 2020$/GT-hr or $/engine-hr | 190 | 190 | 190 | 190 | 190 | 190
Major Maintenance Cost, 2020$/GT-start | N/A | N/A | N/A | N/A | N/A | N/A
Major Maintenance Cost, 2020$/MWh | 3 | 3 | 3 | 3 | 3 | 3
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - GAS OPERATION
Total Variable O&M Cost, 2020$/MWh | 10.09 | 9.97 | 9.87 | 9.87 | 10.19 | 9.74
Water Related O&M, $/MWh | 8.37 | 8.24 | 8.14 | 8.14 | 8.46 | 8.01
SCR Related Costs, $/MWh | 0.82 | 0.83 | 0.83 | 0.83 | 0.83 | 0.83
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - FUEL OIL OPERATION
Total Variable O&M Cost, 2020$/MWh | 10.12 | 10.02 | 9.92 | 9.92 | 10.23 | 9.81
Water Related O&M, $/MWh | 8.22 | 8.12 | 8.02 | 8.02 | 8.3 | 7.88
SCR Related Costs, $/MWh | 1 | 1 | 1 | 1 | 1.03 | 1.03
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
CAPITAL COST ADD / DEDUCT FOR GAS ONLY
Capital Costs, 2020 MM$ | 11.3157 | 11.3157 | -11.3157 | -11.3157 | -12.3191 | -12.3191
Owner's Costs, 2020 MM$ | 7 | 7 | -7 | -7 | -7.1 | -7.1
CAPITAL COST ADD / DEDUCT TO REMOVE SCR/CO
Capital Costs, 2020 MM$ | -17.1 | -17.1 | -17.1 | -17.1 | -20.4 | -20.4
Owner's Costs, 2020 MM$ | -0.9 | -0.9 | -0.9 | -0.9 | -1.1 | -1.1
ESTIMATED BASE LOAD OPERATING EMISSIONS: NATURAL GAS
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 166.8 | 166.8 | 166.8 | 166.8 | 166.8 | 166.8
SO2 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
CO | 302.4 | 302.4 | 302.4 | 302.4 | 302.4 | 302.4
CO2 | 208800 | 208800 | 208800 | 208800 | 208800 | 208800
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 13.3 | 13.3 | 13.3 | 13.3 | 13.3 | 13.3
SO2 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
CO | 6.7 | 6.7 | 6.7 | 6.7 | 6.7 | 6.7
CO2 | 208800 | 208800 | 208800 | 208800 | 208800 | 208800
ESTIMATED BASE LOAD OPERATING EMISSIONS: ULTRA-LOW SULFUR FUEL OIL
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 278 | 278 | 278 | 278 | 278 | 278
SO2 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
CO | 81.4 | 81.4 | 81.4 | 81.4 | 81.4 | 81.4
CO2 | 278400 | 278400 | 278400 | 278400 | 278400 | 278400
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 41.7 | 41.7 | 41.7 | 41.7 | 41.7 | 41.7
SO2 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6 | 2.6
CO | 12.2 | 12.2 | 12.2 | 12.2 | 12.2 | 12.2
CO2 | 278400 | 278400 | 278400 | 278400 | 278400 | 278400
Notes
Note 1: Capital cost assumes EPC full wrap methodology. Electrical scope ends at the high side of the GSU.
Note 2: Simple cycle GT starts are not affected by hot, warm or cold conditions. Simple cycle starts assume purge credits are available.
Note 3: MECL start time assumes the min load at which the GT achieves the steady state NOx emissions ppm rate. The SCR compliance start time assumes a cold start, ending at the time when the catalysts are heated and the NOx levels meet the desired SCR emissions.
Note 4: Outage and availability statistics are collected using the NERC Generating Availability Data System. Simple cycle data is based on North American units that came online in 2010 or later. Reporting period is 2012-2019.
Note 5: Degraded performance assumed for all scenarios. For Siemens A65, 2.5% average degradation is assumed. All performance ratings based on NATURAL GAS operation. Minimum loads are based on OEM information at requested ambient conditions.
Note 6: Assumes incoming gas pressure of 250 psig. Compression included in EPC scope. Owner's costs include 5 miles pipeline for all zones except Zone J, which assumes 1 mile. 12" pipeline for aero and F class. 16" pipeline for J class.
Note 7: Capital and fixed O&M costs are presented in 2020 USD $MM.
Note 8: FOM costs assume 7 full time personnel. FOM costs do not include engine lease fees that may be available with LTSA, depending on OEM.
Note 9: Major maintenance $/hr holds for all aero gas turbines. Major maintenance $/hr holds for frame gas turbines where hours per start is >27.
Note 10: VOM assumes the use of temporarily trailers for demineralized water treatment.
Note 11: Emissions estimates are shown for steady state operation at ISO conditions.
Note 12: Fuel Oil emissions based on ultra low sulfur diesel. Per the US EPA, this fuel must meet 15 ppm sulfur.
Note 13: Estimated Costs exclude decommisioning costs and salvage values.

## Raw_F-Class
NYISO DCR TECHNOLOGY ASSESSMENT
SIMPLE CYCLE FRAME F-CLASS
PRELIMINARY AND CONFIDENTIAL - NOT FOR CONSTRUCTION
May 2020 - DRAFT REV 4.1 [AG UPDATED 7.27.2020]
PROJECT TYPE | ZONE C | ZONE F | ZONE G - Dutchess | ZONE G - Rockland | ZONE J | ZONE K
BASE PLANT DESCRIPTION
Number of Gas Turbines | 1 | 1 | 1 | 1 | 1 | 1
Representative Class Gas Turbine | GE 7F.05 | GE 7F.05 | GE 7F.05 | GE 7F.05 | GE 7F.05 | GE 7F.05
Startup Time to Base Load, min | 11 fast / 30 conventional | 11 fast / 30 conventional | 11 fast / 30 conventional | 11 fast / 30 conventional | 11 fast / 30 conventional | 11 fast / 30 conventional
Startup Time to MECL, min | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional
Cold Startup Time to SCR Compliance, min | 45 | 45 | 45 | 45 | 45 | 45
Equivalent Forced Outage Rate Demand, % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Assumed Land Use During Operation, Acres (Not Construction Land Use) | 15 | 15 | 15 | 15 | 12 | 15
Fuel Design | Natural Gas Only | Natural Gas Only | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil)
Inlet Conditioning | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler
Heat Rejection | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger
NOx Control | DLN (Gas) | DLN (Gas) | DLN (Gas), Water Injection (Fuel Oil) | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR
CO Control | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | CO Catalyst | CO Catalyst | CO Catalyst
Particulate Control | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice
Interconnection Voltage, kV | 345 | 345 | 345 | 345 | 345 | 138
Technology Rating | Mature | Mature | Mature | Mature | Mature | Mature
Permitting & Construction Schedule (Years from FNTP) | 3 | 3 | 3 | 3 | 3 | 3
ESTIMATED PERFORMANCE (All BASED ON NATURAL GAS OPERATION)
Summer Performance
Ambient Temperature, °F | 64.39 | 65.46 | 67.14 | 67.14 | 70.71 | 67.8
Relative Humidity, % | 76.02% | 69.1% | 77.21% | 77.21% | 66.44% | 77.3%
Net Plant Output, kW | 215800 | 217000 | 217000 | 217000 | 217800 | 218000
Net Plant Heat Rate, Btu/kWh (HHV) | 10180 | 10180 | 10200 | 10200 | 10210 | 10200
Heat Input, MMBtu/h (HHV) | 2200 | 2210 | 2210 | 2210 | 2220 | 2220
Min Load Plant Output, kW | 93300 | 93600 | 93800 | 93800 | 93600 | 94200
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13360 | 13370 | 13390 | 13390 | 13430 | 13400
Min LoadHeat Input, MMBtu/h (HHV) | 1250 | 1250 | 1260 | 1260 | 1260 | 1260
Winter Performance
Ambient Temperature, °F | 31.96 | 33.13 | 36.05 | 36.05 | 41.19 | 39.5
Relative Humidity, % | 74.44% | 65.62% | 75.54% | 75.54% | 60.9% | 69.2%
Net Plant Output, kW | 224900 | 225900 | 226500 | 226500 | 226900 | 227200
Net Plant Heat Rate, Btu/kWh (HHV) | 9880 | 9880 | 9890 | 9890 | 9900 | 9890
Heat Input, MMBtu/h (HHV) | 2220 | 2230 | 2240 | 2240 | 2250 | 2250
Min Load Plant Output, kW | 93300 | 93800 | 94000 | 94000 | 94200 | 94300
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13630 | 13630 | 13630 | 13630 | 13620 | 13620
Min LoadHeat Input, MMBtu/h (HHV) | 1270 | 1280 | 1280 | 1280 | 1280 | 1280
Spring-Fall (ISO) Performance
Ambient Temperature, °F | 59 | 59 | 59 | 59 | 59 | 59
Relative Humidity, % | 60% | 60% | 60% | 60% | 60% | 60%
Net Plant Output, kW | 219800 | 221000 | 221900 | 221900 | 223000 | 223100
Net Plant Heat Rate, Btu/kWh (HHV) | 10160 | 10160 | 10160 | 10160 | 10160 | 10160
Heat Input, MMBtu/h (HHV) | 2230 | 2250 | 2250 | 2250 | 2270 | 2270
Min Load Plant Output, kW | 91900 | 91100 | 91400 | 91400 | 91900 | 91900
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13630 | 13640 | 13630 | 13630 | 13630 | 13630
Min LoadHeat Input, MMBtu/h (HHV) | 1250 | 1240 | 1250 | 1250 | 1250 | 1250
Summer DMNC Performance
Ambient Temperature, °F | 88.86 | 89.43 | 92.85 | 92.85 | 93.25 | 88.8
Relative Humidity, % | 57.7% | 54.65% | 51.49% | 51.49% | 58.8% | 59%
Net Plant Output, kW | 208700 | 210000 | 210000 | 210000 | 210100 | 211700
Net Plant Heat Rate, Btu/kWh (HHV) | 10360 | 10350 | 10370 | 10350 | 10370 | 10360
Heat Input, MMBtu/h (HHV) | 2160 | 2170 | 2180 | 2170 | 2180 | 2190
Min Load Plant Output, kW | 88400 | 88700 | 88200 | 88200 | 88600 | 89800
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13690 | 13700 | 13760 | 13760 | 13780 | 13690
Min LoadHeat Input, MMBtu/h (HHV) | 1210 | 1220 | 1210 | 1210 | 1220 | 1230
Winter DMNC Performance
Ambient Temperature, °F | 10.84 | 13.23 | 12.48 | 12.48 | 21.15 | 16.5
Relative Humidity, % | 55.67% | 59.08% | 57.55% | 57.55% | 46.44% | 50.2%
Net Plant Output, kW | 225900 | 227100 | 228000 | 228000 | 229200 | 229200
Net Plant Heat Rate, Btu/kWh (HHV) | 9830 | 9830 | 9830 | 9830 | 9850 | 9840
Heat Input, MMBtu/h (HHV) | 2220 | 2230 | 2240 | 2240 | 2260 | 2260
Min Load Plant Output, kW | 93800 | 94200 | 94600 | 94600 | 95100 | 95100
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13690 | 13680 | 13680 | 13680 | 13640 | 13660
Min LoadHeat Input, MMBtu/h (HHV) | 1280 | 1290 | 1290 | 1290 | 1300 | 1300
ICAP Performance
Ambient Temperature, °F | 90 | 90 | 90 | 90 | 90 | 90
Relative Humidity, % | 70% | 70% | 70% | 70% | 70% | 70%
Net Plant Output, kW | 207100 | 208200 | 209100 | 209100 | 210200 | 210200
Net Plant Heat Rate, Btu/kWh (HHV) | 10360 | 10360 | 10360 | 10360 | 10360 | 10360
Heat Input, MMBtu/h (HHV) | 2150 | 2160 | 2170 | 2170 | 2180 | 2180
Min Load Plant Output, kW | 88400 | 88700 | 89100 | 89100 | 89500 | 89500
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13690 | 13720 | 13720 | 13720 | 13720 | 13720
Min LoadHeat Input, MMBtu/h (HHV) | 1210 | 1220 | 1220 | 1220 | 1230 | 1230
ESTIMATED STARTUP FUEL USAGE
Start to Base Load, MMBtu | 140 (fast) / 325 (typ) | 140 (fast) / 325 (typ) | 140 (fast) / 325 (typ) | 140 (fast) / 325 (typ) | 140 (fast) / 325 (typ) | 140 (fast) / 325 (typ)
ESTIMATED CAPITAL AND O&M COSTS
EPC Project Capital Costs, 2020 MM$ (w/o Owner's Costs) | 143.41 | 146.35 | 167.55 | 199.35 | 227.95 | 224.91
Labor | 39.7787 | 41.8578 | 50.095 | 64.9592 | 86.4897 | 84.2284
Materials | 26.9097 | 26.9785 | 32.7138 | 41.0688 | 44.9703 | 44.951
Turbines or Batteries | 38 | 38 | 39.5 | 39.5 | 39.5 | 39.5
Other | 38.7204 | 39.5148 | 45.2375 | 53.8254 | 56.9867 | 56.2265
Owner's Cost Allowances, 2020 MM$ | 59.2 | 59.36 | 68.02 | 69.87 | 116.9 | 62.36
Owner's Project Development | 0.37 | 0.37 | 0.37 | 0.37 | 0.48 | 0.41
Owner's Operational Personnel Prior to COD | 0.44 | 0.44 | 0.44 | 0.44 | 0.57 | 0.48
Owner's Engineer | 1.02 | 1.02 | 1.02 | 1.02 | 1.33 | 1.12
Owner's Project Management | 1.13 | 1.13 | 1.13 | 1.13 | 1.47 | 1.24
Owner's Legal Costs | 1 | 1 | 1 | 1 | 1.3 | 1.1
Owner's Start-up Engineering and Commissioning | 0.27 | 0.27 | 0.27 | 0.27 | 0.35 | 0.3
Sales Tax | 0 | 0 | 0 | 0 | 0 | 0
Construction Power and Water | 0.51 | 0.51 | 0.51 | 0.51 | 0.66 | 0.56
Permitting and Licensing Fees | 1 | 1 | 1 | 1 | 1.3 | 1.1
Switchyard | 10.25 | 10.25 | 10.25 | 10.25 | 43.8 | 5.59
Electrical Interconnection and Deliverability | 11 | 11 | 11 | 11 | 13.01 | 6.5
Gas Interconnection and Reinforcement | 14.3 | 14.3 | 14.3 | 14.3 | 20 | 14.3
System Deliverability Upgrade Costs | 0 | 0 | 0 | 0 | 0 | 0
Emission Reduction Credits | 0.2 | 0.2 | 0.2 | 0.3 | 0.3 | 0.3
Political Concessions & Area Development | 0.5 | 0.5 | 0.5 | 0.5 | 0.65 | 0.55
Startup/Testing (Fuel & Consumables) | 0.83 | 0.83 | 3.1 | 3.1 | 3.1 | 3.1
Initial Fuel Inventory | 0 | 0 | 4.88 | 4.88 | 4.88 | 4.88
Site Security | 0.58 | 0.58 | 0.58 | 0.58 | 0.75 | 0.64
Operating Spare Parts | 5.5 | 5.5 | 5.5 | 5.5 | 5.5 | 5.5
Builders Risk Insurance (0.45% of Construction Costs) | 0.65 | 0.66 | 0.75 | 0.9 | 1.03 | 1.01
Owner's Contingency (5% for Screening Purposes) | 9.65 | 9.8 | 11.22 | 12.82 | 16.42 | 13.68
AFUDC, 2020 MM$ | 14.1827 | 14.3997 | 16.4899 | 18.8454 | 24.1395 | 20.1089
EPC Portion | 10.0387 | 10.2445 | 11.7285 | 13.9545 | 15.9565 | 15.7437
Non-EPC Portion | 4.144 | 4.1552 | 4.7614 | 4.8909 | 8.183 | 4.3652
Total Project Costs, 2020 MM$ | 216.7927 | 220.1097 | 252.0599 | 288.0654 | 368.9895 | 307.3789
EPC Cost Per kW, 2020 $/kW (Based on ICAP kW) | 690 | 700 | 800 | 950 | 1080 | 1070
Total Cost Per kW, 2020 $/kW (Based on ICAP kW) | 1050 | 1060 | 1210 | 1380 | 1760 | 1460
FIXED O&M COSTS
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3 | 1.3 | 1.7 | 1.5
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Site Leasing Allowance, 2020$/MM/Yr | 0.33 | 0.33 | 0.33 | 0.33 | 3.24 | 0.39
Property Insurance Allowance, 2020$MM/Yr | 0.86046 | 0.8781 | 1.0053 | 1.1961 | 1.3677 | 1.3495
FIXED O&M COSTS - DUAL FUEL
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3 | 1.3 | 1.7 | 1.5
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Site Leasing Allowance, 2020$MM/Yr | 0.33 | 0.33 | 0.33 | 0.33 | 3.24 | 0.39
Property Insurance Allowance, 2020$MM/Yr | 0.86046 | 0.8781 | 1.0053 | 1.1961 | 1.3677 | 1.3495
LEVELIZED MAJOR MAINTENANCE COSTS
Major Maintenance Cost, 2020$/GT-hr or $/engine-hr | 350 | 350 | 350 | 350 | 350 | 350
Major Maintenance Cost, 2020$/GT-start | 9500 | 9500 | 9500 | 9500 | 9500 | 9500
Major Maintenance Cost, 2020$/MWh | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - GAS OPERATION
Total Variable O&M Cost, 2020$/MWh | 1.52 | 1.52 | 1.52 | 1.52 | 1.54 | 1.52
Water Related O&M, $/MWh | 0.04 | 0.04 | 0.04 | 0.04 | 0.06 | 0.04
SCR Related Costs, $/MWh | 0.58 | 0.58 | 0.58 | 0.58 | 0.57 | 0.57
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9 | 0.9 | 0.91 | 0.91
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - FUEL OIL OPERATION
Total Variable O&M Cost, 2020$/MWh | 8.84 | 8.84 | 8.84 | 8.84 | 9.21 | 8.83
Water Related O&M, $/MWh | 7.14 | 7.14 | 7.14 | 7.14 | 7.52 | 7.15
SCR Related Costs, $/MWh | 0.8 | 0.8 | 0.8 | 0.8 | 0.79 | 0.79
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.89
CAPITAL COST ADD / DEDUCT FOR GAS ONLY
Capital Costs, 2020 MM$ | 16.9 | 16.9 | -16.9 | -16.9 | -20.1 | -20.1
Owner's Costs, 2020 MM$ | 8.5 | 8.5 | -8.5 | -8.5 | -8.6 | -8.6
CAPITAL COST ADD / DEDUCT TO REMOVE SCR/CO
Capital Costs, 2020 MM$ | 20.6 | 20.6 | 20.6 | -20.6 | -24 | -24
Owner's Costs, 2020 MM$ | 1.1 | 1.1 | 1.1 | -1.1 | -1.3 | -1.3
ESTIMATED BASE LOAD OPERATING EMISSIONS: NATURAL GAS
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 79.9 | 79.9 | 79.9 | 79.9 | 79.9 | 79.9
SO2 | 4.5 | 4.5 | 4.6 | 4.6 | 4.6 | 4.6
CO | 48.6 | 48.6 | 48.6 | 48.6 | 48.6 | 48.6
CO2 | 271200 | 272400 | 273600 | 273600 | 276000 | 276000
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 17.8 | 17.8 | 17.8 | 17.8 | 17.8 | 17.8
SO2 | 4.5 | 4.5 | 4.6 | 4.6 | 4.6 | 4.6
CO | 10.8 | 10.8 | 10.8 | 10.8 | 10.8 | 10.8
CO2 | 271200 | 272400 | 273600 | 273600 | 276000 | 276000
ESTIMATED BASE LOAD OPERATING EMISSIONS: ULTRA-LOW SULFUR FUEL OIL
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 430 | 430 | 430 | 430 | 430 | 430
SO2 | 3.4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
CO | 84.3 | 84.3 | 84.3 | 84.3 | 84.3 | 84.3
CO2 | 361600 | 363200 | 364800 | 364800 | 368000 | 368000
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 64.5 | 64.5 | 64.5 | 64.5 | 64.5 | 64.5
SO2 | 3.4 | 3.5 | 3.5 | 3.5 | 3.5 | 3.5
CO | 14.3 | 14.3 | 14.3 | 14.3 | 14.3 | 14.3
CO2 | 361600 | 363200 | 364800 | 364800 | 368000 | 368000
Notes
Note 1: Capital cost assumes EPC full wrap methodology. Electrical scope ends at the high side of the GSU.
Note 2: Simple cycle GT starts are not affected by hot, warm or cold conditions. Simple cycle starts assume purge credits are available.
Note 3: MECL start time assumes the min load at which the GT achieves the steady state NOx emissions ppm rate. The SCR compliance start time assumes a cold start, ending at the time when the catalysts are heated and the NOx levels meet the desired SCR emissions.
Note 4: Outage and availability statistics are collected using the NERC Generating Availability Data System. Simple cycle data is based on North American units that came online in 2010 or later. Reporting period is 2012-2019.
Note 5: Degraded performance assumed for all scenarios. For frame units, 3% average degradation is assumed. All performance ratings based on NATURAL GAS operation. Minimum loads are based on OEM information at requested ambient conditions.
Note 6: Assumes incoming gas pressure of 250 psig. Compression included in EPC scope. Owner's costs include 5 miles pipeline for all zones except Zone J, which assumes 1 mile. 12" pipeline for aero and F class. 16" pipeline for J class.
Note 7: Capital and fixed O&M costs are presented in 2020 USD $MM.
Note 8: FOM costs assume 7 full time personnel. FOM costs do not include engine lease fees that may be available with LTSA, depending on OEM.
Note 9: Major maintenance $/hr holds for all aero gas turbines. Major maintenance $/hr holds for frame gas turbines where hours per start is >27.
Note 10: VOM assumes the use of temporarily trailers for demineralized water treatment.
Note 11: Emissions estimates are shown for steady state operation at ISO conditions.
Note 12: Fuel Oil emissions based on ultra low sulfur diesel. Per the US EPA, this fuel must meet 15 ppm sulfur.
Note 13: Estimated Costs exclude decommisioning costs and salvage values.

## Raw_J-Class25ppm
NYISO DCR TECHNOLOGY ASSESSMENT
SIMPLE CYCLE FRAME J-CLASS (GE HA.02)
PRELIMINARY AND CONFIDENTIAL - NOT FOR CONSTRUCTION
May 2020 - DRAFT REV 4.1 [AG UPDATED 7.27.2020]
PROJECT TYPE | ZONE C | ZONE F | ZONE G - Dutchess | ZONE G - Rockland | ZONE J | ZONE K
BASE PLANT DESCRIPTION
Number of Gas Turbines | 1 | 1 | 1 | 1 | 1 | 1
Representative Class Gas Turbine | GE 7HA.02 | GE 7HA.02 | GE 7HA.02 | GE 7HA.02 | GE 7HA.02 | GE 7HA.02
Startup Time to Base Load, min | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional
Startup Time to MECL, min | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional
Cold Startup Time to SCR Compliance, min | 45 | 45 | 45 | 45 | 45 | 45
Equivalent Forced Outage Rate Demand, % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Assumed Land Use During Operation, Acres (Not Construction Land Use) | 15 | 15 | 15 | 15 | 12 | 15
Fuel Design | Natural Gas Only | Natural Gas Only | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil)
Inlet Conditioning | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler
Heat Rejection | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger
NOx Control | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR | DLN (Gas), Water Injection (Fuel Oil), SCR
CO Control | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst | CO Catalyst
Particulate Control | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice
Interconnection Voltage, kV | 345 | 345 | 345 | 345 | 345 | 138
Technology Rating | Mature | Mature | Mature | Mature | Mature | Mature
Permitting & Construction Schedule (Years from FNTP) | 3 | 3 | 3 | 3 | 3 | 3
ESTIMATED PERFORMANCE (All BASED ON NATURAL GAS OPERATION)
Summer Performance
Ambient Temperature, °F | 64.39 | 65.46 | 67.14 | 67.14 | 70.71 | 67.8
Relative Humidity, % | 76.02% | 69.1% | 77.21% | 77.21% | 66.44% | 77.3%
Net Plant Output, kW | 355600 | 357700 | 357400 | 357400 | 358700 | 359000
Net Plant Heat Rate, Btu/kWh (HHV) | 9350 | 9350 | 9360 | 9360 | 9370 | 9370
Heat Input, MMBtu/h (HHV) | 3320 | 3340 | 3350 | 3350 | 3360 | 3360
Min Load Plant Output, kW | 141100 | 141600 | 141900 | 141900 | 141700 | 142500
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 11940 | 11940 | 11950 | 11950 | 11970 | 11960
Min LoadHeat Input, MMBtu/h (HHV) | 1690 | 1690 | 1700 | 1700 | 1700 | 1700
Winter Performance
Ambient Temperature, °F | 31.96 | 33.13 | 36.05 | 36.05 | 41.19 | 39.5
Relative Humidity, % | 74.44% | 65.62% | 75.54% | 75.54% | 60.9% | 69.2%
Net Plant Output, kW | 367400 | 369200 | 370200 | 370200 | 370200 | 371100
Net Plant Heat Rate, Btu/kWh (HHV) | 9280 | 9290 | 9300 | 9300 | 9300 | 9300
Heat Input, MMBtu/h (HHV) | 3410 | 3430 | 3440 | 3440 | 3440 | 3450
Min Load Plant Output, kW | 110200 | 110700 | 111000 | 111000 | 111000 | 111300
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13420 | 13420 | 13420 | 13420 | 13390 | 13400
Min LoadHeat Input, MMBtu/h (HHV) | 1480 | 1490 | 1490 | 1490 | 1490 | 1490
Spring-Fall (ISO) Performance
Ambient Temperature, °F | 59 | 59 | 59 | 59 | 59 | 59
Relative Humidity, % | 60% | 60% | 60% | 60% | 60% | 60%
Net Plant Output, kW | 359500 | 361400 | 362900 | 362900 | 364800 | 364900
Net Plant Heat Rate, Btu/kWh (HHV) | 9340 | 9340 | 9340 | 9340 | 9340 | 9340
Heat Input, MMBtu/h (HHV) | 3360 | 3380 | 3390 | 3390 | 3410 | 3410
Min Load Plant Output, kW | 108400 | 107400 | 107800 | 107800 | 108400 | 108400
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13440 | 13450 | 13450 | 13450 | 13440 | 13440
Min LoadHeat Input, MMBtu/h (HHV) | 1460 | 1440 | 1450 | 1450 | 1460 | 1460
Summer DMNC Performance
Ambient Temperature, °F | 88.86 | 89.43 | 92.85 | 92.85 | 93.25 | 88.8
Relative Humidity, % | 57.7% | 54.65% | 51.49% | 51.49% | 58.8% | 59%
Net Plant Output, kW | 346100 | 348200 | 348300 | 348200 | 348500 | 351100
Net Plant Heat Rate, Btu/kWh (HHV) | 9460 | 9450 | 9460 | 9450 | 9470 | 9460
Heat Input, MMBtu/h (HHV) | 3270 | 3290 | 3290 | 3290 | 3300 | 3320
Min Load Plant Output, kW | 133400 | 133700 | 132500 | 132500 | 133300 | 135500
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12120 | 12120 | 12170 | 12170 | 12190 | 12120
Min LoadHeat Input, MMBtu/h (HHV) | 1620 | 1620 | 1610 | 1610 | 1620 | 1640
Winter DMNC Performance
Ambient Temperature, °F | 10.84 | 13.23 | 12.48 | 12.48 | 21.15 | 16.5
Relative Humidity, % | 55.67% | 59.08% | 57.55% | 57.55% | 46.44% | 50.2%
Net Plant Output, kW | 366000 | 368600 | 369900 | 369900 | 374100 | 373000
Net Plant Heat Rate, Btu/kWh (HHV) | 9210 | 9210 | 9210 | 9210 | 9250 | 9230
Heat Input, MMBtu/h (HHV) | 3370 | 3390 | 3410 | 3410 | 3460 | 3440
Min Load Plant Output, kW | 109800 | 110600 | 110900 | 110900 | 112200 | 111900
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13590 | 13590 | 13590 | 13590 | 13500 | 13550
Min LoadHeat Input, MMBtu/h (HHV) | 1490 | 1500 | 1510 | 1510 | 1510 | 1520
ICAP Performance
Ambient Temperature, °F | 90 | 90 | 90 | 90 | 90 | 90
Relative Humidity, % | 70% | 70% | 70% | 70% | 70% | 70%
Net Plant Output, kW | 343700 | 345600 | 347000 | 347000 | 348800 | 348800
Net Plant Heat Rate, Btu/kWh (HHV) | 9460 | 9460 | 9460 | 9460 | 9460 | 9460
Heat Input, MMBtu/h (HHV) | 3250 | 3270 | 3280 | 3280 | 3300 | 3300
Min Load Plant Output, kW | 133400 | 134000 | 134500 | 134500 | 135200 | 135200
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12120 | 12160 | 12160 | 12160 | 12150 | 12150
Min LoadHeat Input, MMBtu/h (HHV) | 1620 | 1630 | 1640 | 1640 | 1640 | 1640
ESTIMATED STARTUP FUEL USAGE
Start to Base Load, MMBtu | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ)
ESTIMATED CAPITAL AND O&M COSTS
EPC Project Capital Costs, 2020 MM$ (w/o Owner's Costs) | 224.17 | 227.24 | 257.13 | 267.44 | 302.49 | 299.43
Labor | 51.9108 | 54.7882 | 63.184 | 72.896 | 99.2194 | 96.7678
Materials | 49.2164 | 48.6388 | 61.1649 | 61.8622 | 65.1948 | 65.2972
Turbines or Batteries | 67 | 67 | 68.5 | 68.5 | 68.5 | 68.5
Other | 56.0424 | 56.809 | 64.283 | 64.1868 | 69.5718 | 68.87
Owner's Cost Allowances, 2020 MM$ | 68.7 | 68.87 | 81.63 | 82.51 | 126.14 | 75.38
Owner's Project Development | 0.37 | 0.37 | 0.37 | 0.37 | 0.48 | 0.41
Owner's Operational Personnel Prior to COD | 0.44 | 0.44 | 0.44 | 0.44 | 0.57 | 0.48
Owner's Engineer | 1.02 | 1.02 | 1.02 | 1.02 | 1.33 | 1.12
Owner's Project Management | 1.13 | 1.13 | 1.13 | 1.13 | 1.47 | 1.24
Owner's Legal Costs | 1 | 1 | 1 | 1 | 1.3 | 1.1
Owner's Start-up Engineering and Commissioning | 0.27 | 0.27 | 0.27 | 0.27 | 0.35 | 0.3
Sales Tax | 0 | 0 | 0 | 0 | 0 | 0
Construction Power and Water | 0.55 | 0.55 | 0.55 | 0.55 | 0.72 | 0.61
Permitting and Licensing Fees | 1 | 1 | 1 | 1 | 1.3 | 1.1
Switchyard | 10.25 | 10.25 | 10.25 | 10.25 | 43.8 | 5.59
Electrical Interconnection and Deliverability | 11 | 11 | 11 | 11 | 13.01 | 6.5
Gas Interconnection and Reinforcement | 17.9 | 17.9 | 17.9 | 17.9 | 20 | 17.9
System Deliverability Upgrade Costs | 0 | 0 | 0 | 0 | 0 | 0
Emission Reduction Credits | 0.07 | 0.07 | 0.07 | 0.4 | 0.4 | 0.4
Political Concessions & Area Development | 0.5 | 0.5 | 0.5 | 0.5 | 0.65 | 0.55
Startup/Testing (Fuel & Consumables) | 1.15 | 1.15 | 4.5 | 4.5 | 4.5 | 4.5
Initial Fuel Inventory | 0 | 0 | 7.24 | 7.24 | 7.24 | 7.24
Site Security | 0.58 | 0.58 | 0.58 | 0.58 | 0.75 | 0.64
Operating Spare Parts | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Builders Risk Insurance (0.45% of Construction Costs) | 1.01 | 1.02 | 1.16 | 1.2 | 1.36 | 1.35
Owner's Contingency (5% for Screening Purposes) | 13.96 | 14.12 | 16.15 | 16.66 | 20.41 | 17.85
AFUDC, 2020 MM$ | 20.5009 | 20.7277 | 23.7132 | 24.4965 | 30.0041 | 26.2367
EPC Portion | 15.6919 | 15.9068 | 17.9991 | 18.7208 | 21.1743 | 20.9601
Non-EPC Portion | 4.809 | 4.8209 | 5.7141 | 5.7757 | 8.8298 | 5.2766
Total Project Costs, 2020 MM$ | 313.3709 | 316.8377 | 362.4732 | 374.4465 | 458.6341 | 401.0467
EPC Cost Per kW, 2020 $/kW (Based on ICAP kW) | 650 | 660 | 740 | 770 | 870 | 860
Total Cost Per kW, 2020 $/kW (Based on ICAP kW) | 910 | 920 | 1040 | 1080 | 1310 | 1150
FIXED O&M COSTS
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3 | 1.3 | 1.7 | 1.5
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Site Leasing Allowance, 2020$/MM/Yr | 0.33 | 0.33 | 0.33 | 0.33 | 3.24 | 0.39
Property Insurance Allowance, 2020$MM/Yr | 1.345 | 1.3634 | 1.5428 | 1.6046 | 1.8149 | 1.7966
FIXED O&M COSTS - DUAL FUEL
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3 | 1.3 | 1.7 | 1.5
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.5 | 1.5 | 1.5 | 1.5 | 1.5 | 1.5
Site Leasing Allowance, 2020$MM/Yr | 0.33 | 0.33 | 0.33 | 0.33 | 3.24 | 0.39
Property Insurance Allowance, 2020$MM/Yr | 1.345 | 1.3634 | 1.5428 | 1.6046 | 1.8149 | 1.7966
LEVELIZED MAJOR MAINTENANCE COSTS
Major Maintenance Cost, 2020$/GT-hr or $/engine-hr | 600 | 600 | 600 | 600 | 600 | 600
Major Maintenance Cost, 2020$/GT-start | 26600 | 26600 | 26600 | 26600 | 26600 | 26600
Major Maintenance Cost, 2020$/MWh | 1.6 | 1.6 | 1.6 | 1.6 | 1.6 | 1.6
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - GAS OPERATION
Total Variable O&M Cost, 2020$/MWh | 1.4 | 1.39 | 1.39 | 1.39 | 1.43 | 1.39
Water Related O&M, $/MWh | 0.03 | 0.03 | 0.03 | 0.03 | 0.05 | 0.03
SCR Related Costs, $/MWh | 0.47 | 0.46 | 0.46 | 0.46 | 0.48 | 0.46
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - FUEL OIL OPERATION
Total Variable O&M Cost, 2020$/MWh | 10.91 | 10.91 | 10.93 | 10.93 | 11.46 | 10.93
Water Related O&M, $/MWh | 9.31 | 9.31 | 9.33 | 9.33 | 9.86 | 9.33
SCR Related Costs, $/MWh | 0.7 | 0.7 | 0.7 | 0.7 | 0.7 | 0.7
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9 | 0.9 | 0.9 | 0.9
CAPITAL COST ADD / DEDUCT FOR GAS ONLY
Capital Costs, 2020 MM$ | 25.4 | 25.4 | -25.4 | -25.4 | -30.2 | -30.2
Owner's Costs, 2020 MM$ | 12.5 | 12.5 | -12.5 | -12.5 | -12.7 | -12.7
CAPITAL COST ADD / DEDUCT TO REMOVE SCR/CO
Capital Costs, 2020 MM$ | N/A | N/A | N/A | N/A | N/A | N/A
Owner's Costs, 2020 MM$ | N/A | N/A | N/A | N/A | N/A | N/A
ESTIMATED BASE LOAD OPERATING EMISSIONS: NATURAL GAS
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 330.5 | 330.5 | 330.5 | 330.5 | 330.5 | 330.5
SO2 | 6.8 | 6.8 | 6.9 | 6.9 | 6.9 | 6.9
CO | 72.4 | 72.4 | 72.4 | 72.4 | 72.4 | 72.4
CO2 | 408000 | 410400 | 411600 | 411600 | 414000 | 414000
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 26.4 | 26.4 | 26.4 | 26.4 | 26.4 | 26.4
SO2 | 6.8 | 6.8 | 6.9 | 6.9 | 6.9 | 6.9
CO | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1
CO2 | 408000 | 410400 | 411600 | 411600 | 414000 | 414000
ESTIMATED BASE LOAD OPERATING EMISSIONS: ULTRA-LOW SULFUR FUEL OIL
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 640 | 640 | 640 | 640 | 640 | 640
SO2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.3 | 5.3
CO | 109.4 | 109.4 | 109.4 | 109.4 | 109.4 | 109.4
CO2 | 544000 | 547200 | 548800 | 548800 | 552000 | 552000
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 96 | 96 | 96 | 96 | 96 | 96
SO2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.3 | 5.3
CO | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6
CO2 | 544000 | 547200 | 548800 | 548800 | 552000 | 552000
Notes
Note 1: Capital cost assumes EPC full wrap methodology. Electrical scope ends at the high side of the GSU.
Note 2: Simple cycle GT starts are not affected by hot, warm or cold conditions. Simple cycle starts assume purge credits are available.
Note 3: MECL start time assumes the min load at which the GT achieves the steady state NOx emissions ppm rate. The SCR compliance start time assumes a cold start, ending at the time when the catalysts are heated and the NOx levels meet the desired SCR emissions.
Note 4: Outage and availability statistics are collected using the NERC Generating Availability Data System. Simple cycle data is based on North American units that came online in 2010 or later. Reporting period is 2012-2019.
Note 5: Degraded performance assumed for all scenarios. For frame units, 3% average degradation is assumed. All performance ratings based on NATURAL GAS operation. Minimum loads are based on OEM information at requested ambient conditions.
Note 6: Assumes incoming gas pressure of 250 psig. Compression included in EPC scope. Owner's costs include 5 miles pipeline for all zones except Zone J, which assumes 1 mile. 12" pipeline for aero and F class. 16" pipeline for J class.
Note 7: Capital and fixed O&M costs are presented in 2020 USD $MM.
Note 8: FOM costs assume 7 full time personnel. FOM costs do not include engine lease fees that may be available with LTSA, depending on OEM.
Note 9: Major maintenance $/hr holds for all aero gas turbines. Major maintenance $/hr holds for frame gas turbines where hours per start is >27.
Note 10: VOM assumes the use of temporarily trailers for demineralized water treatment.
Note 11: Emissions estimates are shown for steady state operation at ISO conditions.
Note 12: Fuel Oil emissions based on ultra low sulfur diesel. Per the US EPA, this fuel must meet 15 ppm sulfur.
Note 13: Estimated Costs exclude decommisioning costs and salvage values.

## Raw_J-Class15ppm
NYISO DCR TECHNOLOGY ASSESSMENT
SIMPLE CYCLE FRAME J-CLASS (GE HA.02)
PRELIMINARY AND CONFIDENTIAL - NOT FOR CONSTRUCTION
May 2020 - DRAFT REV 4.1 [AG UPDATED 7.27.2020]
PROJECT TYPE | ZONE C | ZONE F | ZONE G - Dutchess
BASE PLANT DESCRIPTION
Number of Gas Turbines | 1 | 1 | 1
Representative Class Gas Turbine | GE 7HA.02 | GE 7HA.02 | GE 7HA.02
Startup Time to Base Load, min | 10 fast / 30 conventional | 10 fast / 30 conventional | 10 fast / 30 conventional
Startup Time to MECL, min | 8 fast / 24 conventional | 8 fast / 24 conventional | 8 fast / 24 conventional
Cold Startup Time to SCR Compliance, min | 45 | 45 | 45
Equivalent Forced Outage Rate Demand, % | 4.34% | 4.34% | 4.34%
Assumed Land Use During Operation, Acres (Not Construction Land Use) | 15 | 15 | 15
Fuel Design | Natural Gas Only | Natural Gas Only | Dual Fuel (Natural Gas and Fuel Oil)
Inlet Conditioning | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler
Heat Rejection | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger | Fin Fan Heat Exchanger
NOx Control | DLN (Gas) | DLN (Gas) | DLN (Gas), Water Injection (Fuel Oil)
CO Control | CO Catalyst | CO Catalyst | CO Catalyst
Particulate Control | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice
Interconnection Voltage, kV | 345 | 345 | 345
Technology Rating | Mature | Mature | Mature
Permitting & Construction Schedule (Years from FNTP) | 3 | 3 | 3
ESTIMATED PERFORMANCE (All BASED ON NATURAL GAS OPERATION)
Summer Performance
Ambient Temperature, °F | 64.39 | 65.46 | 67.14
Relative Humidity, % | 76.02% | 69.1% | 77.21%
Net Plant Output, kW | 338000 | 341200 | 340900
Net Plant Heat Rate, Btu/kWh (HHV) | 9370 | 9390 | 9390
Heat Input, MMBtu/h (HHV) | 3170 | 3200 | 3200
Min Load Plant Output, kW | 134100 | 135500 | 134700
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 11970 | 11990 | 12000
Min LoadHeat Input, MMBtu/h (HHV) | 1610 | 1620 | 1620
Winter Performance
Ambient Temperature, °F | 31.96 | 33.13 | 36.05
Relative Humidity, % | 74.44% | 65.62% | 75.54%
Net Plant Output, kW | 346100 | 351000 | 350500
Net Plant Heat Rate, Btu/kWh (HHV) | 9320 | 9320 | 9340
Heat Input, MMBtu/h (HHV) | 3230 | 3270 | 3270
Min Load Plant Output, kW | 103800 | 105300 | 105100
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13480 | 13480 | 13470
Min LoadHeat Input, MMBtu/h (HHV) | 1400 | 1420 | 1420
Spring-Fall (ISO) Performance
Ambient Temperature, °F | 59 | 59 | 59
Relative Humidity, % | 60% | 60% | 60%
Net Plant Output, kW | 340400 | 342200 | 343500
Net Plant Heat Rate, Btu/kWh (HHV) | 9340 | 9350 | 9340
Heat Input, MMBtu/h (HHV) | 3180 | 3200 | 3210
Min Load Plant Output, kW | 101100 | 100200 | 102000
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13470 | 13370 | 13430
Min LoadHeat Input, MMBtu/h (HHV) | 1360 | 1340 | 1370
Summer DMNC Performance
Ambient Temperature, °F | 88.86 | 89.43 | 92.85
Relative Humidity, % | 57.7% | 54.65% | 51.49%
Net Plant Output, kW | 329300 | 334000 | 331600
Net Plant Heat Rate, Btu/kWh (HHV) | 9470 | 9470 | 9480
Heat Input, MMBtu/h (HHV) | 3120 | 3160 | 3140
Min Load Plant Output, kW | 126800 | 128800 | 126700
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12150 | 12150 | 12220
Min LoadHeat Input, MMBtu/h (HHV) | 1540 | 1560 | 1550
Winter DMNC Performance
Ambient Temperature, °F | 10.84 | 13.23 | 12.48
Relative Humidity, % | 55.67% | 59.08% | 57.55%
Net Plant Output, kW | 344700 | 350500 | 350200
Net Plant Heat Rate, Btu/kWh (HHV) | 9250 | 9250 | 9250
Heat Input, MMBtu/h (HHV) | 3190 | 3240 | 3240
Min Load Plant Output, kW | 103400 | 105100 | 105100
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 13650 | 13640 | 13640
Min LoadHeat Input, MMBtu/h (HHV) | 1410 | 1430 | 1430
ICAP Performance
Ambient Temperature, °F | 90 | 90 | 90
Relative Humidity, % | 70% | 70% | 70%
Net Plant Output, kW | 326700 | 328500 | 329900
Net Plant Heat Rate, Btu/kWh (HHV) | 9490 | 9500 | 9490
Heat Input, MMBtu/h (HHV) | 3100 | 3120 | 3130
Min Load Plant Output, kW | 126700 | 127300 | 127900
Min Load Net Plant Heat Rate, Btu/kWh (HHV) | 12190 | 12180 | 12280
Min LoadHeat Input, MMBtu/h (HHV) | 1540 | 1550 | 1570
ESTIMATED STARTUP FUEL USAGE
Start to Base Load, MMBtu | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ) | 240 (fast) / 490 (typ)
ESTIMATED CAPITAL AND O&M COSTS
EPC Project Capital Costs, 2020 MM$ (w/o Owner's Costs) | 180.7347 | 183.801 | 213.697
Labor | 39.0206 | 41.8882 | 50.2829
Materials | 29.5321 | 28.9487 | 41.4786
Turbines or Batteries | 66.9984 | 66.9955 | 68.5006
Other | 45.1837 | 45.9502 | 53.4243
Owner's Cost Allowances, 2020 MM$ | 66.6537 | 66.8215 | 79.5771
Owner's Project Development | 0.37 | 0.37 | 0.37
Owner's Operational Personnel Prior to COD | 0.44 | 0.44 | 0.44
Owner's Engineer | 1.02 | 1.02 | 1.02
Owner's Project Management | 1.13 | 1.13 | 1.13
Owner's Legal Costs | 1 | 1 | 1
Owner's Start-up Engineering and Commissioning | 0.27 | 0.27 | 0.27
Sales Tax | 0 | 0 | 0
Construction Power and Water | 0.55 | 0.55 | 0.55
Permitting and Licensing Fees | 1 | 1 | 1
Switchyard | 10.25 | 10.25 | 10.25
Electrical Interconnection and Deliverability | 11 | 11 | 11
Gas Interconnection and Reinforcement | 17.9 | 17.9 | 17.9
System Deliverability Upgrade Costs | 0 | 0 | 0
Emission Reduction Credits | 0.4 | 0.4 | 0.4
Political Concessions & Area Development | 0.5 | 0.5 | 0.5
Startup/Testing (Fuel & Consumables) | 1.15 | 1.15 | 4.5
Initial Fuel Inventory | 0 | 0 | 7.24
Site Security | 0.58 | 0.58 | 0.58
Operating Spare Parts | 6.5 | 6.5 | 6.5
Builders Risk Insurance (0.45% of Construction Costs) | 0.81331 | 0.8271 | 0.96164
Owner's Contingency (5% for Screening Purposes) | 11.7804 | 11.9344 | 13.9654
AFUDC, 2020 MM$ | 17.3172 | 17.5436 | 20.5292
EPC Portion | 12.6514 | 12.8661 | 14.9588
Non-EPC Portion | 4.6658 | 4.6775 | 5.5704
Total Project Costs, 2020 MM$ | 264.7056 | 268.166 | 313.8033
EPC Cost Per kW, 2020 $/kW (Based on ICAP kW) | 550 | 560 | 650
Total Cost Per kW, 2020 $/kW (Based on ICAP kW) | 810 | 820 | 950
FIXED O&M COSTS
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.5 | 1.5 | 1.5
Site Leasing Allowance, 2020$/MM/Yr | 0.33 | 0.33 | 0.33
Property Insurance Allowance, 2020$MM/Yr | 1.0844 | 1.1028 | 1.2822
FIXED O&M COSTS - DUAL FUEL
Fixed O&M Cost - LABOR, 2020$MM/Yr | 0.9 | 1 | 1.3
Fixed O&M Cost - OTHER, 2020$MM/Yr | 1.5 | 1.5 | 1.5
Site Leasing Allowance, 2020$MM/Yr | 0.33 | 0.33 | 0.33
Property Insurance Allowance, 2020$MM/Yr | 1.0844 | 1.1028 | 1.2822
LEVELIZED MAJOR MAINTENANCE COSTS
Major Maintenance Cost, 2020$/GT-hr or $/engine-hr | 600 | 600 | 600
Major Maintenance Cost, 2020$/GT-start | 26600 | 26600 | 26600
Major Maintenance Cost, 2020$/MWh | 1.6 | 1.6 | 1.6
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - GAS OPERATION
Total Variable O&M Cost, 2020$/MWh | 0.93 | 0.93 | 0.93
Water Related O&M, $/MWh | 0.03 | 0.03 | 0.03
SCR Related Costs, $/MWh | 0 | 0 | 0
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - FUEL OIL OPERATION
Total Variable O&M Cost, 2020$/MWh | 10.21 | 10.21 | 10.21
Water Related O&M, $/MWh | 9.31 | 9.31 | 9.31
SCR Related Costs, $/MWh | 0 | 0 | 0
Other Consumables and Variable O&M, $/MWh | 0.9 | 0.9 | 0.9
CAPITAL COST ADD / DEDUCT FOR GAS ONLY
Capital Costs, 2020 MM$ | 25.4 | 25.4 | -25.4
Owner's Costs, 2020 MM$ | 12.5 | 12.5 | -12.5
CAPITAL COST ADD / DEDUCT TO REMOVE SCR/CO
Capital Costs, 2020 MM$ | N/A | N/A | N/A
Owner's Costs, 2020 MM$ | N/A | N/A | N/A
ESTIMATED BASE LOAD OPERATING EMISSIONS: NATURAL GAS
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 188.6 | 188.6 | 188.6
SO2 | 6.4 | 6.4 | 6.4
CO | 68.9 | 68.9 | 68.9
CO2 | 381600 | 384000 | 385200
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 26.4 | 26.4 | 26.4
SO2 | 6.4 | 6.4 | 6.4
CO | 16.1 | 16.1 | 16.1
CO2 | 381600 | 384000 | 385200
ESTIMATED BASE LOAD OPERATING EMISSIONS: ULTRA-LOW SULFUR FUEL OIL
All GTs Operating, NO SCR / CO Catalyst (lb/hr, HHV)
NOX | 640 | 640 | 640
SO2 | 4.8 | 4.9 | 4.9
CO | 109.4 | 109.4 | 109.4
CO2 | 508800 | 512000 | 513600
All GTs with SCR and CO Catalyst (lb/hr, HHV)
NOX | 96 | 96 | 96
SO2 | 4.8 | 4.9 | 4.9
CO | 18.6 | 18.6 | 18.6
CO2 | 508800 | 512000 | 513600
Notes
Note 1: Capital cost assumes EPC full wrap methodology. Electrical scope ends at the high side of the GSU.
Note 2: Simple cycle GT starts are not affected by hot, warm or cold conditions. Simple cycle starts assume purge credits are available.
Note 3: MECL start time assumes the min load at which the GT achieves the steady state NOx emissions ppm rate. The SCR compliance start time assumes a cold start, ending at the time when the catalysts are heated and the NOx levels meet the desired SCR emissions.
Note 4: Outage and availability statistics are collected using the NERC Generating Availability Data System. Simple cycle data is based on North American units that came online in 2010 or later. Reporting period is 2012-2019.
Note 5: Degraded performance assumed for all scenarios. For frame units, 3% average degradation is assumed. All performance ratings based on NATURAL GAS operation. Minimum loads are based on OEM information at requested ambient conditions.
Note 6: Assumes incoming gas pressure of 250 psig. Compression included in EPC scope. Owner's costs include 5 miles pipeline for all zones except Zone J, which assumes 1 mile. 12" pipeline for aero and F class. 16" pipeline for J class.
Note 7: Capital and fixed O&M costs are presented in 2020 USD $MM.
Note 8: FOM costs assume 7 full time personnel. FOM costs do not include engine lease fees that may be available with LTSA, depending on OEM.
Note 9: Major maintenance $/hr holds for all aero gas turbines. Major maintenance $/hr holds for frame gas turbines where hours per start is >27.
Note 10: VOM assumes the use of temporarily trailers for demineralized water treatment.
Note 11: Emissions estimates are shown for steady state operation at ISO conditions.
Note 12: Fuel Oil emissions based on ultra low sulfur diesel. Per the US EPA, this fuel must meet 15 ppm sulfur.
Note 13: Estimated Costs exclude decommisioning costs and salvage values.

## Raw_J-Class_CC
NYISO DCR TECHNOLOGY ASSESSMENT
COMBINED CYCLE 1x1 GE HA.02
PRELIMINARY AND CONFIDENTIAL - NOT FOR CONSTRUCTION
May 2020 - DRAFT REV 4.1 [AG UPDATED 7.27.2020]
PROJECT ZONE: | ZONE C | ZONE F | ZONE G - Dutchess | ZONE G - Rockland | ZONE J | ZONE K
BASE PLANT DESCRIPTION | 1x1 GE HA.02 | 1x1 GE HA.02 | 1x1 GE HA.02 | 1x1 GE HA.02 | 1x1 GE HA.02 | 1x1 GE HA.02
Number of Gas Turbines | 1 | 1 | 1 | 1 | 1 | 1
Number of Steam Turbines | 1 | 1 | 1 | 1 | 1 | 1
Representative Class Gas Turbine | GE 7HA.02 | GE 7HA.02 | GE 7HA.02 | GE 7HA.02 | GE 7HA.02 | GE 7HA.02
Steam Conditions (Main Steam / Reheat) | 1,085°F / 1,085°F | 1,085°F / 1,085°F | 1,085°F / 1,085°F | 1,085°F / 1,085°F | 1,085°F / 1,085°F | 1,085°F / 1,085°F
Main Steam Pressure | 2330 | 2330 | 2330 | 2330 | 2330 | 2330
Steam Cycle Type | Subcritical | Subcritical | Subcritical | Subcritical | Subcritical | Subcritical
Startup Time, Minutes (Cold Start to Unfired Base Load) | 180 | 180 | 180 | 180 | 180 | 180
Startup Time, Minutes (Warm Start to Unfired Base Load) | 120 | 120 | 120 | 120 | 120 | 120
Startup Time, Minutes (Hot Start to Unfired Base Load) | 80 | 80 | 80 | 80 | 80 | 80
Startup Time, Minutes (Cold Start to Stack Emissions Compliance) | 60 | 60 | 60 | 60 | 60 | 60
Equivalent Forced Outage Rate Demand, % | 2.92% | 2.92% | 2.92% | 2.92% | 2.92% | 2.92%
Assumed Land Use During Operation, Acres (Not Construction Land Use) | 30 | 30 | 30 | 30 | 27 | 30
Fuel Design | Natural Gas Only | Natural Gas Only | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil) | Dual Fuel (Natural Gas and Fuel Oil)
Inlet Conditioning | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler | Evaporative Cooler
Heat Rejection | Air Cooled Condenser (ACC) | Air Cooled Condenser (ACC) | Air Cooled Condenser (ACC) | Air Cooled Condenser (ACC) | Air Cooled Condenser (ACC) | Air Cooled Condenser (ACC)
NOx Control | DLN/SCR | DLN/SCR | DLN/SCR | DLN/SCR | DLN/SCR | DLN/SCR
CO Control | Oxidation Catalyst | Oxidation Catalyst | Oxidation Catalyst | Oxidation Catalyst | Oxidation Catalyst | Oxidation Catalyst
Particulate Control | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice | Good Combustion Practice
Interconnection Voltage, kV | 345 | 345 | 345 | 345 | 345 | 345
Technology Rating | Mature | Mature | Mature | Mature | Mature | Mature
Permitting & Construction Schedule (Years from FNTP) | 4 | 4 | 4 | 4 | 4 | 4
ESTIMATED PERFORMANCE
Base Load Performance @ ICAP: 90 °F ¦ 70% RH (Nominal)
Net Plant Output, kW | 495100 | 498500 | 500600 | 500600 | 502200 | 502500
Net Plant Heat Rate, Btu/kWh (HHV) | 6410 | 6400 | 6400 | 6400 | 6410 | 6410
Heat Input, MMBtu/h (HHV) | 3170 | 3190 | 3200 | 3200 | 3220 | 3220
Incremental Duct Fired Performance @ ICAP: 90 °F ¦ 70% RH (Nominal)
Incremental Duct Fired Output, kW | 103800 | 104200 | 103200 | 103200 | 102900 | 107700
Incremental Heat Rate, Btu/kWh (HHV) | 8530 | 8540 | 8550 | 8550 | 8600 | 8530
Incremental Heat Input, MMBtu/h (HHV) | 890 | 890 | 880 | 880 | 880 | 920
Minimum Load (Single Turbine at MECL) @ ICAP: 90 °F ¦ 70% RH (Nominal)
Net Plant Output, kW | 221500 | 223400 | 224400 | 224400 | 225300 | 224900
Net Plant Heat Rate, Btu/kWh (HHV) | 7340 | 7320 | 7320 | 7320 | 7320 | 7340
Heat Input, MMBtu/h (HHV) | 1630 | 1640 | 1640 | 1640 | 1650 | 1650
Base Load Performance @ Winter DMNC
Net Plant Output, kW | 530000 | 532500 | 536300 | 536300 | 544900 | 542600
Net Plant Heat Rate, Btu/kWh (HHV) | 6390 | 6390 | 6390 | 6390 | 6380 | 6380
Heat Input, MMBtu/h (HHV) | 3390 | 3400 | 3430 | 3430 | 3480 | 3460
Incremental Duct Fired Performance @ Winter DMNC
Incremental Duct Fired Output, kW | 110400 | 110900 | 108800 | 108800 | 105600 | 111900
Incremental Heat Rate, Btu/kWh (HHV) | 8740 | 8740 | 8740 | 8740 | 8700 | 8730
Incremental Heat Input, MMBtu/h (HHV) | 960 | 970 | 950 | 950 | 920 | 980
Minimum Load (Single Turbine at MECL) @ Winter DMNC
Net Plant Output, kW | 196100 | 197100 | 198400 | 198400 | 200400 | 200000
Net Plant Heat Rate, Btu/kWh (HHV) | 7650 | 7650 | 7630 | 7630 | 7590 | 7620
Heat Input, MMBtu/h (HHV) | 1500 | 1510 | 1510 | 1510 | 1520 | 1520
Base Load Performance @ Winter
Net Plant Output, kW | 539200 | 542100 | 544800 | 544800 | 546700 | 547800
Net Plant Heat Rate, Btu/kWh (HHV) | 6360 | 6360 | 6350 | 6350 | 6350 | 6340
Heat Input, MMBtu/h (HHV) | 3430 | 3450 | 3460 | 3460 | 3470 | 3470
Incremental Duct Fired Performance @ Winter
Incremental Duct Fired Output, kW | 104100 | 104200 | 102700 | 102700 | 101600 | 106700
Incremental Heat Rate, Btu/kWh (HHV) | 8720 | 8720 | 8730 | 8730 | 8710 | 8730
Incremental Heat Input, MMBtu/h (HHV) | 910 | 910 | 900 | 900 | 880 | 930
Minimum Load (Single Turbine at MECL) @ Winter
Net Plant Output, kW | 197000 | 198000 | 198700 | 198700 | 199300 | 199500
Net Plant Heat Rate, Btu/kWh (HHV) | 7570 | 7560 | 7550 | 7550 | 7530 | 7540
Heat Input, MMBtu/h (HHV) | 1490 | 1500 | 1500 | 1500 | 1500 | 1500
Base Load Performance @ Spring / Fall
Net Plant Output, kW | 520400 | 532900 | 535000 | 535000 | 536800 | 537600
Net Plant Heat Rate, Btu/kWh (HHV) | 6300 | 6300 | 6300 | 6300 | 6310 | 6300
Heat Input, MMBtu/h (HHV) | 3280 | 3360 | 3370 | 3370 | 3390 | 3390
Incremental Unfired Performance with Evaporative Coolers @ Spring / Fall
Incremental Output with Evap Coolers, kW | 3900 | 3900 | 3900 | 3900 | 3900 | 3900
Net Plant Heat Rate with Evap Coolers, Btu/kWh (HHV) | 8590 | 8580 | 8590 | 8590 | 8600 | 8580
Incremental Duct Fired Performance with Evaporative Coolers @ Spring / Fall
Incremental Duct Fired Output, kW | 99900 | 100400 | 99400 | 99400 | 99800 | 104400
Incremental Heat Rate, Btu/kWh (HHV) | 8850 | 8830 | 8830 | 8830 | 8810 | 8860
Incremental Heat Input, MMBtu/h (HHV) | 880 | 890 | 880 | 880 | 880 | 920
Minimum Load (Single Turbine at MECL) @ Spring / Fall
Net Plant Output, kW | 191500 | 192600 | 193400 | 193400 | 194500 | 194300
Net Plant Heat Rate, Btu/kWh (HHV) | 7540 | 7540 | 7530 | 7530 | 7530 | 7540
Heat Input, MMBtu/h (HHV) | 1440 | 1450 | 1460 | 1460 | 1460 | 1470
Base Load Performance @ Summer
Net Plant Output, kW | 509900 | 513300 | 514700 | 514700 | 512300 | 517900
Net Plant Heat Rate, Btu/kWh (HHV) | 6370 | 6360 | 6360 | 6360 | 6370 | 6370
Heat Input, MMBtu/h (HHV) | 3250 | 3260 | 3270 | 3270 | 3260 | 3300
Incremental Duct Fired Performance @ Summer
Incremental Duct Fired Output, kW | 103100 | 103000 | 102200 | 102200 | 103600 | 107200
Incremental Heat Rate, Btu/kWh (HHV) | 8580 | 8610 | 8590 | 8590 | 8600 | 8590
Incremental Heat Input, MMBtu/h (HHV) | 880 | 890 | 880 | 880 | 890 | 920
Minimum Load (Single Turbine at MECL) @ Summer
Net Plant Output, kW | 232100 | 233400 | 234000 | 234000 | 232300 | 235700
Net Plant Heat Rate, Btu/kWh (HHV) | 7130 | 7130 | 7130 | 7130 | 7180 | 7130
Heat Input, MMBtu/h (HHV) | 1650 | 1660 | 1670 | 1670 | 1670 | 1680
Base Load Performance @ Summer DMNC
Net Plant Output, kW | 486000 | 488300 | 486500 | 486500 | 484700 | 501600
Net Plant Heat Rate, Btu/kWh (HHV) | 6410 | 6410 | 6410 | 6410 | 6440 | 6400
Heat Input, MMBtu/h (HHV) | 3120 | 3130 | 3120 | 3120 | 3120 | 3210
Incremental Unfired Performance with Evaporative Coolers @ Summer DMNC
Incremental Output with Evap Coolers, kW | 28200 | 28200 | 33000 | 33000 | 35300 | 19100
Incremental Heat Rate with Evap Coolers, Btu/kWh (HHV) | 6590 | 6640 | 6400 | 6400 | 6600 | 6420
Incremental Fired Performance with Evaporative Coolers @ Summer DMNC
Incremental Output with Evap Coolers, kW | 100400 | 100300 | 99700 | 99700 | 98900 | 104600
Incremental Heat Rate with Evap Coolers, Btu/kWh (HHV) | 8660 | 8650 | 8640 | 8640 | 8770 | 8590
Incremental Heat Input, MMBtu/h (HHV) | 870 | 870 | 860 | 860 | 870 | 900
Minimum Load (Single Turbine at MECL) @ Summer DMNC
Net Plant Output, kW | 216900 | 218300 | 217400 | 217400 | 216500 | 224300
Net Plant Heat Rate, Btu/kWh (HHV) | 7370 | 7350 | 7370 | 7370 | 7400 | 7330
Heat Input, MMBtu/h (HHV) | 1600 | 1600 | 1600 | 1600 | 1600 | 1640
ESTIMATED STARTUP FUEL USAGE
Start to Unfired Base Load, MMBtu (WARM Start) | 3940 | 3940 | 3940 | 3940 | 3940 | 3940
ESTIMATED CAPITAL AND O&M COSTS
EPC Project Capital Costs, 2020 MM$ (w/o Owner's Costs) | 511.6 | 524.15 | 568.83 | 611.36 | 696.47 | 690.37
Labor | 154.9754 | 166.4038 | 189.8406 | 228.4151 | 295.8498 | 291.0298
Materials | 161.7239 | 162.3314 | 168.2856 | 169.2446 | 171.9294 | 170.6734
Turbines or Batteries | 67 | 67 | 68.5 | 68.5 | 68.5 | 68.5
Other | 127.8998 | 128.4174 | 142.2087 | 145.1973 | 160.1873 | 160.1656
Owner's Cost Allowances, 2020 MM$ | 106.4 | 107.09 | 121.65 | 125.03 | 177.45 | 131.34
Owner's Project Development | 3.5 | 3.5 | 3.5 | 3.5 | 4.55 | 3.85
Owner's Operational Personnel Prior to COD | 2.4 | 2.4 | 2.4 | 2.4 | 3.12 | 2.64
Owner's Engineer | 2.6 | 2.6 | 2.6 | 2.6 | 3.38 | 2.86
Owner's Project Management | 4.8 | 4.8 | 4.8 | 4.8 | 6.24 | 5.28
Owner's Legal Costs | 1 | 1 | 1 | 1 | 1.3 | 1.1
Owner's Start-up Engineering and Commissioning | 0.54 | 0.54 | 0.54 | 0.54 | 0.7 | 0.59
Sales Tax | 0 | 0 | 0 | 0 | 0 | 0
Construction Power and Water | 1.54 | 1.54 | 1.54 | 1.54 | 2 | 1.69
Permitting and Licensing Fees | 1 | 1 | 1 | 1 | 1.3 | 1.1
Switchyard | 18.94 | 18.94 | 18.94 | 18.94 | 54.63 | 18.94
Electrical Interconnection and Deliverability | 11 | 11 | 11 | 11 | 13.01 | 11
Gas Interconnection and Reinforcement | 17.9 | 17.9 | 17.9 | 17.9 | 20 | 17.9
System Deliverability Upgrade Costs | 0 | 0 | 0 | 0 | 0 | 0
Emission Reduction Credits | 0.2 | 0.2 | 0.2 | 1.2 | 1.2 | 1.2
Political Concessions & Area Development | 0.5 | 0.5 | 0.5 | 0.5 | 0.65 | 0.55
Startup/Testing (Fuel & Consumables) | 1.15 | 1.15 | 5.45 | 5.45 | 5.45 | 5.45
Initial Fuel Inventory | 0 | 0 | 7.24 | 7.24 | 7.24 | 7.24
Site Security | 1.1 | 1.1 | 1.1 | 1.1 | 1.43 | 1.21
Operating Spare Parts | 6.5 | 6.5 | 6.5 | 6.5 | 6.5 | 6.5
Builders Risk Insurance (0.45% of Construction Costs) | 2.3 | 2.36 | 2.56 | 2.75 | 3.13 | 3.11
Owner's Contingency (5% for Screening Purposes) | 29.43 | 30.06 | 32.88 | 35.07 | 41.62 | 39.13
AFUDC, 2020 MM$ | 43.26 | 44.1868 | 48.3336 | 51.5473 | 61.1744 | 57.5197
EPC Portion | 35.812 | 36.6905 | 39.8181 | 42.7952 | 48.7529 | 48.3259
Non-EPC Portion | 7.448 | 7.4963 | 8.5155 | 8.7521 | 12.4215 | 9.1938
Total Project Costs, 2020 MM$ | 661.26 | 675.4268 | 738.8136 | 787.9373 | 935.0944 | 879.2297
EPC Cost Per UNFIRED kW, 2020 $/kW (Based on ICAP kW) | 1030 | 1050 | 1140 | 1220 | 1390 | 1370
Total Cost Per UNFIRED kW, 2020 $/kW (Based on ICAP kW) | 1340 | 1350 | 1480 | 1570 | 1860 | 1750
EPC Cost Per FIRED kW, 2020 $/kW (Based on ICAP kW) | 850 | 870 | 940 | 1010 | 1150 | 1130
Total Cost Per FIRED kW, 2020 $/kW (Based on ICAP kW) | 1100 | 1120 | 1220 | 1300 | 1550 | 1440
FIXED O&M COSTS
Fixed O&M Cost - LABOR, 2020$MM/Yr | 2.8286 | 3.1429 | 4.0857 | 4.0857 | 5.3429 | 4.7143
Fixed O&M Cost - OTHER, 2020$MM/Yr | 2.14 | 2.14 | 2.14 | 2.14 | 2.14 | 2.14
Site Leasing Allowance, 2020$/MM/Yr | 0.66 | 0.66 | 0.66 | 0.66 | 7.29 | 0.78
Property Insurance Allowance, 2020$MM/Yr | 3.0696 | 3.1449 | 3.413 | 3.6682 | 4.1788 | 4.1422
FIXED O&M COSTS - DUAL FUEL
Fixed O&M Cost - LABOR, 2020$MM/Yr | 2.8286 | 3.1429 | 4.0857 | 4.0857 | 5.3429 | 4.7143
Fixed O&M Cost - OTHER, 2020$MM/Yr | 2.14 | 2.14 | 2.14 | 2.14 | 2.14 | 2.14
Site Leasing Allowance, 2020$MM/Yr | 0.66 | 0.66 | 0.66 | 0.66 | 7.29 | 0.78
Property Insurance Allowance, 2020$MM/Yr | 3.0696 | 3.1449 | 3.413 | 3.6682 | 4.1788 | 4.1422
LEVELIZED CAPITAL MAINTENANCE COSTS
Major Maintenance Cost, 2020 $/GT-hr | 600 | 600 | 600 | 600 | 600 | 600
Major Maintenance Cost, 2020$/GT-start | 26600 | 26600 | 26600 | 26600 | 26600 | 26600
Major Maintenance Cost, 2020 $/MWh | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - GAS OPERATION
Total Variable O&M Cost, 2020 $/MWh | 1.59 | 1.59 | 1.59 | 1.59 | 1.61 | 1.58
Water Related O&M ($/MWh) | 0.05 | 0.05 | 0.05 | 0.05 | 0.07 | 0.05
SCR Related Costs, $/MWh | 0.32 | 0.32 | 0.32 | 0.32 | 0.32 | 0.32
Other Consumables and Variable O&M ($/MWh) | 1.22 | 1.22 | 1.22 | 1.22 | 1.22 | 1.21
Incremental Duct Fired Variable O&M, 2020 $/MWh (excl. GT major maint.) | 0.66 | 0.66 | 0.66 | 0.66 | 0.66 | 0.66
Water Related O&M ($/MWh) | 0.11 | 0.11 | 0.11 | 0.11 | 0.12 | 0.09
SCR Reagent, $/MWh | 0.13 | 0.13 | 0.13 | 0.13 | 0.13 | 0.13
Other Consumables and Variable O&M ($/MWh) | 0.42 | 0.42 | 0.42 | 0.42 | 0.41 | 0.44
NON-FUEL VARIABLE O&M COSTS (EXCLUDES MAJOR MAINTENANCE) - FUEL OIL OPERATION
Total Variable O&M Cost, 2020 $/MWh | 2.45 | 2.45 | 2.45 | 2.45 | 2.84 | 2.48
Water Related O&M ($/MWh) | 0.75 | 0.75 | 0.75 | 0.75 | 1.15 | 0.78
SCR Related Costs, $/MWh | 0.5 | 0.5 | 0.5 | 0.5 | 0.46 | 0.48
Other Consumables and Variable O&M ($/MWh) | 1.2 | 1.2 | 1.2 | 1.2 | 1.23 | 1.22
Incremental Duct Fired Variable O&M, 2020 $/MWh (excl. GT major maint.) | N/A | N/A | N/A | N/A | N/A | N/A
Water Related O&M ($/MWh) | N/A | N/A | N/A | N/A | N/A | N/A
SCR Reagent, $/MWh | N/A | N/A | N/A | N/A | N/A | N/A
Other Consumables and Variable O&M ($/MWh) | N/A | N/A | N/A | N/A | N/A | N/A
CAPITAL COST ADD / DEDUCT FOR GAS ONLY
Capital Costs, 2020 MM$ | 25.4 | 25.4 | -25.4 | -25.4 | -30.2 | -30.2
Owner's Costs, 2020 MM$ | 13.511 | 13.511 | -13.511 | -13.511 | -13.7726 | -13.7726
ESTIMATED BASE LOAD OPERATING EMISSIONS, lb/MMBtu (HHV)
NOX | 26.4 | 26.4 | 26.4 | 26.4 | 26.4 | 26.4
SO2 | 6.6 | 6.7 | 6.7 | 6.7 | 6.8 | 6.8
CO | 16.1 | 16.1 | 16.1 | 16.1 | 16.1 | 16.1
CO2 | 393600 | 403200 | 404400 | 404400 | 406800 | 406800
ESTIMATED BASE LOAD OPERATING EMISSIONS: ULTRA-LOW SULFUR FUEL OIL
NOX | 96 | 96 | 96 | 96 | 96 | 96
SO2 | 5.2 | 5.2 | 5.2 | 5.2 | 5.3 | 5.3
CO | 18.6 | 18.6 | 18.6 | 18.6 | 18.6 | 18.6
CO2 | 544000 | 547200 | 548800 | 548800 | 552000 | 552000
Notes
Note 1: Capital cost assumes EPC full wrap methodology. Electrical scope ends at the high side of the GSU. CCGT unit includes duct firing capability.
Note 2: Performance ratings were determined using heat balance modeling software. Performance is based on 1.8% average degradation for capacity and 1.1% average degradation for heat rate. All performance is based on NATURAL GAS operation. Min load ratings are based on OEM performance information at specified ambient conditions.
Note 3: Variable O&M costs are based on performance at ISO conditions.
Note 4: Capital and fixed O&M costs are presented in 2020 USD $MM.
Note 5: Major maintenance $/hr holds for frame gas turbines where hours per start is >27.
Note 6: The duct firing incremental values note incremental performance output. The incremental heat rate reflects the effective heat rate of the additional output due to the duct burners.
Note 7: Startup time to stack emissions compliance is not the same as the start time for gas turbine MECL. Stack emissions compliance is expected to be limited by the temperature of the CO catalyst, which impacts VOC emissions.
Note 8: Outage and availability statistics are collected using the NERC Generating Availability Data System. Combined cycle data is based on North American units that came online in 2010 or later. Reporting period is 2012-2019.
Note 9: Cold start is >72 hours after shutdown. Hot start is <8 hours after shutdown.
Note 10: Startup times reflect unrestricted, conventional starts for all gas turbines. These start times assume the inclusion of terminal point desuperheaters, full bypass, and associated controls. Fast start packages are not included in CCGT plants.
Note 14: Fixed O&M assumes 22 FTE for a 1x1 configuration.
Note 15: Variable O&M costs assume onsite demineralized water treatment system (included in EPC cost).
Note 16: Emissions estimates are shown for steady state operation at ISO conditions. Estimates account for the impacts of SCR and CO catalysts.
Note 17: Estimated costs exclude decommisioning costs and salvage values.