## Legend
SERIES REACTORS ON 77 AND 78 LINES BY-PASSED
| Base Case Dispatch Distribution of | Niagara 115 kV units | Niagara 230 kV units | Lewiston
| Niagara Generation 115 kV vs. 230 kV units | MW Output | MW Output | MW Output
| Dispatch 1 | 1140 | 1320 | 240
| Dispatch 2 | 1540 | 920 | 240
Minimum Criteria:
Baseline results according to the minimum sufficiency criteria
Additional Information Beyond Minimum Criteria:
Transmission security results (N-1 and N-2) to provide additional information to developers showing potential overloads under conditions when importing the full 1000 MW from Ontario
Note for N-1-0 Analysis:
The term "base case" is used to describe violations where the system could not be adjusted following the first contingency to adequately secure the system to an element's continuous rating (Rate A)
| Sheet Name | Transmission Security Analysis | Transfer Criteria (Normal or Emergency) | OH -> NY Interchange (MW) | Ontario Re-Dispatch Adjustment (if applicable) | Public Policy Transmission Need Criteria
| Minimum_Criteria | Summary of the thermal and voltage violations under N-1, N-1-0, and N-1-1 conditions of the Public Policy Transmission Need
| Additional_Info_Beyond_Criteria | Summary of the informative thermal violations under N-1 and N-2 conditions beyond the mandatory criteria
| N-1_ETC_OH_1000 | N-1 | Emergency | 1000 | NA | Minimum Criteria
| N-1_NTC_OH_0 | N-1 | Normal | 0 | NA | Minimum Criteria
| N-1-1_NTC_OH_1000_Adjust | N-1-0 and N-1-1 | Normal | 1000 | Ontario Allowed to Adjust to an OH->NY Interchange of 0 MW | Minimum Criteria
| N-1-1_ETC_OH_1000_Adjust | N-1-0 and N-1-1 | Emergency | 1000 | Ontario Allowed to Adjust to an OH->NY Interchange of 0 MW | Minimum Criteria
| N-1_NTC_OH_1000 | N-1 | Normal | 1000 | NA | Additional Info Beyond Criteria
| N-2_NTC_OH_1000_Fixed | N-2 | Normal | 1000 | Ontario Dispatch Fixed | Additional Info Beyond Criteria
| N-2_ETC_OH_1000_Fixed | N-2 | Emergency | 1000 | Ontario Dispatch Fixed | Additional Info Beyond Criteria
| Ratings_Minimum_Criteria | Contains information on limiting equipment which the ratings are based for elements identified in the "Minimum_Criteria" tab
| Ratings_Beyond_Criteria | Contains information on limiting equipment which the ratings are based for elements identified in the "Additional_Infp_Beyond_Criteria" tab

## Minimum_Criteria
SERIES REACTORS ON 77 AND 78 LINES BY-PASSED
N-1 Thermal Overloads (Emergency Transfer Criteria) - 1000 MW Ontario Import
| Monitored Facility | Applicable | Dispatch 1 - Niagara 230 kV Max |  | Dispatch 2 - Niagara 115 kV Max
|  | Rating [MVA] | Contingency | AC % Loading | Contingency | AC % Loading
| 135303 SAWYER77 230 135415 PACKARD2 230 1 | 704 | B:PACKT3 | 117.27 | S:PA_HNTL78 | 111.11
| 135304 SAWYER78 230 135415 PACKARD2 230 2 | 746 | S:PA_HNTL77 | 110.19 | S:PA_HNTL77 | 105.06
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 755 | B:PACKT3 | 101.13 | - | -
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | 755 | OE:PACK_77 | 100.29 | - | -
N-1 Thermal Overloads (Normal Transfer Criteria) - 0 MW Ontario Import
| Monitored Facility | Applicable | Dispatch 1 - Niagara 230 kV Max |  | Dispatch 2 - Niagara 115 kV Max
|  | Rating [MVA] | Contingency | AC % Loading | Contingency | AC % Loading
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 166 | T:77&78 | 114.14 | T:77&78 | 119.04
| 130762 GARDV230 230 130767 STOLE230 230 1 | 478 | T:77&78 | 112.32 | T:77&78 | 108.09
| 135304 SAWYER78 230 135415 PACKARD2 230 2 | 644 | S:PA_HNTL77 | 108.34 | S:PA_HNTL77 | 102.21
| 135303 SAWYER77 230 135415 PACKARD2 230 1 | 644 | S:PA_HNTL78 | 108.12 | S:PA_HNTL78 | 102
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 (See footnote) | 841 | T:61&64 | 103.3413 | T:61&64 | 87.17
| 130847 ROLL 115 115 130857 STOLE115 115 1 | 90 | SB:181:ER | 103.22 | SB:181:ER | 102.95
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 (See footnote) | 351 | DCT:115:193+194 | 101.47 | DCT:115:193+194 | 121.0226
| 135450 GRDNVL1 115 135453 LONG-180 115 1 | 166 | DCT:230:77+78+THR | 101.07 | DCT:230:77+78+THR | 108.23
| 130795 DEPEW115 115 130799 ERIE 115 115 1 | 119 | SB:PK115 30+40 | 100.75 | SB:PK115 30+40 | 100.81
| 135460 PACK(N)E 115 147850 NIAG115E 115 2 (See footnote) | 328 | DCT:115:101+191 | 90.82 | DCT:115:101+191 | 110.6
| 135460 PACK(N)E 115 135538 LONG-182 115 1 | 208 | - | - | DCT:230:77+78 | 103.73
| 135449 GR.I-182 115 135459 NI.B-182 115 1 | 181 | - | - | DCT:230:77+78+THR | 101.07
Footnote - Uses NYSRC Reliability Rule Exception #13. Developer must ensure that sufficient generation can be reduced at Niagara to return the flows to less than their STE ratings within 5 minutes and to less than their LTE ratings within 10 minutes from the initial overload.
N-1-0 Thermal Overloads (Normal Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
|  |  | Dispatch 1 |  |  | Dispatch 2
| Monitored Facility | Applicable Rating [MVA] | First Contingency | Second Contingency | AC %Loading | First Contingency | Second Contingency | AC %Loading
| 135304 SAWYER78 230 135415 PACKARD2 230 2 | 556 | HUNTLEY - PACKARD 77 230 | Base Case | 109.74 | HUNTLEY - PACKARD 77 230 | Base Case | 101.66
| 135303 SAWYER77 230 135415 PACKARD2 230 1 | 556 | HUNTLEY - PACKARD 78 230 | Base Case | 108.56 | HUNTLEY - PACKARD 78 230 | Base Case | 101.37
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 620 | NIAGARA - PACKARD 62 230 | Base Case | 107.79 | - | - | -
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 620 | NIAGARA - PACKARD 61 230 | Base Case | 107.68 | - | - | -
N-1-1 Thermal Overloads (Normal Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
|  |  | Dispatch 1 |  |  | Dispatch 2
| Monitored Facility | Applicable Rating [MVA] | First Contingency | Second Contingency | AC %Loading | First Contingency | Second Contingency | AC %Loading
| 130762 GARDV230 230 130767 STOLE230 230 1 | 478 | R:HC-SR_37&W-F_171 | T:77&78 | 122.33 | R:HC-SR_37&W-F_171 | T:77&78 | 122.56
| 135304 SAWYER78 230 135415 PACKARD2 230 2 | 644 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 115.53 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 77 230 | 107.57
| 135303 SAWYER77 230 135415 PACKARD2 230 1 | 644 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 114.33 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 107.34
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | 654 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 104.23 | - | - | -
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 654 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 103.28 | - | - | -
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 (See footnote) | 841 | NIAG - NEWROCH 1 345 | T:61&64 | 100.4056 | R:HC-SR_37&W-F_171 | T:61&64 | 86.65
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 (See footnote) | 288 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 100.39 | - | - | -
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 (See footnote) | 841 | NIAGARA - ROBINSON 64 230 | T:62&BP76 | 100.2095 | STOLLRD - GARDENVILL 66 230 | T:62&BP76 | 86.4
| 135497 ZRMN-133 115 135562 S214-133 115 1 | 206 | - | - | - | PACKARD 230/115 4TR | NIAGARA 230/115 2TR | 100.05
Footnote - Uses NYSRC Reliability Rule Exception #13. Developer must ensure that sufficient generation can be reduced at Niagara to return the flows to less than their STE ratings within 5 minutes and to less than their LTE ratings within 10 minutes from the initial overload.
N-1-0 Thermal Overloads (Emergency Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
|  |  | Dispatch 1 |  |  | Dispatch 2
| Monitored Facility | Applicable Rating [MVA] | First Contingency | Second Contingency | AC %Loading | First Contingency | Second Contingency | AC %Loading
| 135304 SAWYER78 230 135415 PACKARD2 230 2 | 556 | HUNTLEY - PACKARD 77 230 | Base Case | 109.89 | HUNTLEY - PACKARD 77 230 | Base Case | 103.75
| 135303 SAWYER77 230 135415 PACKARD2 230 1 | 556 | HUNTLEY - PACKARD 78 230 | Base Case | 109.66 | HUNTLEY - PACKARD 78 230 | Base Case | 103.65
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 620 | NIAGARA - PACKARD 62 230 | Base Case | 108.24 | - | - | -
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 620 | NIAGARA - PACKARD 61 230 | Base Case | 107.77 | - | - | -
N-1-1 Thermal Overloads (Emergency Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
|  |  | Dispatch 1 - Niagara 230 kV Max |  |  | Dispatch 2 - Niagara 115 kV Max
| Monitored Facility | Applicable Rating [MVA] | First Contingency | Second Contingency | AC %Loading | First Contingency | Second Contingency | AC %Loading
| 130762 GARDV230 230 130767 STOLE230 230 1 | 478 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 108.34 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 103.19
| 135303 SAWYER77 230 135415 PACKARD2 230 1 | 704 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 105.57 | - | - | -
| Voltage Violations |  | Key Contingency |  |  | Monitored Facility
| Multiple instances of low-voltage and non-convergence violations under both N-1 and N-1-1 conditions for all cases; load was modified (PQBRK = 0.7) to solve cases. |  | Any combination resulting in the loss of two out of three Sawyer transformers under N-1 (Towers 77&78, 77&80) or N-1-1 (any combination of the 77, 79, 80 lines) |  |  | HUNTLEY 230 kV and GARDENVILLE 230 kV

## Additional_Info_Beyond_Criteria
SERIES REACTORS ON 77 AND 78 LINES BY-PASSED
N-1 Thermal Overloads (NTC) - 1000 MW Ontario Import
| Monitored Facility | Applicable | Dispatch 1 - Niagara 230 kV Max |  | Dispatch 2 - Niagara 115 kV Max
|  | Rating [MVA] | Contingency | AC % Loading | Contingency | AC % Loading
| 135303 SAWYER77 230 135415 PACKARD2 230 1 | 644 | SB:78PK | 128.37 | SB:78PK | 121.6
| 135304 SAWYER78 230 135415 PACKARD2 230 2 | 644 | S:PA_HNTL77 | 127.64 | S:PA_HNTL77 | 121.7
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 166 | T:77&78 | 126.93 | T:77&78 | 132.29
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 (See footnote) | 841 | DCT:230:62+76 | 119.06 | DCT:230:62+76 | 103.21
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 654 | BUS:230:PK-2 | 116.75 | BUS:230:PK-2 | 110.03
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | 654 | NF:230:77 PK | 115.78 | NF:230:77 PK | 109.94
| 130762 GARDV230 230 130767 STOLE230 230 1 | 478 | T:77&78 | 115.12 | T:77&78 | 111.61
| 135450 GRDNVL1 115 135453 LONG-180 115 1 | 166 | DCT:230:77+78+THR | 112.83 | DCT:230:77+78+THR | 120.39
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 (See footnote) | 841 | DCT:230:61+64 | 111.47 | DCT:230:61+64 | 95.49
| 130795 DEPEW115 115 130799 ERIE 115 115 1 | 119 | SB:PK115 30+40 | 111.08 | SB:PK115 30+40 | 111.48
| 135460 PACK(N)E 115 135538 LONG-182 115 1 | 208 | T:77&78 | 110.17 | T:77&78 | 114.81
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 (See footnote) | 351 | DCT:115:193+194 | 108.08 | DCT:115:193+194 | 127.68
| 135449 GR.I-182 115 135459 NI.B-182 115 1 | 181 | T:77&78 | 107.96 | T:77&78 | 113.28
| 135442 ECWA-181 115 135458 NI.B-181 115 1 | 181 | DCT:230:77+78 | 107.11 | DCT:230:77+78 | 111.88
| 135497 ZRMN-133 115 135562 S214-133 115 1 | 185 | DCT:230:77+78+THR | 106.99 | DCT:230:77+78+THR | 111.27
| 135442 ECWA-181 115 135495 YNG-181 115 1 | 181 | T:77&78 | 106.55 | T:77&78 | 111.28
| 135451 HUNTLEY1 115 135562 S214-133 115 1 | 181 | DCT:230:77+78+THR | 105.95 | DCT:230:77+78+THR | 110.3
| 135449 GR.I-182 115 135538 LONG-182 115 1 | 208 | T:77&78 | 105.54 | T:77&78 | 110.28
| 135437 CLSP-181 115 135495 YNG-181 115 1 | 163 | DCT:230:77+78 | 102.69 | DCT:230:77+78 | 107.63
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 181 | DCT:230:77+78+THR | 102.66 | NF:115:133 HT | 111.17
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 (See footnote) | 288 | DCT:230:77+78+THR | 102.36 | - | -
| 130834 N.BRW115 115 135437 CLSP-181 115 1 | 163 | DCT:230:77+78 | 101.74 | DCT:230:77+78 | 106.68
| 130847 ROLL 115 115 130857 STOLE115 115 1 | 90 | SB:181:ER | 101.58 | SB:181:ER | 101.55
| 135443 ECWA-182 115 135459 NI.B-182 115 1 | 181 | DCT:230:77+78+THR | 100.6 | DCT:230:77+78+THR | 106.01
| 135443 ECWA-182 115 135496 YNG-182 115 1 | 181 | DCT:230:77+78+THR | 100.6 | DCT:230:77+78+THR | 106.04
| 130766 ROBIN230 230 147841 NIAGAR2E 230 1 (See footnote) | 550 | DCT:230:77+78+THR | 92.02 | DCT:230:77+78+THR | 85.46
| 135460 PACK(N)E 115 147850 NIAG115E 115 2 (See footnote) | 328 | DCT:115:101+191 | 88.34 | DCT:115:101+191 | 108.21
| 135433 AMHST-38 115 135472 S129-38 115 1 | 151 | - | - | T:77&78 | 100.88
| 135434 AMHST-39 115 135473 S129-39 115 1 | 151 | - | - | T:77&78 | 100.13
| 135434 AMHST-39 115 135478 S140-39 115 1 | 151 | - | - | T:77&78 | 100.13
| 135441 FMC-39 115 135473 S129-39 115 1 | 151 | - | - | DCT:230:77+78 | 102.67
| 135451 HUNTLEY1 115 135472 S129-38 115 1 | 151 | - | - | T:77&78 | 103.68
| 135452 LOCKPORT 115 135510 SHAW-102 115 1 | 253 | - | - | SB:37:LP | 103.25
| 135453 LONG-180 115 147850 NIAG115E 115 1 (See footnote) | 265 | - | - | DCT:230:77+78 | 79.6
| 135460 PACK(N)E 115 147850 NIAG115E 115 1 (See footnote) | 351 | - | - | DCT:115:192+195 | 92.02
Footnote - Uses NYSRC Reliability Rule Exception #13. Developer must ensure that sufficient generation can be reduced at Niagara to return the flows to less than their STE ratings within 5 minutes and to less than their LTE ratings within 10 minutes from the initial overload.
N-2 Normal Transfer Criteria - Locked Dispatch - OH Import 1000
|  |  | Dispatch 1 - Niagara 230 kV Max |  |  | Dispatch 2 - Niagara 115 kV Max
| Monitored Facility | Applicable Rating [MVA] | First Contingency | Second Contingency | AC %Loading | First Contingency | Second Contingency | AC %Loading
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 (See footnote) | 288 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 156.28 | NIAGARA - ROBINSON 64 230 | T:77&78 | 127.22
| 135303 SAWYER77 230 135415 PACKARD2 230 1 | 644 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3230 | 152.48 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3230 | 143.22
| 130762 GARDV230 230 130767 STOLE230 230 1 | 478 | WTHRS - MEYER 230 | T:77&78 | 150.28 | WTHRS - MEYER 230 | T:77&78 | 146.85
| 135304 SAWYER78 230 135415 PACKARD2 230 2 | 644 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 150.14 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 143.05
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 (See footnote) | 841 | NIAGARA - ROBINSON 64 230 | T:62&BP76 | 140.79 | NIAGARA - ROBINSON 64 230 | T:62&BP76 | 122.75
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 654 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 140.29 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 131.12
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 (See footnote) | 841 | BECK - PACKARD BP76 230 | T:61&64 | 139.76 | BECK - PACKARD BP76 230 | T:61&64 | 121.84
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 206 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 139.43 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 140.95
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | 654 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 137.87 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 130.89
| 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | 587 | NIAGARA - PACKARD 62 230 | T:61&64 | 137.67 | NIAGARA - PACKARD 62 230 | T:61&64 | 122.03
| 135415 PACKARD2 230 135460 PACK(N)E 115 1 | 250 | NIAGARA 230/115 1TR | T:77&78 | 132.74 | NIAGARA - ROBINSON 64 230 | T:77&78 | 119.19
| 135450 GRDNVL1 115 135453 LONG-180 115 1 | 206 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 130.84 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 134.06
| 135451 HUNTLEY1 115 135472 S129-38 115 1 | 185 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 128.21 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 127.64
| 135441 FMC-39 115 135473 S129-39 115 1 | 185 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 127.1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 126.53
| 135433 AMHST-38 115 135472 S129-38 115 1 | 185 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 125.2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 124.54
| 135449 GR.I-182 115 135459 NI.B-182 115 1 | 226 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 124.46 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 126.03
| 135434 AMHST-39 115 135473 S129-39 115 1 | 185 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 124.36 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 123.71
| 135434 AMHST-39 115 135478 S140-39 115 1 | 185 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 124.35 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 123.67
| 135497 ZRMN-133 115 135562 S214-133 115 1 | 206 | NIAGARA - ROBINSON 64 230 | T:77&78 | 122.9 | NIAGARA - ROBINSON 64 230 | T:77&78 | 129.03
| 135460 PACK(N)E 115 135538 LONG-182 115 1 | 265 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 122.81 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 124.43
| 130834 N.BRW115 115 135437 CLSP-181 115 1 | 181 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 121.54 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 123.81
| 135437 CLSP-181 115 135495 YNG-181 115 1 | 183 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 121.33 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 123.56
| 135451 HUNTLEY1 115 135562 S214-133 115 1 | 206 | NIAGARA - ROBINSON 64 230 | T:77&78 | 119.66 | NIAGARA - ROBINSON 64 230 | T:77&78 | 125
| 135449 GR.I-182 115 135538 LONG-182 115 1 | 265 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 117.98 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 119.58
| 130764 MEYER230 230 131343 MEYER M4 34.5 1 | 294 | CANDQUA - STNYRDG 68A 230 | SB:GARD230_T7-12 | 116.68 | CANDQUA - STNYRDG 68A 230 | SB:GARD230_T7-12 | 116.41
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 206 | NIAGARA - ROBINSON 64 230 | T:77&78 | 116.46 | NIAGARA - ROBINSON 64 230 | T:77&78 | 121.23
| 135443 ECWA-182 115 135496 YNG-182 115 1 | 226 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 116.09 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 117.85
| 135443 ECWA-182 115 135459 NI.B-182 115 1 | 226 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 115.93 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 117.69
| 135442 ECWA-181 115 135458 NI.B-181 115 1 | 226 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 115.64 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 117.18
| 135442 ECWA-181 115 135495 YNG-181 115 1 | 226 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 114.7 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 116.23
| 135441 FMC-39 115 135451 HUNTLEY1 115 1 | 206 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 114.09 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 113.58
| 135383 S219-182 115 135505 WALDENTP 115 1 | 206 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 113.78 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 116.22
| 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | 654 | HUNTLEY - GARDENVILL 79 230 | SB:ROBI230 | 113.65 | HUNTLEY - GARDENVILL 79 230 | SB:ROBI230 | 107.44
| 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | 180 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 113.31 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 115.28
| 135460 PACK(N)E 115 147850 NIAG115E 115 2 (See footnote) | 328 | NIAGARA - PACKARD 62 230 | T:61&191 | 113.19 | NIAGARA - PACKARD 62 230 | T:61&191 | 127.84
| 130815 HINMN115 115 131611 HARIS115 115 1 | 306 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 109.46 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 100.61
| 135452 LOCKPORT 115 135851 SHEL-113 115 1 | 180 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 109.32 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 111.24
| 135453 LONG-180 115 147850 NIAG115E 115 1 (See footnote) | 265 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 107.21 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 109.95
| 130764 MEYER230 230 131122 WTHRS230 230 1 | 494 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 107.03 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 106.42
| 130815 HINMN115 115 135452 LOCKPORT 115 1 | 280 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 106.01 | - | - | -
| 130799 ERIE 115 115 130834 N.BRW115 115 1 | 159 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 105.82 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 109.24
| 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | 654 | HUNTLEY - GARDENVILL 80 230 | SB:ROBI230 | 105.49 | - | - | -
| 135306 SAWYER79 230 135418 SUNY-79 230 1 | 654 | HUNTLEY - GARDENVILL 80 230 | SB:ROBI230 | 105.49 | - | - | -
| 135305 SAWYER80 230 135419 SUNY-80 230 1 | 654 | HUNTLEY - GARDENVILL 79 230 | SB:ROBI230 | 105.27 | - | - | -
| 135861 MORTIMER 115 149011 S82-1115 115 1 | 357.9 | ROCH - PANNELL RP-1 345 | SB:PANN345_3902 | 104.97 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 103.75
| 135383 S219-182 115 135496 YNG-182 115 1 | 226 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 104.64 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 106.87
| 135445 FORD-142 115 135484 S55-142 115 1 | 108 | WTHRS - MEYER 230 | T:73&74 | 104.32 | WTHRS - MEYER 230 | T:73&74 | 104.91
| 135269 CLVB-142 115 135445 FORD-142 115 1 | 108 | WTHRS - MEYER 230 | T:73&74 | 104.3 | WTHRS - MEYER 230 | T:73&74 | 104.89
| 135432 AM.S-182 115 135505 WALDENTP 115 1 | 206 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 102.87 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 105.69
| 130766 ROBIN230 230 147841 NIAGAR2E 230 1 (See footnote) | 657 | NIAGARA 230/115 1TR | T:77&78 | 102.55 | R:HC-FV_37&W-F_171 | T:77&78 | 94.56
| 135433 AMHST-38 115 135477 S140-38 115 1 | 226 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 102.49 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 101.91
| 135415 PACKARD2 230 135461 PACK(S)W 115 2 | 250 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 102.32 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 109.8
| 135413 GRDNVL2 230 135418 SUNY-79 230 1 | 654 | HUNTLEY - GARDENVILL 80 230 | SB:ROBI230 | 102.26 | - | - | -
| 135450 GRDNVL1 115 135475 S139-141 115 1 | 108 | WTHRS - MEYER 230 | T:73&74 | 102.15 | WTHRS - MEYER 230 | T:73&74 | 102.73
| 135475 S139-141 115 135483 S55-141 115 1 | 108 | WTHRS - MEYER 230 | T:73&74 | 102.12 | WTHRS - MEYER 230 | T:73&74 | 102.7
| 135268 CLVB-141 115 135483 S55-141 115 1 | 108 | WTHRS - MEYER 230 | T:73&74 | 102.1 | WTHRS - MEYER 230 | T:73&74 | 102.68
| 135413 GRDNVL2 230 135419 SUNY-80 230 1 | 654 | HUNTLEY - GARDENVILL 79 230 | SB:ROBI230 | 102.05 | - | - | -
| 135452 LOCKPORT 115 135872 SOUR-111 115 1 | 199 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 100.52 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 102.39
| 135435 SUMIT PK 115 135454 MLPN-129 115 1 | 283 | - | - | - | NIAGARA - ROBINSON 64 230 | T:77&78 | 104.09
| 135454 MLPN-129 115 135461 PACK(S)W 115 1 | 298 | - | - | - | NIAGARA - ROBINSON 64 230 | T:77&78 | 103.31
| 135455 MLPN-130 115 135461 PACK(S)W 115 1 | 298 | - | - | - | NIAGARA - ROBINSON 64 230 | T:77&78 | 103.98
| 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | 298 | - | - | - | NIAGARA - ROBINSON 64 230 | T:77&78 | 103.59
Footnote - Uses NYSRC Reliability Rule Exception #13. Developer must ensure that sufficient generation can be reduced at Niagara to return the flows to less than their STE ratings within 5 minutes and to less than their LTE ratings within 10 minutes from the initial overload.
N-2 Emergency Transfer Criteria - Locked Dispatch - OH Import 1000
|  |  | Dispatch 1 - Niagara 230 kV Max |  |  | Dispatch 2 - Niagara 115 kV Max
| Monitored Facility | Applicable Rating [MVA] | First Contingency | Second Contingency | AC %Loading | First Contingency | Second Contingency | AC %Loading
| 135303 SAWYER77 230 135415 PACKARD2 230 1 | 704 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 139.28 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 130.78
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 288 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 137.97 | - | - | -
| 135304 SAWYER78 230 135415 PACKARD2 230 2 | 746 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL77 | 128.8 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL77 | 122.11
| 130762 GARDV230 230 130767 STOLE230 230 1 | 478 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 121.64 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 117.06
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 755 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 121.52 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 113.58
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 841 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 62 230 | 119.62 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 62 230 | 103.74
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 841 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 61 230 | 119.36 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 61 230 | 103.51
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | 755 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 77 230 | 118.44 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 112.04
| 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | 587 | NIAGARA - PACKARD 61 230 | NIAGARA - PACKARD 62 230 | 115 | NIAGARA - PACKARD 61 230 | B:PACKT4 | 102.08
| 135497 ZRMN-133 115 135562 S214-133 115 1 | 206 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 103.34 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 105.69
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 206 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 102.84 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 106.99
| 130815 HINMN115 115 131611 HARIS115 115 1 | 306 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 102.39 | - | - | -
| 130764 MEYER230 230 131343 MEYER M4 34.5 1 | 336 | CANDQUA - STNYRDG 68A 230 | STOLLRD - GARDENVILL 66 230 | 102.03 | CANDQUA - STNYRDG 68A 230 | STOLLRD - GARDENVILL 66 230 | 101.79
| 130815 HINMN115 115 135452 LOCKPORT 115 1 | 280 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 100.75 | - | - | -
| 135451 HUNTLEY1 115 135562 S214-133 115 1 | 206 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 100.3 | NIAGARA 230/115 2TR | B:PACKT4 | 102.92
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 206 | - | - | - | NIAGARA 230/115 2TR | B:PACKT4 | 100.64

## N-1_ETC_OH_1000
SERIES REACTORS ON 77 AND 78 LINES BY-PASSED
Niagara Dispatch | Monitored Facility | Contingency |  | Rate Base (MVA) | Rate Cont (MVA) | Final AC %Loading
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | B:PACKT3 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1B:PACKT3 | 566 | 755 | 101.13
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OE:PACK_78 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1OE:PACK_78 | 566 | 755 | 100.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1HUNTLEY - PACKARD 78 230 | 566 | 755 | 100.16
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LN:230:78 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1LN:230:78 | 566 | 755 | 100.16
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 Max |  | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 M |  |  | 101.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1B:PACKT3 | 556 | 704 | 117.27
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1S:PA_HNTL78 | 556 | 704 | 116.53
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OE:PACK_78 | 135303 SAWYER77 230 135415 PACKARD2 230 1OE:PACK_78 | 556 | 704 | 116.37
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1HUNTLEY - PACKARD 78 230 | 556 | 704 | 116.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LN:230:78 | 135303 SAWYER77 230 135415 PACKARD2 230 1LN:230:78 | 556 | 704 | 116.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1S:PA_HNTL78 | 556 | 704 | 111.11
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1B:PACKT3 | 556 | 704 | 111.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OE:PACK_78 | 135303 SAWYER77 230 135415 PACKARD2 230 1OE:PACK_78 | 556 | 704 | 110.93
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1HUNTLEY - PACKARD 78 230 | 556 | 704 | 110.85
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LN:230:78 | 135303 SAWYER77 230 135415 PACKARD2 230 1LN:230:78 | 556 | 704 | 110.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OE:HNTLEY_78 | 135303 SAWYER77 230 135415 PACKARD2 230 1OE:HNTLEY_78 | 556 | 704 | 106.8
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OE:HNTLEY_78 | 135303 SAWYER77 230 135415 PACKARD2 230 1OE:HNTLEY_78 | 556 | 704 | 101.53
| 135303 SAWYER77 230 135415 PACKARD2 230 1 Max |  | 135303 SAWYER77 230 135415 PACKARD2 230 1 M |  |  | 117.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OE:PACK_77 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2OE:PACK_77 | 566 | 755 | 100.29
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2HUNTLEY - PACKARD 77 230 | 566 | 755 | 100.16
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:230:77 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2LN:230:77 | 566 | 755 | 100.16
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 Max |  | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 M |  |  | 100.29
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | S:PA_HNTL77 | 135304 SAWYER78 230 135415 PACKARD2 230 2S:PA_HNTL77 | 556 | 746 | 110.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OE:PACK_77 | 135304 SAWYER78 230 135415 PACKARD2 230 2OE:PACK_77 | 556 | 746 | 110.02
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | 135304 SAWYER78 230 135415 PACKARD2 230 2HUNTLEY - PACKARD 77 230 | 556 | 746 | 109.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LN:230:77 | 135304 SAWYER78 230 135415 PACKARD2 230 2LN:230:77 | 556 | 746 | 109.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | B:PACKT4 | 135304 SAWYER78 230 135415 PACKARD2 230 2B:PACKT4 | 556 | 746 | 107.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | S:PA_HNTL77 | 135304 SAWYER78 230 135415 PACKARD2 230 2S:PA_HNTL77 | 556 | 746 | 105.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OE:PACK_77 | 135304 SAWYER78 230 135415 PACKARD2 230 2OE:PACK_77 | 556 | 746 | 104.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | 135304 SAWYER78 230 135415 PACKARD2 230 2HUNTLEY - PACKARD 77 230 | 556 | 746 | 104.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LN:230:77 | 135304 SAWYER78 230 135415 PACKARD2 230 2LN:230:77 | 556 | 746 | 104.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | B:PACKT4 | 135304 SAWYER78 230 135415 PACKARD2 230 2B:PACKT4 | 556 | 746 | 102.1
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OE:HNTLEY_77 | 135304 SAWYER78 230 135415 PACKARD2 230 2OE:HNTLEY_77 | 556 | 746 | 101.12
| 135304 SAWYER78 230 135415 PACKARD2 230 2 Max |  | 135304 SAWYER78 230 135415 PACKARD2 230 2 M |  |  | 110.19
| Grand Max |  |  |  |  | 117.27
Any combination resulting in the loss of two out of three Sawyer transformers under N-1 (Towers 77&78, 77&80) or N-1-1 (any combination of the 77, 79, 80 lines)

## N-1_NTC_OH_0
SERIES REACTORS ON 77 AND 78 LINES BY-PASSED
Niagara Dispatch | Monitored Facility | Cont Name |  | Rate Base (MVA) | Rate Cont (MVA) | Final AC %Loading
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | DCT:115:193+194 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&168 | 273 | 299 | 142.07
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | DCT:115:193+194 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&66 | 273 | 299 | 119.12
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | SB:129:PK | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&175 | 273 | 299 | 117.67
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | BUS:115:PK-60 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&177 | 273 | 299 | 115.75
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | SB:129:PK | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&97 | 273 | 299 | 107.29
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | BUS:115:PK-60 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&121 | 273 | 299 | 104.88
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 Max |  |  |  |  | 142.07
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | DCT:115:101+191 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&169 | 247 | 275 | 131.91
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | DCT:230:61+191 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&170 | 247 | 275 | 127.04
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | T:61&191 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&171 | 247 | 275 | 127.04
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | DCT:115:101+191 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&78 | 247 | 275 | 108.32
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | DCT:230:61+191 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&107 | 247 | 275 | 105.46
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | T:61&191 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&108 | 247 | 275 | 105.46
| 135460 PACK(N)E 115 147850 NIAG115E 115 2 Max |  |  |  |  | 131.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DCT:230:61+64 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&64 | 620 | 717 | 121.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | T:61&64 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&65 | 620 | 717 | 121.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DCT:230:61+191 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&98 | 620 | 717 | 107.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | T:61&191 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&99 | 620 | 717 | 107.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:230:61 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&118 | 620 | 717 | 104.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&119 | 620 | 717 | 104.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:230:61 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&120 | 620 | 717 | 104.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DCT:230:61+64 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&215 | 620 | 717 | 102.24
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | T:61&64 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&216 | 620 | 717 | 102.24
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 Max |  |  |  |  | 121.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:77+78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&172 | 160 | 166 | 119.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | T:77&78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&173 | 160 | 166 | 119.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:77+78+THR | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&174 | 160 | 166 | 118.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:180+182N | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&178 | 160 | 166 | 114.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | T:77&78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&70 | 160 | 166 | 114.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:77+78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&71 | 160 | 166 | 114.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:77+78+THR | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&72 | 160 | 166 | 113.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:180+182S | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&179 | 160 | 166 | 113.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:54+182S | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&180 | 160 | 166 | 111.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+THR+ELM3-4 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&186 | 160 | 166 | 107.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+ELM3-4 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&187 | 160 | 166 | 107.91
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:54+182S | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&109 | 160 | 166 | 105.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:180+182N | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&122 | 160 | 166 | 104.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SB:GI115 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&196 | 160 | 166 | 104.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SB:182N:PK | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&197 | 160 | 166 | 104.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:180+182S | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&123 | 160 | 166 | 104.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+THR | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&200 | 160 | 166 | 103.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&201 | 160 | 166 | 103.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | T:79&80 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&202 | 160 | 166 | 103.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | BUS:115:PK-30 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&204 | 160 | 166 | 103.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+THR+ELM1-2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&205 | 160 | 166 | 103.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+ELM1-2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&206 | 160 | 166 | 103.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+ELM1-2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&207 | 160 | 166 | 103.28
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+THR+ELM3-4 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&128 | 160 | 166 | 103.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+ELM3-4 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&130 | 160 | 166 | 103.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&210 | 160 | 166 | 103.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&211 | 160 | 166 | 103.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&229 | 160 | 166 | 101.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&230 | 160 | 166 | 101.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NF:115:182 GI-N | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&234 | 160 | 166 | 101.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NF:115:182 PK | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&238 | 160 | 166 | 100.91
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 Max |  |  |  |  | 119.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DCT:230:62+76 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&68 | 620 | 717 | 116.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | T:62&BP76 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&69 | 620 | 717 | 116.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DCT:230:27+62 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&92 | 620 | 717 | 107.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | T:62&PA27 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&93 | 620 | 717 | 107.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&111 | 620 | 717 | 105.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:230:62 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&112 | 620 | 717 | 105.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:230:62 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&113 | 620 | 717 | 105.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SB:PK230 BS3+4 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&124 | 620 | 717 | 104.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SB:PA230_R506 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&125 | 620 | 717 | 104.18
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 Max |  |  |  |  | 116.03
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | T:77&78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&73 | 474 | 478 | 112.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DCT:230:77+78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&74 | 474 | 478 | 112.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DCT:230:77+78+THR | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&75 | 474 | 478 | 112.11
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DCT:230:77+78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&184 | 474 | 478 | 108.1
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | T:77&78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&185 | 474 | 478 | 108.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DCT:230:77+78+THR | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&190 | 474 | 478 | 107.54
| 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  |  |  | 112.32
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 1 | DCT:115:192+195 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&181 | 273 | 301 | 111.29
| 135460 PACK(N)E 115 147850 NIAG115E 115 1 Max |  |  |  |  | 111.29
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | S:PA_HNTL77 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&77 | 556 | 644 | 108.34
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NF:230:77 PK | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&79 | 556 | 644 | 108.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OE:PACK_77 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&80 | 556 | 644 | 108.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LN:230:77 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&82 | 556 | 644 | 108.07
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&83 | 556 | 644 | 108.07
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LN:230:77 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&84 | 556 | 644 | 108.07
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:PA230_R3430 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&110 | 556 | 644 | 105.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:77PK | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&114 | 556 | 644 | 105.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BUS:230:PK-4 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&115 | 556 | 644 | 105.17
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | B:PACKT4 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&116 | 556 | 644 | 105.17
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:77PK+THR | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&117 | 556 | 644 | 104.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:PK230 BS3+4 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&126 | 556 | 644 | 104.1
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:PA230_R506 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&127 | 556 | 644 | 104.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | S:PA_HNTL77 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&217 | 556 | 644 | 102.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NF:230:77 PK | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&218 | 556 | 644 | 102.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OE:PACK_77 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&219 | 556 | 644 | 102.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&221 | 556 | 644 | 101.93
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LN:230:77 | Any combination resulting in the loss of two out of three Sawyer transformers under N-1 (Towers 77&78, 77&80) or N-1-1 (any combination of the 77, 79, 80 lines) | 556 | 644 | 101.93
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LN:230:77 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&223 | 556 | 644 | 101.93
| 135304 SAWYER78 230 135415 PACKARD2 230 2 Max |  |  |  |  | 108.34
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:77+78+THR | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&183 | 160 | 166 | 108.23
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:77+78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&188 | 160 | 166 | 107.66
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | T:77&78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&189 | 160 | 166 | 107.66
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | SB:PK115 30+40 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&208 | 160 | 166 | 103.23
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:77+78+THR | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&138 | 160 | 166 | 101.07
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | T:77&78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&162 | 160 | 166 | 100.62
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:77+78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&166 | 160 | 166 | 100.5
| 135450 GRDNVL1 115 135453 LONG-180 115 1 Max |  |  |  |  | 108.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | S:PA_HNTL78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&81 | 556 | 644 | 108.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NF:230:78 PK | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&85 | 556 | 644 | 107.95
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OE:PACK_78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&86 | 556 | 644 | 107.95
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LN:230:78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&87 | 556 | 644 | 107.86
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&88 | 556 | 644 | 107.86
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LN:230:78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&89 | 556 | 644 | 107.86
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:78PK | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&90 | 556 | 644 | 107.82
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:PA230_R3230 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&91 | 556 | 644 | 107.82
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BUS:230:PK-2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&94 | 556 | 644 | 107.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | B:PACKT3 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&95 | 556 | 644 | 107.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:78PK+THR | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&96 | 556 | 644 | 107.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:PK230 BS2+3 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&100 | 556 | 644 | 106.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:PA230_R304 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&101 | 556 | 644 | 106.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | S:PA_HNTL78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&220 | 556 | 644 | 102
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NF:230:78 PK | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&224 | 556 | 644 | 101.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OE:PACK_78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&225 | 556 | 644 | 101.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LN:230:78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&226 | 556 | 644 | 101.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&227 | 556 | 644 | 101.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LN:230:78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&228 | 556 | 644 | 101.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:78PK | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&263 | 556 | 644 | 100.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:PA230_R3230 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&264 | 556 | 644 | 100.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BUS:230:PK-2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&268 | 556 | 644 | 100.45
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | B:PACKT3 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&269 | 556 | 644 | 100.45
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:78PK+THR | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&270 | 556 | 644 | 100.37
| 135303 SAWYER77 230 135415 PACKARD2 230 1 Max |  |  |  |  | 108.12
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | DCT:230:77+78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&198 | 200 | 208 | 103.73
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | T:77&78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&199 | 200 | 208 | 103.73
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | DCT:230:77+78+THR | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&203 | 200 | 208 | 103.32
| 135460 PACK(N)E 115 135538 LONG-182 115 1 Max |  |  |  |  | 103.73
Dispatch 1 | 130847 ROLL 115 115 130857 STOLE115 115 1 | SB:181:ER | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&129 | 90 | 90 | 103.22
Dispatch 2 | 130847 ROLL 115 115 130857 STOLE115 115 1 | SB:181:ER | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&213 | 90 | 90 | 102.95
| 130847 ROLL 115 115 130857 STOLE115 115 1 Max |  |  |  |  | 103.22
Dispatch 1 | 135305 SAWYER80 230 135309 SAWYERB3 230 1 | DCT:230:77+78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&135 | 220 | 252 | 101.38
Dispatch 1 | 135305 SAWYER80 230 135309 SAWYERB3 230 1 | T:77&78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&140 | 220 | 252 | 100.88
Dispatch 2 | 135305 SAWYER80 230 135309 SAWYERB3 230 1 | T:77&78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&257 | 220 | 252 | 100.73
Dispatch 2 | 135305 SAWYER80 230 135309 SAWYERB3 230 1 | DCT:230:77+78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&261 | 220 | 252 | 100.72
| 135305 SAWYER80 230 135309 SAWYERB3 230 1 Max |  |  |  |  | 101.38
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | DCT:230:77+78+THR | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&235 | 174 | 181 | 101.07
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | DCT:230:77+78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&236 | 174 | 181 | 100.94
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | T:77&78 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&237 | 174 | 181 | 100.93
| 135449 GR.I-182 115 135459 NI.B-182 115 1 Max |  |  |  |  | 101.07
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SB:PK115 30+40 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&251 | 119 | 119 | 100.81
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SB:PK115 30+40 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&154 | 119 | 119 | 100.75
| 130795 DEPEW115 115 130799 ERIE 115 115 1 Max |  |  |  |  | 100.81
| Grand Max |  |  |  |  | 142.07

## N-1-1_NTC_OH_1000_Adjust
SERIES REACTORS ON 77 AND 78 LINES BY-PASSED
Niagara Dispatch | Monitored Facility | First Level Scenario | Cont Name | Rate Base (MVA) | Rate Cont (MVA) | SCD AC %Loading
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 474 | 478 | 122.56
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 474 | 478 | 122.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 474 | 478 | 122.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 474 | 478 | 122.33
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 474 | 478 | 120.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:77&78 | 474 | 478 | 120.14
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:77&78 | 474 | 478 | 119.96
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 474 | 478 | 119.09
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 474 | 478 | 118.83
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - HOMERCTY | T:77&78 | 474 | 478 | 116.92
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 474 | 478 | 116.19
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 474 | 478 | 116.15
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 474 | 478 | 115.72
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 474 | 478 | 115.38
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 474 | 478 | 115.19
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 474 | 478 | 113.68
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 474 | 478 | 113.68
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 474 | 478 | 113.63
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - HOMERCTY | T:77&78 | 474 | 478 | 113.63
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 474 | 478 | 113.59
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | T:77&78 | 474 | 478 | 112.2
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | T:77&78 | 474 | 478 | 110.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | T:77&78 | 474 | 478 | 110.07
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | T:77&78 | 474 | 478 | 109.59
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | T:77&78 | 474 | 478 | 109.47
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 1TR | T:77&78 | 474 | 478 | 109.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | T:77&78 | 474 | 478 | 109.15
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | T:77&78 | 474 | 478 | 108.71
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 474 | 478 | 108.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 3TR | T:77&78 | 474 | 478 | 108.43
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 474 | 478 | 108.42
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 474 | 478 | 108.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ERIE E - 4 MILE 230 | T:77&78 | 474 | 478 | 108.26
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS1 | T:77&78 | 474 | 478 | 108.13
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | T:77&78 | 474 | 478 | 108.09
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:INDEK-OL | T:77&78 | 474 | 478 | 107.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 3TR | T:77&78 | 474 | 478 | 107.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 1TR | T:77&78 | 474 | 478 | 107.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - INDEPNC 26 345 | T:77&78 | 474 | 478 | 107.46
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - 9MI1 8 345 | T:77&78 | 474 | 478 | 107.45
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 4 | T:77&78 | 474 | 478 | 107.28
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 5 | T:77&78 | 474 | 478 | 107.28
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 6 | T:77&78 | 474 | 478 | 107.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 4 MILE - ERIE SE 230 | T:77&78 | 474 | 478 | 107.26
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 7 | T:77&78 | 474 | 478 | 107.26
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:INDEK-OL | T:77&78 | 474 | 478 | 107.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS1 | T:77&78 | 474 | 478 | 107.11
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ERIE E - 4 MILE 230 | T:77&78 | 474 | 478 | 107.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | T:77&78 | 474 | 478 | 107.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 4 MILE - ERIE SE 230 | T:77&78 | 474 | 478 | 106.77
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - VOLNEY 6 345 | T:77&78 | 474 | 478 | 106.67
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE 345/115 1TR | T:77&78 | 474 | 478 | 106.61
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN7 | T:77&78 | 474 | 478 | 106.6
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE 345/115 1TR | T:77&78 | 474 | 478 | 106.37
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK - SRIPL 68 230 | T:77&78 | 474 | 478 | 106.22
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OS - EL - LFYTE 17 345 | T:77&78 | 474 | 478 | 106.07
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SRIPL - ERIE E 69 230 | T:77&78 | 474 | 478 | 106.05
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN7 | T:77&78 | 474 | 478 | 105.78
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS2 | T:77&78 | 474 | 478 | 105.71
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | MAINSBRG 345/115 1TR | T:77&78 | 474 | 478 | 105.61
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAG - KINTIGH 345 | T:77&78 | 474 | 478 | 105.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - INDEPNC 26 345 | T:77&78 | 474 | 478 | 105.45
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - EDIC 2-15 345 | T:77&78 | 474 | 478 | 105.44
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:STL1_G1 | T:77&78 | 474 | 478 | 105.39
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:STL1_G2 | T:77&78 | 474 | 478 | 105.39
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:KINTIGH | T:77&78 | 474 | 478 | 105.39
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | MAINSBRG 345/115 1TR | T:77&78 | 474 | 478 | 105.36
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | T:77&78 | 474 | 478 | 105.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | EDIC - FITZ 345 | T:77&78 | 474 | 478 | 105.35
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:DUPONT46 | T:77&78 | 474 | 478 | 105.35
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROBRD 230/115/34.5 1TR | T:77&78 | 474 | 478 | 105.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 4 | T:77&78 | 474 | 478 | 105.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 5 | T:77&78 | 474 | 478 | 105.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 6 | T:77&78 | 474 | 478 | 105.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 474 | 478 | 105.26
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - BECK PA27 230 | T:77&78 | 474 | 478 | 105.25
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - ELM 70 230 | T:77&78 | 474 | 478 | 105.24
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:Q234_CLIB_G10 | T:77&78 | 474 | 478 | 105.24
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:Q234_CLIB_G20 | T:77&78 | 474 | 478 | 105.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - VOL 21 345 | T:77&78 | 474 | 478 | 105.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 2TR | T:77&78 | 474 | 478 | 105.2
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:DUPONT46 | T:77&78 | 474 | 478 | 105.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:OSWEGO 5 | T:77&78 | 474 | 478 | 105.18
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 61 230 | T:77&78 | 474 | 478 | 105.18
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK - SRIPL 68 230 | T:77&78 | 474 | 478 | 105.18
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:STL1_G1 | T:77&78 | 474 | 478 | 105.18
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:STL1_G2 | T:77&78 | 474 | 478 | 105.18
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 345/230 4TR | T:77&78 | 474 | 478 | 105.15
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:Q234_CLIB_G10 | T:77&78 | 474 | 478 | 105.14
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:Q234_CLIB_G20 | T:77&78 | 474 | 478 | 105.14
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROBRD 230/115/34.5 1TR | T:77&78 | 474 | 478 | 105.1
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 3 | T:77&78 | 474 | 478 | 105.1
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 1 | T:77&78 | 474 | 478 | 105.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 2 | T:77&78 | 474 | 478 | 105.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:GENMLS61 | T:77&78 | 474 | 478 | 105.08
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SRIPL - ERIE E 69 230 | T:77&78 | 474 | 478 | 105.04
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:OXBOWNUG | T:77&78 | 474 | 478 | 105.03
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:OSWEGO 6 | T:77&78 | 474 | 478 | 105
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS2 | T:77&78 | 474 | 478 | 105
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:FITZPATR | T:77&78 | 474 | 478 | 104.99
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:HOORKN86 | T:77&78 | 474 | 478 | 104.99
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 7 | T:77&78 | 474 | 478 | 104.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:ELLICTVL | T:77&78 | 474 | 478 | 104.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:WOLEAN55 | T:77&78 | 474 | 478 | 104.99
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 61 230 | T:77&78 | 474 | 478 | 104.98
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:HOORKN85 | T:77&78 | 474 | 478 | 104.97
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - ELM 71 230 | T:77&78 | 474 | 478 | 104.96
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:GENMLS61 | T:77&78 | 474 | 478 | 104.94
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:HYDLRACE | T:77&78 | 474 | 478 | 104.92
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:ELLICTVL | T:77&78 | 474 | 478 | 104.91
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 345/230 3TR | T:77&78 | 474 | 478 | 104.89
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 345/230 5TR | T:77&78 | 474 | 478 | 104.89
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:MODERNLF | T:77&78 | 474 | 478 | 104.89
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 474 | 478 | 104.88
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - ELM 71 230 | T:77&78 | 474 | 478 | 104.87
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WATERCURE - OAKDALE 71 230 | T:77&78 | 474 | 478 | 104.86
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - NEWROCH 1 345 | T:77&78 | 474 | 478 | 104.86
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - NEWROCH 2 345 | T:77&78 | 474 | 478 | 104.86
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - NEWROCH 3 345 | T:77&78 | 474 | 478 | 104.86
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 5 115 | T:77&78 | 474 | 478 | 104.85
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:WOLEAN55 | T:77&78 | 474 | 478 | 104.85
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 3TR | T:77&78 | 474 | 478 | 104.85
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 4TR | T:77&78 | 474 | 478 | 104.85
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - 9MI1 8 345 | T:77&78 | 474 | 478 | 104.85
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 230/115 1TR | T:77&78 | 474 | 478 | 104.84
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAG - KINTIGH 345 | T:77&78 | 474 | 478 | 104.84
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FUL - CLAY 4 115 | T:77&78 | 474 | 478 | 104.83
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NEWROCH 345/115 1TR | T:77&78 | 474 | 478 | 104.83
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NEWROCH 345/115 2TR | T:77&78 | 474 | 478 | 104.83
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LHH - CLAY 7 115 | T:77&78 | 474 | 478 | 104.82
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - BECK PA27 230 | T:77&78 | 474 | 478 | 104.82
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 3TR | T:77&78 | 474 | 478 | 104.82
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:HOORKN86 | T:77&78 | 474 | 478 | 104.82
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NEWROCH 345/115 2TR | T:77&78 | 474 | 478 | 104.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - TEAL 11 115 | T:77&78 | 474 | 478 | 104.81
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 1TR | T:77&78 | 474 | 478 | 104.81
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 3TR | T:77&78 | 474 | 478 | 104.81
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - VOL 21 345 | T:77&78 | 474 | 478 | 104.81
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:HOORKN85 | T:77&78 | 474 | 478 | 104.81
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - BECK_TSA 345 | T:77&78 | 474 | 478 | 104.8
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - BECK_TSB 345 | T:77&78 | 474 | 478 | 104.8
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 2TR | T:77&78 | 474 | 478 | 104.8
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 1TR | T:77&78 | 474 | 478 | 104.79
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 2TR | T:77&78 | 474 | 478 | 104.79
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 5TR | T:77&78 | 474 | 478 | 104.79
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NEWROCH 345/115 1TR | T:77&78 | 474 | 478 | 104.77
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | BECK - PACKARD BP76 230 | T:77&78 | 474 | 478 | 104.77
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - WOOD 17 115 | T:77&78 | 474 | 478 | 104.77
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN8 | T:77&78 | 474 | 478 | 104.76
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN9 | T:77&78 | 474 | 478 | 104.76
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:SRANDOLP | T:77&78 | 474 | 478 | 104.76
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:VANDALIA | T:77&78 | 474 | 478 | 104.76
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OSW - VOL 11 345 | T:77&78 | 474 | 478 | 104.75
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BURT | T:77&78 | 474 | 478 | 104.75
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 4TR | T:77&78 | 474 | 478 | 104.74
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA 345/115 1TR | T:77&78 | 474 | 478 | 104.74
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA 345/115 2TR | T:77&78 | 474 | 478 | 104.74
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 62 230 | T:77&78 | 474 | 478 | 104.73
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DEWITT3 - LAFAYTTE 345 | T:77&78 | 474 | 478 | 104.73
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - NEWROCH 1 345 | T:77&78 | 474 | 478 | 104.72
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - NEWROCH 2 345 | T:77&78 | 474 | 478 | 104.72
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - NEWROCH 3 345 | T:77&78 | 474 | 478 | 104.72
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OSW - VOL 12 345 | T:77&78 | 474 | 478 | 104.72
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDL - FRASER 32 345 | T:77&78 | 474 | 478 | 104.72
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:HYDLRACE | T:77&78 | 474 | 478 | 104.72
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - ELM 70 230 | T:77&78 | 474 | 478 | 104.71
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - 9MI1 9 345 | T:77&78 | 474 | 478 | 104.71
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - VOL 20 345 | T:77&78 | 474 | 478 | 104.71
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 62 230 | T:77&78 | 474 | 478 | 104.71
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL - CLAY PC-1 345 | T:77&78 | 474 | 478 | 104.71
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY 345/115 1TR | T:77&78 | 474 | 478 | 104.71
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY 345/115 2TR | T:77&78 | 474 | 478 | 104.71
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 230/115 1TR | T:77&78 | 474 | 478 | 104.71
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - IND 25 345 | T:77&78 | 474 | 478 | 104.7
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:MODERNLF | T:77&78 | 474 | 478 | 104.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL - CLAY PC-2 345 | T:77&78 | 474 | 478 | 104.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - VOLNEY 6 345 | T:77&78 | 474 | 478 | 104.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:VANDALIA | T:77&78 | 474 | 478 | 104.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WATERCURE - OAKDALE 71 230 | T:77&78 | 474 | 478 | 104.69
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DEWITT 345/115 2TR | T:77&78 | 474 | 478 | 104.69
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OSW - VOL 11 345 | T:77&78 | 474 | 478 | 104.69
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BURT | T:77&78 | 474 | 478 | 104.69
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN8 | T:77&78 | 474 | 478 | 104.69
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN9 | T:77&78 | 474 | 478 | 104.69
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:SRANDOLP | T:77&78 | 474 | 478 | 104.69
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - LM 14 115 | T:77&78 | 474 | 478 | 104.68
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 345/115 3TR | T:77&78 | 474 | 478 | 104.68
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 345/115 4TR | T:77&78 | 474 | 478 | 104.68
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - PANNELL RP-1 345 | T:77&78 | 474 | 478 | 104.68
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - PANNELL RP-2 345 | T:77&78 | 474 | 478 | 104.68
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA 345/115 1TR | T:77&78 | 474 | 478 | 104.68
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA 345/115 2TR | T:77&78 | 474 | 478 | 104.68
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 474 | 478 | 104.67
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 104.66
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - VOL 20 345 | T:77&78 | 474 | 478 | 104.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | T:77&78 | 474 | 478 | 104.65
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 345/115 2TR | T:77&78 | 474 | 478 | 104.65
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 4TR | T:77&78 | 474 | 478 | 104.65
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 2TR | T:77&78 | 474 | 478 | 104.65
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - 9MI1 9 345 | T:77&78 | 474 | 478 | 104.65
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - IND 25 345 | T:77&78 | 474 | 478 | 104.65
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 2TR | T:77&78 | 474 | 478 | 104.64
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FUL - CLAY 4 115 | T:77&78 | 474 | 478 | 104.64
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OSW - VOL 12 345 | T:77&78 | 474 | 478 | 104.64
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | EDIC - MRCY ue 1-7 345 | T:77&78 | 474 | 478 | 104.64
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DEWITT 345/115 2TR | T:77&78 | 474 | 478 | 104.63
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 M6TR | T:77&78 | 474 | 478 | 104.63
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 M8TR | T:77&78 | 474 | 478 | 104.63
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 1TR | T:77&78 | 474 | 478 | 104.63
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 2TR | T:77&78 | 474 | 478 | 104.63
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LHH - CLAY 7 115 | T:77&78 | 474 | 478 | 104.63
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - TEAL 11 115 | T:77&78 | 474 | 478 | 104.63
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 474 | 478 | 104.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 345/230 3TR | T:77&78 | 474 | 478 | 104.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 345/230 5TR | T:77&78 | 474 | 478 | 104.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - FITZ 10 345 | T:77&78 | 474 | 478 | 104.62
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK 230/115 31TR | T:77&78 | 474 | 478 | 104.61
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK 230/115 41TR | T:77&78 | 474 | 478 | 104.61
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 5 115 | T:77&78 | 474 | 478 | 104.61
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 345/115 3TR | T:77&78 | 474 | 478 | 104.61
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 345/115 4TR | T:77&78 | 474 | 478 | 104.61
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:OXBOWNUG | T:77&78 | 474 | 478 | 104.6
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 345/115 2TR | T:77&78 | 474 | 478 | 104.6
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - WOOD 17 115 | T:77&78 | 474 | 478 | 104.59
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 474 | 478 | 104.58
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 M7TR | T:77&78 | 474 | 478 | 104.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK 230/115 31TR | T:77&78 | 474 | 478 | 104.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK 230/115 41TR | T:77&78 | 474 | 478 | 104.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 5TR | T:77&78 | 474 | 478 | 104.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - LM 14 115 | T:77&78 | 474 | 478 | 104.57
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 2TR | T:77&78 | 474 | 478 | 104.55
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 3TR | T:77&78 | 474 | 478 | 104.55
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 4TR | T:77&78 | 474 | 478 | 104.55
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 1TR | T:77&78 | 474 | 478 | 104.55
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 2TR | T:77&78 | 474 | 478 | 104.55
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OSW 345/115 1TR | T:77&78 | 474 | 478 | 104.55
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R506 | 474 | 478 | 104.53
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 3TR | T:77&78 | 474 | 478 | 104.53
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 3 115 | T:77&78 | 474 | 478 | 104.52
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - TEAL 10 115 | T:77&78 | 474 | 478 | 104.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 474 | 478 | 104.51
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 13 345 | T:77&78 | 474 | 478 | 104.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OSW 345/115 1TR | T:77&78 | 474 | 478 | 104.5
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:9MIPT1 | T:77&78 | 474 | 478 | 104.48
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 3TR | T:77&78 | 474 | 478 | 104.48
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 104.46
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY 345/115 1TR | T:77&78 | 474 | 478 | 104.46
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY 345/115 2TR | T:77&78 | 474 | 478 | 104.46
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | VOL - MARCY 19 345 | T:77&78 | 474 | 478 | 104.43
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - BECK_TSA 345 | T:77&78 | 474 | 478 | 104.4
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - BECK_TSB 345 | T:77&78 | 474 | 478 | 104.4
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DEWITT3 - LAFAYTTE 345 | T:77&78 | 474 | 478 | 104.4
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 4MILE 230/115 1TR | T:77&78 | 474 | 478 | 104.39
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - PANNELL RP-1 345 | T:77&78 | 474 | 478 | 104.38
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 10 | T:77&78 | 474 | 478 | 104.37
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 11 | T:77&78 | 474 | 478 | 104.37
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 12 | T:77&78 | 474 | 478 | 104.37
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 13 | T:77&78 | 474 | 478 | 104.37
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 8 | T:77&78 | 474 | 478 | 104.37
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 9 | T:77&78 | 474 | 478 | 104.37
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:UDG-184 | T:77&78 | 474 | 478 | 104.37
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 4MILE 230/115 1TR | T:77&78 | 474 | 478 | 104.34
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LOCKPORT | T:77&78 | 474 | 478 | 104.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 474 | 478 | 104.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 M6TR | T:77&78 | 474 | 478 | 104.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 M8TR | T:77&78 | 474 | 478 | 104.3
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 1-3 | T:77&78 | 474 | 478 | 104.29
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 4-6 | T:77&78 | 474 | 478 | 104.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - PANNELL RP-2 345 | T:77&78 | 474 | 478 | 104.28
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 7-9 | T:77&78 | 474 | 478 | 104.28
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 10-12 | T:77&78 | 474 | 478 | 104.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 M7TR | T:77&78 | 474 | 478 | 104.26
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WATERCURE 345/230 1TR | T:77&78 | 474 | 478 | 104.24
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - DUNKIRK 73 230 | T:77&78 | 474 | 478 | 104.23
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - DUNKIRK 74 230 | T:77&78 | 474 | 478 | 104.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WATERCURE 345/230 2TR | T:77&78 | 474 | 478 | 104.22
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - FITZ 10 345 | T:77&78 | 474 | 478 | 104.21
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 13 345 | T:77&78 | 474 | 478 | 104.2
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | EDIC - MRCY ue 1-7 345 | T:77&78 | 474 | 478 | 104.16
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:SITHE 1 | T:77&78 | 474 | 478 | 104.15
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:SITHE 2 | T:77&78 | 474 | 478 | 104.15
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ELBRIDGE 345/115 1TR | T:77&78 | 474 | 478 | 104.14
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 474 | 478 | 104.13
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 345/230 4TR | T:77&78 | 474 | 478 | 104.1
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WATERCURE 345/230 1TR | T:77&78 | 474 | 478 | 104.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WATERCURE 345/230 2TR | T:77&78 | 474 | 478 | 104.07
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAG - NEWROCH 1 345 | T:77&78 | 474 | 478 | 104.01
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:ESYR | T:77&78 | 474 | 478 | 104.01
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - DUNKIRK 73 230 | T:77&78 | 474 | 478 | 103.98
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:UDG-184 | T:77&78 | 474 | 478 | 103.98
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - DUNKIRK 74 230 | T:77&78 | 474 | 478 | 103.97
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 1 | T:77&78 | 474 | 478 | 103.97
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 2 | T:77&78 | 474 | 478 | 103.97
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 3 | T:77&78 | 474 | 478 | 103.97
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | T:77&78 | 474 | 478 | 103.95
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:GINNA | T:77&78 | 474 | 478 | 103.93
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OS - EL - LFYTE 17 345 | T:77&78 | 474 | 478 | 103.89
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:SITHE 1 | T:77&78 | 474 | 478 | 103.78
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:SITHE 2 | T:77&78 | 474 | 478 | 103.78
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:ESYR | T:77&78 | 474 | 478 | 103.76
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 8 | T:77&78 | 474 | 478 | 103.69
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 9 | T:77&78 | 474 | 478 | 103.69
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 474 | 478 | 103.67
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 103.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ELBRIDGE 345/115 1TR | T:77&78 | 474 | 478 | 103.65
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:KINTIGH | T:77&78 | 474 | 478 | 103.62
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 10 | T:77&78 | 474 | 478 | 103.6
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | VOL - MARCY 19 345 | T:77&78 | 474 | 478 | 103.6
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 103.55
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | EDIC - FITZ 345 | T:77&78 | 474 | 478 | 103.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 1-3 | T:77&78 | 474 | 478 | 103.49
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 7-9 | T:77&78 | 474 | 478 | 103.49
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 10-12 | T:77&78 | 474 | 478 | 103.49
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 4-6 | T:77&78 | 474 | 478 | 103.48
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDL - FRASER 32 345 | T:77&78 | 474 | 478 | 103.47
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 474 | 478 | 103.42
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:9 MI PT2 | T:77&78 | 474 | 478 | 103.41
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 11 | T:77&78 | 474 | 478 | 103.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 12 | T:77&78 | 474 | 478 | 103.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 13 | T:77&78 | 474 | 478 | 103.35
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:OSWEGO 5 | T:77&78 | 474 | 478 | 103.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL - CLAY PC-1 345 | T:77&78 | 474 | 478 | 103.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL - CLAY PC-2 345 | T:77&78 | 474 | 478 | 103.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 474 | 478 | 103.29
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:9MIPT1 | T:77&78 | 474 | 478 | 103.27
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:GINNA | T:77&78 | 474 | 478 | 103.26
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - FARMVLY | T:77&78 | 474 | 478 | 103.19
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - EDIC 2-15 345 | T:77&78 | 474 | 478 | 103.11
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LOCKPORT | T:77&78 | 474 | 478 | 102.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:OSWEGO 6 | T:77&78 | 474 | 478 | 102.98
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 474 | 478 | 102.72
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - FARMVLY | T:77&78 | 474 | 478 | 102.67
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:FITZPATR | T:77&78 | 474 | 478 | 102.56
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | BECK - PACKARD BP76 230 | T:77&78 | 474 | 478 | 102.39
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:9 MI PT2 | T:77&78 | 474 | 478 | 102.37
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAG - NEWROCH 1 345 | T:77&78 | 474 | 478 | 101.91
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 474 | 478 | 101.88
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 474 | 478 | 101.66
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 474 | 478 | 101.64
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 474 | 478 | 101.58
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 474 | 478 | 101.53
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 3TR | T:77&78 | 474 | 478 | 101.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:79&80 | 474 | 478 | 101.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 100.75
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE - WATERCURE 69 230 | T:77&78 | 474 | 478 | 100.51
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE - ETWANDA 70 230 | T:77&78 | 474 | 478 | 100.51
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:79&80 | 474 | 478 | 100.47
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 474 | 478 | 100.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 3TR | T:77&78 | 474 | 478 | 100.07
| 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  |  |  | 122.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 103.28
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 566 | 654 | 102.48
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_T7-12 | 566 | 654 | 100.64
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 103.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 556 | 644 | 114.33
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 556 | 644 | 113.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_T7-12 | 556 | 644 | 111.68
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3230 | 556 | 644 | 109.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 345 | B:PACKT3 | 556 | 644 | 109.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | Base Case | 556 | 644 | 108.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R304 | 556 | 644 | 108.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL78 | 556 | 644 | 108.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 108
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 556 | 644 | 107.34
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 345 | 556 | 644 | 107.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 556 | 644 | 107
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3230 | 556 | 644 | 106.78
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 556 | 644 | 106.61
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 556 | 644 | 106.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 556 | 644 | 106.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 106.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R304 | 556 | 644 | 105.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 556 | 644 | 105.85
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 105.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3230 | 556 | 644 | 105.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 556 | 644 | 105.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_T7-12 | 556 | 644 | 105
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 556 | 644 | 104.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R304 | 556 | 644 | 104.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 556 | 644 | 103.58
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - INDEPNC 26 345 | S:PA_HNTL78 | 556 | 644 | 103.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - INDEPNC 26 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 103.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - INDEPNC 26 345 | S:PA_HNTL78 | 556 | 644 | 102.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-FV_37&W-F_171 | 556 | 644 | 102.45
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - INDEPNC 26 345 | SB:PA230_R3230 | 556 | 644 | 102.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - INDEPNC 26 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 102.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - INDEPNC 26 345 | SB:PA230_R3230 | 556 | 644 | 102.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - INDEPNC 26 345 | B:PACKT3 | 556 | 644 | 102.12
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - INDEPNC 26 345 | B:PACKT3 | 556 | 644 | 102.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3230 | 556 | 644 | 102
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - HOMERCTY | 556 | 644 | 101.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:67&37A | 556 | 644 | 101.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 556 | 644 | 101.83
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE_B | 556 | 644 | 101.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE 230/115 3TR | S:PA_HNTL78 | 556 | 644 | 101.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | S:PA_HNTL78 | 556 | 644 | 101.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | S:PA_HNTL78 | 556 | 644 | 101.6
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 556 | 644 | 101.58
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | S:PA_HNTL78 | 556 | 644 | 101.55
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | S:PA_HNTL78 | 556 | 644 | 101.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | Base Case | 556 | 644 | 101.37
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE 230/115 3TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 101.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 101.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | S:PA_HNTL78 | 556 | 644 | 101.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | S:PA_HNTL78 | 556 | 644 | 101.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 101.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 101.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - INDEPNC 26 345 | SB:PA230_R304 | 556 | 644 | 101.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:9 MI PT2 | S:PA_HNTL78 | 556 | 644 | 101.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - 9MI1 8 345 | S:PA_HNTL78 | 556 | 644 | 101.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - 9MI1 8 345 | S:PA_HNTL78 | 556 | 644 | 101.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OS - EL - LFYTE 17 345 | S:PA_HNTL78 | 556 | 644 | 101.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 101.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R3230 | 556 | 644 | 101.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R3230 | 556 | 644 | 101.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 101.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | SB:PA230_R3230 | 556 | 644 | 101.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R3230 | 556 | 644 | 101.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL78 | 556 | 644 | 101.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R304 | 556 | 644 | 101.03
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | S:PA_HNTL78 | 556 | 644 | 101.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 101.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:9 MI PT2 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 101
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | SB:PA230_R3230 | 556 | 644 | 100.95
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - 9MI1 8 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.95
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - 9MI1 8 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.94
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OS - EL - LFYTE 17 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.93
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-SR_37&W-F_171 | 556 | 644 | 100.9
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:FV-5M_37&W-F_171 | 556 | 644 | 100.9
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | B:PACKT3 | 556 | 644 | 100.9
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | B:PACKT3 | 556 | 644 | 100.9
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | SB:PA230_R3230 | 556 | 644 | 100.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - 9MI1 8 345 | SB:PA230_R3230 | 556 | 644 | 100.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OS - EL - LFYTE 17 345 | SB:PA230_R3230 | 556 | 644 | 100.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - INDEPNC 26 345 | SB:PA230_R304 | 556 | 644 | 100.83
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R3230 | 556 | 644 | 100.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | B:PACKT3 | 556 | 644 | 100.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | B:PACKT3 | 556 | 644 | 100.82
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R3230 | 556 | 644 | 100.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - 9MI1 8 345 | B:PACKT3 | 556 | 644 | 100.72
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | B:PACKT3 | 556 | 644 | 100.71
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OS - EL - LFYTE 17 345 | B:PACKT3 | 556 | 644 | 100.71
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3230 | 556 | 644 | 100.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:HOORKN85 | S:PA_HNTL78 | 556 | 644 | 100.7
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - SHLDON 67 230 | S:PA_HNTL78 | 556 | 644 | 100.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:HOORKN86 | S:PA_HNTL78 | 556 | 644 | 100.64
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | B:PACKT3 | 556 | 644 | 100.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE 230/115 3TR | SB:PA230_R3230 | 556 | 644 | 100.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | B:PACKT3 | 556 | 644 | 100.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | S:PA_HNTL78 | 556 | 644 | 100.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | B:PACKT3 | 556 | 644 | 100.53
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | B:PACKT3 | 556 | 644 | 100.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | S:PA_HNTL78 | 556 | 644 | 100.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE 230/115 3TR | B:PACKT3 | 556 | 644 | 100.46
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:HOORKN85 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.45
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - SHLDON 67 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:HOORKN86 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | SB:PA230_R3230 | 556 | 644 | 100.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 556 | 644 | 100.34
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:9 MI PT2 | S:PA_HNTL78 | 556 | 644 | 100.34
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - VOLNEY 6 345 | S:PA_HNTL78 | 556 | 644 | 100.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:OSWEGO 6 | S:PA_HNTL78 | 556 | 644 | 100.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:FITZPATR | S:PA_HNTL78 | 556 | 644 | 100.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3230 | 556 | 644 | 100.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | S:PA_HNTL78 | 556 | 644 | 100.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.25
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | SB:PA230_R3230 | 556 | 644 | 100.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3230 | 556 | 644 | 100.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 556 | 644 | 100.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | B:PACKT3 | 556 | 644 | 100.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:9 MI PT2 | SB:PA230_R3230 | 556 | 644 | 100.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE 230/115 4TR | S:PA_HNTL78 | 556 | 644 | 100.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL78 | 556 | 644 | 100.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:9 MI PT2 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:OSWEGO 5 | S:PA_HNTL78 | 556 | 644 | 100.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 556 | 644 | 100.1
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:OSWEGO 6 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:HOORKN85 | SB:PA230_R3230 | 556 | 644 | 100.1
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - VOLNEY 6 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.08
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:HOORKN86 | SB:PA230_R3230 | 556 | 644 | 100.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 556 | 644 | 100.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:FITZPATR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | B:PACKT3 | 556 | 644 | 100.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:FITZPATR | S:PA_HNTL78 | 556 | 644 | 100.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | SB:PA230_R304 | 556 | 644 | 100.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG 345/115 1TR | S:PA_HNTL78 | 556 | 644 | 100.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R3230 | 556 | 644 | 100.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - 9MI1 8 345 | SB:PA230_R3230 | 556 | 644 | 100.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 100.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - VOLNEY 6 345 | SB:PA230_R3230 | 556 | 644 | 100.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:9 MI PT2 | SB:PA230_R3230 | 556 | 644 | 100.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:9 MI PT2 | B:PACKT3 | 556 | 644 | 100.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:OSWEGO 6 | SB:PA230_R3230 | 556 | 644 | 100
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R3230 | 556 | 644 | 100
| 135303 SAWYER77 230 135415 PACKARD2 230 1 Max |  |  |  |  | 114.33
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 104.23
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 566 | 654 | 103.53
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_T7-12 | 566 | 654 | 101.59
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 Max |  |  |  |  | 104.23
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 556 | 644 | 115.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 556 | 644 | 114.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_T7-12 | 556 | 644 | 112.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | Base Case | 556 | 644 | 109.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL77 | 556 | 644 | 108.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 556 | 644 | 108.22
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 108.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 345 | 556 | 644 | 107.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 107.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 556 | 644 | 107.54
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 556 | 644 | 106.79
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 556 | 644 | 106.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 106.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3430 | 556 | 644 | 106.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 556 | 644 | 106.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 345 | B:PACKT4 | 556 | 644 | 106
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 105.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 556 | 644 | 105.22
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_T7-12 | 556 | 644 | 105.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 345 | SB:PA230_R506 | 556 | 644 | 105.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:61&64 | 556 | 644 | 104.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3430 | 556 | 644 | 104.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | B:PACKT4 | 556 | 644 | 104.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R506 | 556 | 644 | 103.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - INDEPNC 26 345 | S:PA_HNTL77 | 556 | 644 | 103.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-FV_37&W-F_171 | 556 | 644 | 103.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - INDEPNC 26 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 103.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3430 | 556 | 644 | 103.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | B:PACKT4 | 556 | 644 | 102.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - HOMERCTY | 556 | 644 | 102.83
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - INDEPNC 26 345 | S:PA_HNTL77 | 556 | 644 | 102.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - INDEPNC 26 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 102.51
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:67&37A | 556 | 644 | 102.45
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE_B | 556 | 644 | 102.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R506 | 556 | 644 | 102.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE 230/115 3TR | S:PA_HNTL77 | 556 | 644 | 101.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | S:PA_HNTL77 | 556 | 644 | 101.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | S:PA_HNTL77 | 556 | 644 | 101.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 556 | 644 | 101.76
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | S:PA_HNTL77 | 556 | 644 | 101.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | S:PA_HNTL77 | 556 | 644 | 101.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | Base Case | 556 | 644 | 101.66
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE 230/115 3TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.56
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | S:PA_HNTL77 | 556 | 644 | 101.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | S:PA_HNTL77 | 556 | 644 | 101.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-SR_37&W-F_171 | 556 | 644 | 101.47
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:FV-5M_37&W-F_171 | 556 | 644 | 101.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:9 MI PT2 | S:PA_HNTL77 | 556 | 644 | 101.44
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - 9MI1 8 345 | S:PA_HNTL77 | 556 | 644 | 101.42
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - 9MI1 8 345 | S:PA_HNTL77 | 556 | 644 | 101.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OS - EL - LFYTE 17 345 | S:PA_HNTL77 | 556 | 644 | 101.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL77 | 556 | 644 | 101.34
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | S:PA_HNTL77 | 556 | 644 | 101.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:9 MI PT2 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - 9MI1 8 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.14
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OS - EL - LFYTE 17 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.13
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - 9MI1 8 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.12
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 101.06
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.97
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:HOORKN85 | S:PA_HNTL77 | 556 | 644 | 100.91
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - SHLDON 67 230 | S:PA_HNTL77 | 556 | 644 | 100.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:40&41 | 556 | 644 | 100.85
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:HOORKN86 | S:PA_HNTL77 | 556 | 644 | 100.85
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | S:PA_HNTL77 | 556 | 644 | 100.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | S:PA_HNTL77 | 556 | 644 | 100.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:HOORKN85 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - SHLDON 67 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:HOORKN86 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.58
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAG345_3108 | 556 | 644 | 100.57
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 556 | 644 | 100.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:9 MI PT2 | S:PA_HNTL77 | 556 | 644 | 100.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - VOLNEY 6 345 | S:PA_HNTL77 | 556 | 644 | 100.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:OSWEGO 6 | S:PA_HNTL77 | 556 | 644 | 100.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:FITZPATR | S:PA_HNTL77 | 556 | 644 | 100.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | S:PA_HNTL77 | 556 | 644 | 100.46
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 556 | 644 | 100.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE 230/115 4TR | S:PA_HNTL77 | 556 | 644 | 100.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL77 | 556 | 644 | 100.38
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:OSWEGO 5 | S:PA_HNTL77 | 556 | 644 | 100.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:9 MI PT2 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.32
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:OSWEGO 6 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.29
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:255_345B302 | 556 | 644 | 100.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - VOLNEY 6 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.27
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:FITZPATR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:FITZPATR | S:PA_HNTL77 | 556 | 644 | 100.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG 345/115 1TR | S:PA_HNTL77 | 556 | 644 | 100.19
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OS - EL - LFYTE 17 345 | S:PA_HNTL77 | 556 | 644 | 100.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 556 | 644 | 100.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 4 MILE - ERIE SE 230 | S:PA_HNTL77 | 556 | 644 | 100.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - VOLNEY 6 345 | S:PA_HNTL77 | 556 | 644 | 100.18
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - NEWROCH 1 345 | 556 | 644 | 100.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.15
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LOCKPORT | S:PA_HNTL77 | 556 | 644 | 100.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | S:PA_HNTL77 | 556 | 644 | 100.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 7 | S:PA_HNTL77 | 556 | 644 | 100.13
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL77 | 556 | 644 | 100.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE 230/115 4TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 4 | S:PA_HNTL77 | 556 | 644 | 100.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 5 | S:PA_HNTL77 | 556 | 644 | 100.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 6 | S:PA_HNTL77 | 556 | 644 | 100.1
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:OSWEGO 5 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL77 | 556 | 644 | 100.09
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH 345/115 5TR | S:PA_HNTL77 | 556 | 644 | 100.09
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-1 345 | S:PA_HNTL77 | 556 | 644 | 100.09
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - VOL 21 345 | S:PA_HNTL77 | 556 | 644 | 100.09
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:STL1_G1 | S:PA_HNTL77 | 556 | 644 | 100.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:STL1_G2 | S:PA_HNTL77 | 556 | 644 | 100.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | S:PA_HNTL77 | 556 | 644 | 100.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | S:PA_HNTL77 | 556 | 644 | 100.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | S:PA_HNTL77 | 556 | 644 | 100.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WATERCURE - OAKDALE 71 230 | S:PA_HNTL77 | 556 | 644 | 100.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | S:PA_HNTL77 | 556 | 644 | 100.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH 345/115 2TR | S:PA_HNTL77 | 556 | 644 | 100.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-2 345 | S:PA_HNTL77 | 556 | 644 | 100.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | S:PA_HNTL77 | 556 | 644 | 100.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | S:PA_HNTL77 | 556 | 644 | 100.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW - VOL 11 345 | S:PA_HNTL77 | 556 | 644 | 100.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - VOL 20 345 | S:PA_HNTL77 | 556 | 644 | 100.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:ELLICTVL | S:PA_HNTL77 | 556 | 644 | 100.04
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA 345/115 1TR | S:PA_HNTL77 | 556 | 644 | 100.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA 345/115 2TR | S:PA_HNTL77 | 556 | 644 | 100.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OKDLE 345/115 2TR | S:PA_HNTL77 | 556 | 644 | 100.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BURT | S:PA_HNTL77 | 556 | 644 | 100.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN8 | S:PA_HNTL77 | 556 | 644 | 100.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN9 | S:PA_HNTL77 | 556 | 644 | 100.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:SRANDOLP | S:PA_HNTL77 | 556 | 644 | 100.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:FITZPATR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 100.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OKDLE 345/115 3TR | S:PA_HNTL77 | 556 | 644 | 100.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OKDLE 345/115 4TR | S:PA_HNTL77 | 556 | 644 | 100.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:VANDALIA | S:PA_HNTL77 | 556 | 644 | 100.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK PA27 230 | S:PA_HNTL77 | 556 | 644 | 100.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | T:77&80 | 556 | 644 | 100.01
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 345/230 3TR | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 345/230 5TR | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 3TR | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 4TR | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-1 345 | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 1TR | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 2TR | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 5 115 | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - LM 14 115 | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FUL - CLAY 4 115 | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LHH - CLAY 7 115 | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 10 115 | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 11 115 | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - WOOD 17 115 | S:PA_HNTL77 | 556 | 644 | 100
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OKDLE 230/115 1TR | S:PA_HNTL77 | 556 | 644 | 100
| 135304 SAWYER78 230 135415 PACKARD2 230 2 Max |  |  |  |  | 115.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:62&BP76 | 620 | 717 | 117.54 | 100.2095
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:62&PA27 | 620 | 717 | 111.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:62&BP76 | 620 | 717 | 111.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:62&BP76 | 620 | 717 | 110.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:62&BP76 | 620 | 717 | 109.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - INDEPNC 26 345 | T:62&BP76 | 620 | 717 | 109.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | STOLLRD - GARDENVILL 66 230 | 620 | 717 | 109.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:62&BP76 | 620 | 717 | 108.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - 9MI1 8 345 | T:62&BP76 | 620 | 717 | 108.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OS - EL - LFYTE 17 345 | T:62&BP76 | 620 | 717 | 108.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | B:STOLE230 | 620 | 717 | 107.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 107.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | T:62&BP76 | 620 | 717 | 107.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | Base Case | 620 | 717 | 107.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | T:62&BP76 | 620 | 717 | 107.77
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | T:62&BP76 | 620 | 717 | 107.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | T:62&BP76 | 620 | 717 | 107.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:GARD230_T7-12 | 620 | 717 | 107.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROBI230 | 620 | 717 | 107.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - ROBINSON 64 345 | 620 | 717 | 107.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - VOLNEY 6 345 | T:62&BP76 | 620 | 717 | 107.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:OSWEGO 6 | T:62&BP76 | 620 | 717 | 106.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:9 MI PT2 | T:62&BP76 | 620 | 717 | 106.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:FITZPATR | T:62&BP76 | 620 | 717 | 106.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:OSWEGO 5 | T:62&BP76 | 620 | 717 | 106.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R506 | 620 | 717 | 106.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | T:62&BP76 | 620 | 717 | 106.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | T:62&BP76 | 620 | 717 | 106.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:62&BP76 | 620 | 717 | 106.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:GINNA | T:62&BP76 | 620 | 717 | 105.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | T:62&BP76 | 620 | 717 | 105.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:9MIPT1 | T:62&BP76 | 620 | 717 | 104.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:62&PA27 | 620 | 717 | 104.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - SHLDON 67 230 | T:62&BP76 | 620 | 717 | 104.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | T:62&BP76 | 620 | 717 | 104.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:5M-SR_37&W-F_171 | T:62&BP76 | 620 | 717 | 104.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HOMERCTY - STOLLRD 37 345 | T:62&BP76 | 620 | 717 | 103.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 5 MILE - STOLLE 37A 345 | T:62&BP76 | 620 | 717 | 103.77
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 1 | T:62&BP76 | 620 | 717 | 103.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 2 | T:62&BP76 | 620 | 717 | 103.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 3 | T:62&BP76 | 620 | 717 | 103.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 345/230 4TR | T:62&PA27 | 620 | 717 | 103.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS1 | T:62&BP76 | 620 | 717 | 103.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:INDEK-OL | T:62&BP76 | 620 | 717 | 103.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:62&PA27 | 620 | 717 | 103.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:NIAG345_3108 | 620 | 717 | 103.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - WATERCURE 69 230 | T:62&BP76 | 620 | 717 | 102.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - ETWANDA 70 230 | T:62&BP76 | 620 | 717 | 102.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | T:62&BP76 | 620 | 717 | 102.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - VOL 21 345 | T:62&BP76 | 620 | 717 | 102.57
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:SITHE 1 | T:62&BP76 | 620 | 717 | 102.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:SITHE 2 | T:62&BP76 | 620 | 717 | 102.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 13 345 | T:62&BP76 | 620 | 717 | 102.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | T:62&PA27 | 620 | 717 | 102.5
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:62&PA27 | 620 | 717 | 102.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:JAMESGN7 | T:62&BP76 | 620 | 717 | 102.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE 230/115 3TR | T:62&BP76 | 620 | 717 | 102.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - INDEPNC 26 345 | T:62&PA27 | 620 | 717 | 102.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | EDIC - FITZ 345 | T:62&BP76 | 620 | 717 | 102.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 345/230 4TR | T:62&BP76 | 620 | 717 | 102.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - EDIC 2-15 345 | T:62&BP76 | 620 | 717 | 102.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:62&BP76 | 620 | 717 | 102.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:62&BP76 | 620 | 717 | 102.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:62&BP76 | 620 | 717 | 102.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DEWITT3 - LAFAYTTE 345 | T:62&BP76 | 620 | 717 | 102.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:62&BP76 | 620 | 717 | 102.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - BECK PA27 230 | T:62&BP76 | 620 | 717 | 102.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R506 | 620 | 717 | 102
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 5 MILE 345/115 1TR | T:62&BP76 | 620 | 717 | 101.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH 345/115 2TR | T:62&BP76 | 620 | 717 | 101.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS2 | T:62&BP76 | 620 | 717 | 101.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 345/230 3TR | T:62&BP76 | 620 | 717 | 101.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 345/230 5TR | T:62&BP76 | 620 | 717 | 101.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LOCKPORT | T:62&BP76 | 620 | 717 | 101.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 4 MILE - ERIE SE 230 | T:62&BP76 | 620 | 717 | 101.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - ELM 71 230 | T:62&BP76 | 620 | 717 | 101.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH 345/115 1TR | T:62&BP76 | 620 | 717 | 101.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | T:62&PA27 | 620 | 717 | 101.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MAINSBRG 345/115 1TR | T:62&BP76 | 620 | 717 | 101.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | ROBINSON - STOLLRD 65 230 | 620 | 717 | 101.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:HOORKN85 | T:62&BP76 | 620 | 717 | 101.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:HOORKN86 | T:62&BP76 | 620 | 717 | 101.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:STL1_G1 | T:62&BP76 | 620 | 717 | 101.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:STL1_G2 | T:62&BP76 | 620 | 717 | 101.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | T:62&BP76 | 620 | 717 | 101.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 101.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NEWROCH 345/115 2TR | T:62&BP76 | 620 | 717 | 101.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NEWROCH 345/115 1TR | T:62&BP76 | 620 | 717 | 101.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH 345/115 3TR | T:62&BP76 | 620 | 717 | 101.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:PA27&BP76 | 620 | 717 | 101.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:Q234_CLIB_G10 | T:62&BP76 | 620 | 717 | 101.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:Q234_CLIB_G20 | T:62&BP76 | 620 | 717 | 101.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - WTRCR 31 345 | T:62&BP76 | 620 | 717 | 101.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - LM 14 115 | T:62&BP76 | 620 | 717 | 101.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:MODERNLF | T:62&BP76 | 620 | 717 | 101.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WATERCURE 345/230 1TR | T:62&BP76 | 620 | 717 | 101.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WATERCURE 345/230 2TR | T:62&BP76 | 620 | 717 | 101.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 5 115 | T:62&BP76 | 620 | 717 | 101.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LHH - CLAY 7 115 | T:62&BP76 | 620 | 717 | 101.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - TEAL 11 115 | T:62&BP76 | 620 | 717 | 101.35
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:62&BP76 | 620 | 717 | 101.34 | 86.3981
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OKDLE 345/115 3TR | T:62&BP76 | 620 | 717 | 101.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OKDLE 345/115 4TR | T:62&BP76 | 620 | 717 | 101.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBRD 230/115/34.5 1TR | T:62&BP76 | 620 | 717 | 101.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FUL - CLAY 4 115 | T:62&BP76 | 620 | 717 | 101.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - WOOD 17 115 | T:62&BP76 | 620 | 717 | 101.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | VOL - MARCY 19 345 | T:62&BP76 | 620 | 717 | 101.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OKDLE 345/115 2TR | T:62&BP76 | 620 | 717 | 101.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:ELLICTVL | T:62&BP76 | 620 | 717 | 101.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:GENMLS61 | T:62&BP76 | 620 | 717 | 101.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:OXBOWNUG | T:62&BP76 | 620 | 717 | 101.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:DUPONT46 | T:62&BP76 | 620 | 717 | 101.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:WOLEAN55 | T:62&BP76 | 620 | 717 | 101.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - NEWROCH 1 345 | T:62&BP76 | 620 | 717 | 101.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - NEWROCH 2 345 | T:62&BP76 | 620 | 717 | 101.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - NEWROCH 3 345 | T:62&BP76 | 620 | 717 | 101.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - 9MI1 8 345 | T:62&PA27 | 620 | 717 | 101.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | T:62&BP76 | 620 | 717 | 101.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 101.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - VOL 20 345 | T:62&BP76 | 620 | 717 | 101.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BURT | T:62&BP76 | 620 | 717 | 101.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:HYDLRACE | T:62&BP76 | 620 | 717 | 101.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:JAMESGN8 | T:62&BP76 | 620 | 717 | 101.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:JAMESGN9 | T:62&BP76 | 620 | 717 | 101.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:SRANDOLP | T:62&BP76 | 620 | 717 | 101.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:VANDALIA | T:62&BP76 | 620 | 717 | 101.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA 345/115 1TR | T:62&BP76 | 620 | 717 | 101.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA 345/115 2TR | T:62&BP76 | 620 | 717 | 101.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OSW - VOL 11 345 | T:62&BP76 | 620 | 717 | 101.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL 345/115 1TR | T:62&BP76 | 620 | 717 | 101.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL 345/115 2TR | T:62&BP76 | 620 | 717 | 101.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OSW - VOL 12 345 | T:62&BP76 | 620 | 717 | 101.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DUNKIRK 230/115 31TR | T:62&BP76 | 620 | 717 | 101.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DUNKIRK 230/115 41TR | T:62&BP76 | 620 | 717 | 101.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - 9MI1 9 345 | T:62&BP76 | 620 | 717 | 101.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | T:62&PA27 | 620 | 717 | 101.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL 345/115 3TR | T:62&BP76 | 620 | 717 | 101.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY 345/115 1TR | T:62&BP76 | 620 | 717 | 101.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY 345/115 2TR | T:62&BP76 | 620 | 717 | 101.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OSW 345/115 1TR | T:62&BP76 | 620 | 717 | 101.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SHLDON - STONYCR 230 | T:62&BP76 | 620 | 717 | 101.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OS - EL - LFYTE 17 345 | T:62&PA27 | 620 | 717 | 101.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | T:62&BP76 | 620 | 717 | 101.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - IND 25 345 | T:62&BP76 | 620 | 717 | 101.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OKDLE 230/115 1TR | T:62&BP76 | 620 | 717 | 101.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WATERCURE - OAKDALE 71 230 | T:62&BP76 | 620 | 717 | 101.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DEWITT 345/115 2TR | T:62&BP76 | 620 | 717 | 101.08
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | T:62&BP76 | 620 | 717 | 101.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | BECK - PACKARD BP76 230 | 620 | 717 | 101.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:62&BP76 | 620 | 717 | 101.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 4MILE 230/115 1TR | T:62&BP76 | 620 | 717 | 100.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:62&PA27 | 620 | 717 | 100.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - BECK_TSA 345 | T:62&BP76 | 620 | 717 | 100.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - BECK_TSB 345 | T:62&BP76 | 620 | 717 | 100.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL 230/115 3TR | T:62&BP76 | 620 | 717 | 100.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL 230/115 4TR | T:62&BP76 | 620 | 717 | 100.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:UDG-184 | T:62&BP76 | 620 | 717 | 100.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | T:62&PA27 | 620 | 717 | 100.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | T:62&BP76 | 620 | 717 | 100.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE 230/115 4TR | T:62&BP76 | 620 | 717 | 100.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | T:62&PA27 | 620 | 717 | 100.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL 230/115 2TR | T:62&BP76 | 620 | 717 | 100.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - FITZ 10 345 | T:62&BP76 | 620 | 717 | 100.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:FITZPATR | T:62&PA27 | 620 | 717 | 100.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL 230/115 M7TR | T:62&BP76 | 620 | 717 | 100.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | EDIC - MRCY ue 1-7 345 | T:62&BP76 | 620 | 717 | 100.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - VOLNEY 6 345 | T:62&PA27 | 620 | 717 | 100.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ELBRIDGE 345/115 1TR | T:62&BP76 | 620 | 717 | 100.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL 230/115 M6TR | T:62&BP76 | 620 | 717 | 100.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL 230/115 M8TR | T:62&BP76 | 620 | 717 | 100.51
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:62&BP76 | 620 | 717 | 100.44
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | BECK - PACKARD BP76 230 | 620 | 717 | 100.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STNYRDG - HILLSIDE 68B 230 | T:62&BP76 | 620 | 717 | 100.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:OSWEGO 6 | T:62&PA27 | 620 | 717 | 100.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 100.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-1 345 | T:62&BP76 | 620 | 717 | 100.22
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | T:62&BP76 | 620 | 717 | 100.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-2 345 | T:62&BP76 | 620 | 717 | 100.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 73 230 | T:62&BP76 | 620 | 717 | 100.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 100.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 74 230 | T:62&BP76 | 620 | 717 | 100.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:OSWEGO 5 | T:62&PA27 | 620 | 717 | 100.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:62&PA27 | 620 | 717 | 100.06
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 Max |  |  |  |  | 117.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | T:61&64 | 620 | 717 | 117.77 | 100.4056
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 1TR | T:61&64 | 620 | 717 | 117
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | T:61&64 | 620 | 717 | 116
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - INDEPNC 26 345 | T:61&64 | 620 | 717 | 114.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | T:61&64 | 620 | 717 | 114.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OS - EL - LFYTE 17 345 | T:61&64 | 620 | 717 | 113.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - 9MI1 8 345 | T:61&64 | 620 | 717 | 113.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LFYTE - CLARKCRNS 36A 345 | T:61&64 | 620 | 717 | 112.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:FITZPATR | T:61&64 | 620 | 717 | 112.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - VOLNEY 6 345 | T:61&64 | 620 | 717 | 112.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-FV_37&W-F_171 | T:61&64 | 620 | 717 | 112.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 4TR | T:61&64 | 620 | 717 | 112.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:OSWEGO 6 | T:61&64 | 620 | 717 | 112.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:9 MI PT2 | T:61&64 | 620 | 717 | 112.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - HOMERCTY | T:61&64 | 620 | 717 | 112.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - SHLDON 67 230 | T:61&64 | 620 | 717 | 112.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:OSWEGO 5 | T:61&64 | 620 | 717 | 112.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - CLARKCRNS 36B 345 | T:61&64 | 620 | 717 | 111.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-SR_37&W-F_171 | T:61&64 | 620 | 717 | 111.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:FV-5M_37&W-F_171 | T:61&64 | 620 | 717 | 111.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK PA27 230 | T:61&64 | 620 | 717 | 110.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:9MIPT1 | T:61&64 | 620 | 717 | 110.57
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - KINTIGH 345 | T:61&64 | 620 | 717 | 110.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - 5MILE 345 | T:61&64 | 620 | 717 | 110.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 345 | T:61&191 | 620 | 717 | 109.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:5M-SR_37&W-F_171 | T:61&64 | 620 | 717 | 109.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 3TR | T:61&64 | 620 | 717 | 109.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 5TR | T:61&64 | 620 | 717 | 109.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HOMERCTY - STOLLRD 37 345 | T:61&64 | 620 | 717 | 108.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 5 MILE - STOLLE 37A 345 | T:61&64 | 620 | 717 | 108.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | STOLLRD - GARDENVILL 66 230 | 620 | 717 | 108.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS1 | T:61&64 | 620 | 717 | 108.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LOCKPORT | T:61&64 | 620 | 717 | 108.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - WATERCURE 69 230 | T:61&64 | 620 | 717 | 108.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - ETWANDA 70 230 | T:61&64 | 620 | 717 | 108.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:INDEK-OL | T:61&64 | 620 | 717 | 108.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 5TR | T:61&64 | 620 | 717 | 108.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE 230/115 3TR | T:61&64 | 620 | 717 | 108.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 13 345 | T:61&64 | 620 | 717 | 108.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:JAMESGN7 | T:61&64 | 620 | 717 | 108
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | EDIC - FITZ 345 | T:61&64 | 620 | 717 | 107.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - EDIC 2-15 345 | T:61&64 | 620 | 717 | 107.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 2TR | T:61&64 | 620 | 717 | 107.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | B:STOLE230 | 620 | 717 | 107.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | T:61&64 | 620 | 717 | 107.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - VOL 21 345 | T:61&64 | 620 | 717 | 107.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DEWITT3 - LAFAYTTE 345 | T:61&64 | 620 | 717 | 107.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SHLDON - STONYCR 230 | T:61&64 | 620 | 717 | 107.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | Base Case | 620 | 717 | 107.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 2TR | T:61&64 | 620 | 717 | 107.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 107.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 345 | T:61&64 | 620 | 717 | 107.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 5 MILE 345/115 1TR | T:61&64 | 620 | 717 | 107.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 1 | T:61&64 | 620 | 717 | 107.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 2 | T:61&64 | 620 | 717 | 107.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 3 | T:61&64 | 620 | 717 | 107.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS2 | T:61&64 | 620 | 717 | 107.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 4 MILE - ERIE SE 230 | T:61&64 | 620 | 717 | 107.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 1TR | T:61&64 | 620 | 717 | 107.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 4 | T:61&64 | 620 | 717 | 107.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 5 | T:61&64 | 620 | 717 | 107.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 6 | T:61&64 | 620 | 717 | 107.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 7 | T:61&64 | 620 | 717 | 107.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | VOL - MARCY 19 345 | T:61&64 | 620 | 717 | 107.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MAINSBRG 345/115 1TR | T:61&64 | 620 | 717 | 107.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 3TR | T:61&64 | 620 | 717 | 107.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:STL1_G1 | T:61&64 | 620 | 717 | 107.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:STL1_G2 | T:61&64 | 620 | 717 | 107.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NEWROCH 345/115 1TR | T:61&64 | 620 | 717 | 107.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NEWROCH 345/115 2TR | T:61&64 | 620 | 717 | 107.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - ELM 71 230 | T:61&64 | 620 | 717 | 107.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:HOORKN85 | T:61&64 | 620 | 717 | 107.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:HOORKN86 | T:61&64 | 620 | 717 | 107.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - WTRCR 31 345 | T:61&64 | 620 | 717 | 107.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROBI230 | 620 | 717 | 107.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:GARD230_T7-12 | 620 | 717 | 107.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:DUPONT46 | T:61&64 | 620 | 717 | 107.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - LM 14 115 | T:61&64 | 620 | 717 | 107.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:Q234_CLIB_G10 | T:61&64 | 620 | 717 | 107.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:Q234_CLIB_G20 | T:61&64 | 620 | 717 | 107.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:GINNA | T:61&64 | 620 | 717 | 107.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WATERCURE 345/230 1TR | T:61&64 | 620 | 717 | 107.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WATERCURE 345/230 2TR | T:61&64 | 620 | 717 | 107.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 5 115 | T:61&64 | 620 | 717 | 107.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OKDLE 345/115 3TR | T:61&64 | 620 | 717 | 107.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OKDLE 345/115 4TR | T:61&64 | 620 | 717 | 107.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LHH - CLAY 7 115 | T:61&64 | 620 | 717 | 107.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - TEAL 11 115 | T:61&64 | 620 | 717 | 107.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OKDLE 345/115 2TR | T:61&64 | 620 | 717 | 107.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:OXBOWNUG | T:61&64 | 620 | 717 | 107.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FUL - CLAY 4 115 | T:61&64 | 620 | 717 | 107.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - WOOD 17 115 | T:61&64 | 620 | 717 | 107.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:GENMLS61 | T:61&64 | 620 | 717 | 107.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:ELLICTVL | T:61&64 | 620 | 717 | 107.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:MODERNLF | T:61&64 | 620 | 717 | 107.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - NEWROCH 1 345 | T:61&64 | 620 | 717 | 107
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - NEWROCH 2 345 | T:61&64 | 620 | 717 | 107
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - NEWROCH 3 345 | T:61&64 | 620 | 717 | 107
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:61&64 | 620 | 717 | 106.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA - ROBINSON 64 345 | 620 | 717 | 106.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL 345/115 1TR | T:61&64 | 620 | 717 | 106.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL 345/115 2TR | T:61&64 | 620 | 717 | 106.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:WOLEAN55 | T:61&64 | 620 | 717 | 106.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - VOL 20 345 | T:61&64 | 620 | 717 | 106.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BURT | T:61&64 | 620 | 717 | 106.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:HYDLRACE | T:61&64 | 620 | 717 | 106.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:VANDALIA | T:61&64 | 620 | 717 | 106.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL 345/115 3TR | T:61&64 | 620 | 717 | 106.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY 345/115 1TR | T:61&64 | 620 | 717 | 106.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY 345/115 2TR | T:61&64 | 620 | 717 | 106.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA 345/115 1TR | T:61&64 | 620 | 717 | 106.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA 345/115 2TR | T:61&64 | 620 | 717 | 106.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OSW - VOL 11 345 | T:61&64 | 620 | 717 | 106.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:JAMESGN8 | T:61&64 | 620 | 717 | 106.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:JAMESGN9 | T:61&64 | 620 | 717 | 106.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:SRANDOLP | T:61&64 | 620 | 717 | 106.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:SITHE 1 | T:61&64 | 620 | 717 | 106.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:SITHE 2 | T:61&64 | 620 | 717 | 106.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OSW - VOL 12 345 | T:61&64 | 620 | 717 | 106.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OSW 345/115 1TR | T:61&64 | 620 | 717 | 106.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - 9MI1 9 345 | T:61&64 | 620 | 717 | 106.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDL - FRASER 32 345 | T:61&64 | 620 | 717 | 106.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DUNKIRK 230/115 31TR | T:61&64 | 620 | 717 | 106.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DUNKIRK 230/115 41TR | T:61&64 | 620 | 717 | 106.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - IND 25 345 | T:61&64 | 620 | 717 | 106.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OKDLE 230/115 1TR | T:61&64 | 620 | 717 | 106.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DEWITT 345/115 2TR | T:61&64 | 620 | 717 | 106.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WATERCURE - OAKDALE 71 230 | T:61&64 | 620 | 717 | 106.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBRD 230/115/34.5 1TR | T:61&64 | 620 | 717 | 106.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 4MILE 230/115 1TR | T:61&64 | 620 | 717 | 106.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:UDG-184 | T:61&64 | 620 | 717 | 106.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK_TSA 345 | T:61&64 | 620 | 717 | 106.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK_TSB 345 | T:61&64 | 620 | 717 | 106.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL 230/115 3TR | T:61&64 | 620 | 717 | 106.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL 230/115 4TR | T:61&64 | 620 | 717 | 106.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE 230/115 4TR | T:61&64 | 620 | 717 | 106.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - FITZ 10 345 | T:61&64 | 620 | 717 | 106.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL 230/115 2TR | T:61&64 | 620 | 717 | 106.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | EDIC - MRCY ue 1-7 345 | T:61&64 | 620 | 717 | 106.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL 230/115 M7TR | T:61&64 | 620 | 717 | 106.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ELBRIDGE 345/115 1TR | T:61&64 | 620 | 717 | 106.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 4TR | T:61&64 | 620 | 717 | 106.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL 230/115 M6TR | T:61&64 | 620 | 717 | 106.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL 230/115 M8TR | T:61&64 | 620 | 717 | 106.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-1 345 | T:61&64 | 620 | 717 | 106.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-2 345 | T:61&64 | 620 | 717 | 106.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 73 230 | T:61&64 | 620 | 717 | 106.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 74 230 | T:61&64 | 620 | 717 | 106.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:ESYR | T:61&64 | 620 | 717 | 105.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STNYRDG - HILLSIDE 68B 230 | T:61&64 | 620 | 717 | 105.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - ELM 70 230 | T:61&64 | 620 | 717 | 105.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ERIE E - 4 MILE 230 | T:61&64 | 620 | 717 | 105.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - FARMVLY | T:61&64 | 620 | 717 | 105.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MEYER - CANDQUA 60 230 | T:61&64 | 620 | 717 | 105.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | T:61&64 | 620 | 717 | 105.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DUNKIRK - SRIPL 68 230 | T:61&64 | 620 | 717 | 104.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SRIPL - ERIE E 69 230 | T:61&64 | 620 | 717 | 104.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STONYCR - WTHRS 230 | T:61&64 | 620 | 717 | 104.55
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-WC_30&W-F_171 | T:61&64 | 620 | 717 | 103.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CANDQUA - STNYRDG 68A 230 | T:61&64 | 620 | 717 | 103.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HCWC/NWES | T:61&64 | 620 | 717 | 103.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:MBWC/NWES | T:61&64 | 620 | 717 | 103.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WTRCR - MAINSBRG 30A 345 | T:61&64 | 620 | 717 | 103.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL - CLAY PC-1 345 | T:61&64 | 620 | 717 | 103.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 7-9 | T:61&64 | 620 | 717 | 103.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 10-12 | T:61&64 | 620 | 717 | 103.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 1-3 | T:61&64 | 620 | 717 | 103.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL - CLAY PC-2 345 | T:61&64 | 620 | 717 | 103.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 4-6 | T:61&64 | 620 | 717 | 103.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | T:61&191 | 620 | 717 | 103.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | T:61&191 | 620 | 717 | 103.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:KINTIGH | T:61&64 | 620 | 717 | 103.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:NIAG345_3108 | 620 | 717 | 102.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-MB_30&W-F_171 | T:61&64 | 620 | 717 | 102.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HCMB/NWES | T:61&64 | 620 | 717 | 102.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MAINSBRG - HOMERCITY 30B 345 | T:61&64 | 620 | 717 | 102.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WTHRS - MEYER 230 | T:61&64 | 620 | 717 | 102.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | T:61&191 | 620 | 717 | 102.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 3TR | T:61&64 | 620 | 717 | 101.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | ROBINSON - STOLLRD 65 230 | 620 | 717 | 101.72
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-SR_37&W-F_171 | T:61&64 | 620 | 717 | 101.63 | 86.6453
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:FV-5M_37&W-F_171 | T:61&64 | 620 | 717 | 101.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | T:61&191 | 620 | 717 | 101.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:PA27&BP76 | 620 | 717 | 101.57
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - INDEPNC 26 345 | T:61&191 | 620 | 717 | 101.44
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 5 MILE - STOLLE 37A 345 | T:61&64 | 620 | 717 | 101.36
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HOMERCTY - STOLLRD 37 345 | T:61&64 | 620 | 717 | 101.36
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - 5MILE 345 | T:61&64 | 620 | 717 | 101.35
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:5M-SR_37&W-F_171 | T:61&64 | 620 | 717 | 101.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 101.21
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE 230/115 3TR | T:61&64 | 620 | 717 | 101.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | BECK - PACKARD BP76 230 | 620 | 717 | 101.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 101
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - INDEPNC 26 345 | T:61&64 | 620 | 717 | 101
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 4TR | T:61&64 | 620 | 717 | 100.91
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - SHLDON 67 230 | T:61&64 | 620 | 717 | 100.86
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:HOORKN85 | T:61&64 | 620 | 717 | 100.84
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | T:61&64 | 620 | 717 | 100.79
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:HOORKN86 | T:61&64 | 620 | 717 | 100.78
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 13 345 | T:61&64 | 620 | 717 | 100.63
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 1TR | T:61&64 | 620 | 717 | 100.33
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DEWITT3 - LAFAYTTE 345 | T:61&64 | 620 | 717 | 100.31
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 7 | T:61&64 | 620 | 717 | 100.3
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 4 | T:61&64 | 620 | 717 | 100.28
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 5 | T:61&64 | 620 | 717 | 100.28
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 6 | T:61&64 | 620 | 717 | 100.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - 9MI1 8 345 | T:61&191 | 620 | 717 | 100.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-FV_37&W-F_171 | T:61&191 | 620 | 717 | 100.21
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LOCKPORT | T:61&64 | 620 | 717 | 100.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - GARDENVILL 79 230 | T:61&64 | 620 | 717 | 100.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OS - EL - LFYTE 17 345 | T:61&191 | 620 | 717 | 100.15
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MAINSBRG 345/115 1TR | T:61&64 | 620 | 717 | 100.1
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL 230/115 M7TR | T:61&64 | 620 | 717 | 100.06
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 2TR | T:61&64 | 620 | 717 | 100.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - GARDENVILL 80 230 | T:61&64 | 620 | 717 | 100.05
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL 230/115 2TR | T:61&64 | 620 | 717 | 100.05
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 5TR | T:61&64 | 620 | 717 | 100.05
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK PA27 230 | T:61&64 | 620 | 717 | 100.01
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:STL1_G1 | T:61&64 | 620 | 717 | 100.01
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:STL1_G2 | T:61&64 | 620 | 717 | 100.01
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 3TR | T:61&64 | 620 | 717 | 100
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 5TR | T:61&64 | 620 | 717 | 100
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROBI230 | 620 | 717 | 100
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 Max |  |  |  |  | 117.77
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | NIAGARA 230/115 2TR | 168 | 206 | 100.05
| 135497 ZRMN-133 115 135562 S214-133 115 1 Max |  |  |  |  | 100.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 192 | 239 | 120.97 | 100.3883
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 192 | 239 | 116.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | T:62&BP76 | 192 | 239 | 109.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 192 | 239 | 103.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 192 | 239 | 103.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 192 | 239 | 103.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:61&64 | 192 | 239 | 102.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:77&78 | 192 | 239 | 100.71
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 Max |  |  |  |  | 120.97
| Grand Max |  |  |  |  | 122.56

## N-1-1_ETC_OH_1000_Adjust
SERIES REACTORS ON 77 AND 78 LINES BY-PASSED
Niagara Dispatch | Monitored Facility | First Contingency | Second Contingency |  | Rate Base (MVA) | Rate Cont (MVA) | SCD AC %Loading
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | Base Case | 135304 SAWYER78 230 135415 PACKARD2 230 2 HUNTLEY - PACKARD 77 230 | 556 | 746 | 109.89
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | Base Case | 135304 SAWYER78 230 135415 PACKARD2 230 2 HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.75
| 135304 SAWYER78 230 135415 PACKARD2 230 2 Max |  |  | 135304 SAWYER78 230 135415 PACKARD2 230 2 Max |  |  | 109.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | Base Case | 135303 SAWYER77 230 135415 PACKARD2 230 1 HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 STOLLRD - GARDENVILL 66 230 | 556 | 704 | 105.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 STOLLRD - GARDENVILL 66 230 | 556 | 704 | 105.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 HUNTLEY - PACKARD 78 230 | 556 | 704 | 105.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 STOLLRD - GARDENVILL 66 230 | 556 | 704 | 105.33
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 HUNTLEY - PACKARD 78 230 | 556 | 704 | 104.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | Base Case | 135303 SAWYER77 230 135415 PACKARD2 230 1 HUNTLEY - PACKARD 78 230 | 556 | 704 | 103.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:9 MI PT2 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:9 MI PT2 | 556 | 704 | 102.77
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:9 MI PT2 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:9 MI PT2 | 556 | 704 | 102.77
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:9 MI PT2 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:9 MI PT2 | 556 | 704 | 102.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 NIAGARA - ROBINSON 64 230 | 556 | 704 | 101.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 STOLLRD - GARDENVILL 66 230 | 556 | 704 | 100.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 ROBINSON - STOLLRD 65 230 | 556 | 704 | 100.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:KINTIGH | 556 | 704 | 100.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:FITZPATR | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 G:FITZPATR | 556 | 704 | 100.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:9MIPT1 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 G:9MIPT1 | 556 | 704 | 100.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 CANDQUA - STNYRDG 68A 230 | 556 | 704 | 100.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 CANDQUA - STNYRDG 68A 230 | 556 | 704 | 100.39
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 ROBINSON - STOLLRD 65 230 | 556 | 704 | 100.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:OSWEGO 5 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:OSWEGO 5 | 556 | 704 | 100.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:KINTIGH | 556 | 704 | 100.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:9 MI PT2 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:9 MI PT2 | 556 | 704 | 100.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:OSWEGO 6 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:OSWEGO 6 | 556 | 704 | 100.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 G:GINNA | 556 | 704 | 100.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 NIAGARA - ROBINSON 64 230 | 556 | 704 | 100.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - VOLNEY 6 345 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 CLAY - VOLNEY 6 345 | 556 | 704 | 100.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - INDEPNC 26 345 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 CLAY - INDEPNC 26 345 | 556 | 704 | 100.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 ROBINSON - STOLLRD 65 230 | 556 | 704 | 100.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 STOLLRD - GARDENVILL 66 230 | 556 | 704 | 100.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 SOMERSET - NEWROCH 1 345 | 556 | 704 | 100.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 CANDQUA - STNYRDG 68A 230 | 556 | 704 | 100.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 HUNTLEY - PACKARD 78 230 | 556 | 704 | 100.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 G:GINNA | 556 | 704 | 100.12
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:FITZPATR | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 G:FITZPATR | 556 | 704 | 100.12
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:9MIPT1 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 G:9MIPT1 | 556 | 704 | 100.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 CANDQUA - STNYRDG 68A 230 | 556 | 704 | 100.11
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 WTHRS - MEYER 230 | 556 | 704 | 100.11
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:OSWEGO 5 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:OSWEGO 5 | 556 | 704 | 100.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 SOMERSET - NEWROCH 1 345 | 556 | 704 | 100.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:KINTIGH | 556 | 704 | 100.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:OSWEGO 6 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:OSWEGO 6 | 556 | 704 | 100.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 R:HCWC/NWES | 556 | 704 | 100.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 R:MBWC/NWES | 556 | 704 | 100.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 NIAGARA - ROBINSON 64 230 | 556 | 704 | 100.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 STONYCR - WTHRS 230 | 556 | 704 | 100.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:9 MI PT2 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:9 MI PT2 | 556 | 704 | 100.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:OSWEGO 6 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:OSWEGO 6 | 556 | 704 | 100.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 WTRCR - MAINSBRG 30A 345 | 556 | 704 | 100.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 MAINSBRG - HOMERCITY 30B 345 | 556 | 704 | 100.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 OAKDL - FRASER 32 345 | 556 | 704 | 100.03
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 R:HC-WC_30&W-F_171 | 556 | 704 | 100.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 WTHRS - MEYER 230 | 556 | 704 | 100.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 R:HCMB/NWES | 556 | 704 | 100.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 MAINSBRG - HOMERCITY 30B 345 | 556 | 704 | 100.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 R:HC-MB_30&W-F_171 | 556 | 704 | 100.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 R:HCMB/NWES | 556 | 704 | 100.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 ERIE E - 4 MILE 230 | 556 | 704 | 100.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE 230/115 4TR | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 HILLSIDE 230/115 4TR | 556 | 704 | 100.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 GEN:KINTIGH | 556 | 704 | 100.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | VOL - MARCY 19 345 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 VOL - MARCY 19 345 | 556 | 704 | 100.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - FITZ 345 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 EDIC - FITZ 345 | 556 | 704 | 100.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 OAKDLE - WTRCR 31 345 | 556 | 704 | 100.01
| 135303 SAWYER77 230 135415 PACKARD2 230 1 Max |  |  | 135303 SAWYER77 230 135415 PACKARD2 230 1 Max |  |  | 109.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 130762 GARDV230 230 130767 STOLE230 230 1 HUNTLEY - PACKARD 77 230 | 474 | 478 | 108.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 130762 GARDV230 230 130767 STOLE230 230 1 HUNTLEY - PACKARD 78 230 | 474 | 478 | 105.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 130762 GARDV230 230 130767 STOLE230 230 1 HUNTLEY - PACKARD 77 230 | 474 | 478 | 104.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 130762 GARDV230 230 130767 STOLE230 230 1 HUNTLEY - PACKARD 78 230 | 474 | 478 | 104.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 130762 GARDV230 230 130767 STOLE230 230 1 HUNTLEY - PACKARD 77 230 | 474 | 478 | 104.43
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 130762 GARDV230 230 130767 STOLE230 230 1 HUNTLEY - PACKARD 78 230 | 474 | 478 | 104.41
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 130762 GARDV230 230 130767 STOLE230 230 1 HUNTLEY - PACKARD 77 230 | 474 | 478 | 103.19
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 130762 GARDV230 230 130767 STOLE230 230 1 HUNTLEY - PACKARD 77 230 | 474 | 478 | 100.61
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 130762 GARDV230 230 130767 STOLE230 230 1 HUNTLEY - PACKARD 78 230 | 474 | 478 | 100.51
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 130762 GARDV230 230 130767 STOLE230 230 1 HUNTLEY - PACKARD 78 230 | 474 | 478 | 100.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 130762 GARDV230 230 130767 STOLE230 230 1 HUNTLEY - PACKARD 77 230 | 474 | 478 | 100.36
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 130762 GARDV230 230 130767 STOLE230 230 1 HUNTLEY - PACKARD 78 230 | 474 | 478 | 100.24
| 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  | 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  | 108.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | Base Case | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 NIAGARA - PACKARD 62 230 | 620 | 841 | 108.24
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 Max |  |  | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 Max |  |  | 108.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | Base Case | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 NIAGARA - PACKARD 61 230 | 620 | 841 | 107.77
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 Max |  |  | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 Max |  |  | 107.77
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | B:PACKT4 | 135497 ZRMN-133 115 135562 S214-133 115 1 NIAGARA 230/115 2TR | 168 | 206 | 100.71
| 135497 ZRMN-133 115 135562 S214-133 115 1 Max |  |  | 135497 ZRMN-133 115 135562 S214-133 115 1 Max |  |  | 100.71
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | Base Case | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 HUNTLEY - GARDENVILL 79 230 | 566 | 755 | 100.04
| 135305 SAWYER80 230 135414 HUNTLEY2 230 1 Max |  |  | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 Max |  |  | 100.04
| Grand Max |  |  | Grand Max |  |  | 109.89

## N-1_NTC_OH_1000
SERIES REACTORS ON 77 AND 78 LINES BY-PASSED
Niagara Dispatch | Monitored Facility | Cont Name |  | Rate Base (MVA) | Rate Cont (MVA) | Final AC %Loading
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | T:77&78 | 130762 GARDV230 230 130767 STOLE230 230 1 T:77&78 | 474 | 478 | 115.12
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DCT:230:77+78 | 130762 GARDV230 230 130767 STOLE230 230 1 DCT:230:77+78 | 474 | 478 | 115.1
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DCT:230:77+78+THR | 130762 GARDV230 230 130767 STOLE230 230 1 DCT:230:77+78+THR | 474 | 478 | 114.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | T:77&78 | 130762 GARDV230 230 130767 STOLE230 230 1 T:77&78 | 474 | 478 | 111.61
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DCT:230:77+78 | 130762 GARDV230 230 130767 STOLE230 230 1 DCT:230:77+78 | 474 | 478 | 111.6
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DCT:230:77+78+THR | 130762 GARDV230 230 130767 STOLE230 230 1 DCT:230:77+78+THR | 474 | 478 | 110.61
| 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  |  |  | 115.12
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | DCT:230:77+78+THR | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 DCT:230:77+78+THR | 496 | 550 | 109.92
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | T:77&78 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 T:77&78 | 496 | 550 | 109.42
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | DCT:230:77+78 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 DCT:230:77+78 | 496 | 550 | 109.41
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | DCT:230:77+78+THR | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 DCT:230:77+78+THR | 496 | 550 | 102.08
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | T:77&78 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 T:77&78 | 496 | 550 | 101.77
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | DCT:230:77+78 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 DCT:230:77+78 | 496 | 550 | 101.76
| 130766 ROBIN230 230 147841 NIAGAR2E 230 1 Max |  |  |  |  | 109.92
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SB:PK115 30+40 | 130795 DEPEW115 115 130799 ERIE 115 115 1 SB:PK115 30+40 | 119 | 119 | 111.48
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SB:PK115 30+40 | 130795 DEPEW115 115 130799 ERIE 115 115 1 SB:PK115 30+40 | 119 | 119 | 111.08
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SB:GVNY115 6+7 | 130795 DEPEW115 115 130799 ERIE 115 115 1 SB:GVNY115 6+7 | 119 | 119 | 100.29
| 130795 DEPEW115 115 130799 ERIE 115 115 1 Max |  |  |  |  | 111.48
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | DCT:230:77+78 | 130834 N.BRW115 115 135437 CLSP-181 115 1 DCT:230:77+78 | 139 | 163 | 106.68
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | T:77&78 | 130834 N.BRW115 115 135437 CLSP-181 115 1 T:77&78 | 139 | 163 | 106.68
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | DCT:230:77+78+THR | 130834 N.BRW115 115 135437 CLSP-181 115 1 DCT:230:77+78+THR | 139 | 163 | 106.19
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | DCT:230:77+78 | 130834 N.BRW115 115 135437 CLSP-181 115 1 DCT:230:77+78 | 139 | 163 | 101.74
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | T:77&78 | 130834 N.BRW115 115 135437 CLSP-181 115 1 T:77&78 | 139 | 163 | 101.74
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | DCT:230:77+78+THR | 130834 N.BRW115 115 135437 CLSP-181 115 1 DCT:230:77+78+THR | 139 | 163 | 101.23
| 130834 N.BRW115 115 135437 CLSP-181 115 1 Max |  |  |  |  | 106.68
Dispatch 1 | 130847 ROLL 115 115 130857 STOLE115 115 1 | SB:181:ER | 130847 ROLL 115 115 130857 STOLE115 115 1 SB:181:ER | 90 | 90 | 101.58
Dispatch 2 | 130847 ROLL 115 115 130857 STOLE115 115 1 | SB:181:ER | 130847 ROLL 115 115 130857 STOLE115 115 1 SB:181:ER | 90 | 90 | 101.55
| 130847 ROLL 115 115 130857 STOLE115 115 1 Max |  |  |  |  | 101.58
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | BUS:230:PK-2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 BUS:230:PK-2 | 566 | 654 | 116.75
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | B:PACKT3 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 B:PACKT3 | 566 | 654 | 116.75
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SB:78PK+THR | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 SB:78PK+THR | 566 | 654 | 116.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NF:230:78 PK | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 NF:230:78 PK | 566 | 654 | 115.78
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OE:PACK_78 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 OE:PACK_78 | 566 | 654 | 115.78
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 HUNTLEY - PACKARD 78 230 | 566 | 654 | 115.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LN:230:78 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 LN:230:78 | 566 | 654 | 115.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LN:230:78 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 LN:230:78 | 566 | 654 | 115.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SB:PK230 BS2+3 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 SB:PK230 BS2+3 | 566 | 654 | 113.48
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SB:PA230_R304 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 SB:PA230_R304 | 566 | 654 | 113.47
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SB:78PK | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 SB:78PK | 566 | 654 | 112.48
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SB:PA230_R3230 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 SB:PA230_R3230 | 566 | 654 | 112.48
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | S:PA_HNTL78 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 S:PA_HNTL78 | 566 | 654 | 111.49
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | BUS:230:PK-2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 BUS:230:PK-2 | 566 | 654 | 110.03
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | B:PACKT3 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 B:PACKT3 | 566 | 654 | 110.03
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NF:230:78 PK | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 NF:230:78 PK | 566 | 654 | 109.94
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OE:PACK_78 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 OE:PACK_78 | 566 | 654 | 109.94
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SB:78PK+THR | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 SB:78PK+THR | 566 | 654 | 109.88
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 HUNTLEY - PACKARD 78 230 | 566 | 654 | 109.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LN:230:78 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 LN:230:78 | 566 | 654 | 109.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LN:230:78 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 LN:230:78 | 566 | 654 | 109.79
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NF:230:78 HUN | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 NF:230:78 HUN | 566 | 654 | 108.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OE:HNTLEY_78 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 OE:HNTLEY_78 | 566 | 654 | 108.29
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SB:PK230 BS2+3 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 SB:PK230 BS2+3 | 566 | 654 | 106.91
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SB:PA230_R304 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 SB:PA230_R304 | 566 | 654 | 106.91
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SB:78PK | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 SB:78PK | 566 | 654 | 105.75
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SB:PA230_R3230 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 SB:PA230_R3230 | 566 | 654 | 105.75
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | S:PA_HNTL78 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 S:PA_HNTL78 | 566 | 654 | 105.65
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NF:230:78 HUN | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 NF:230:78 HUN | 566 | 654 | 102.49
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OE:HNTLEY_78 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 OE:HNTLEY_78 | 566 | 654 | 102.49
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 116.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:78PK | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:78PK | 556 | 644 | 128.37
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:PA230_R3230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:PA230_R3230 | 556 | 644 | 128.37
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BUS:230:PK-2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 BUS:230:PK-2 | 556 | 644 | 128.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 B:PACKT3 | 556 | 644 | 128.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:78PK+THR | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:78PK+THR | 556 | 644 | 128.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 S:PA_HNTL78 | 556 | 644 | 127.39
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NF:230:78 PK | 135303 SAWYER77 230 135415 PACKARD2 230 1 NF:230:78 PK | 556 | 644 | 127.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OE:PACK_78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 OE:PACK_78 | 556 | 644 | 127.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 HUNTLEY - PACKARD 78 230 | 556 | 644 | 127.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LN:230:78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 LN:230:78 | 556 | 644 | 127.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LN:230:78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 LN:230:78 | 556 | 644 | 127.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:PK230 BS2+3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:PK230 BS2+3 | 556 | 644 | 124.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:PA230_R304 | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:PA230_R304 | 556 | 644 | 124.83
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:78PK | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:78PK | 556 | 644 | 121.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:PA230_R3230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:PA230_R3230 | 556 | 644 | 121.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | S:PA_HNTL78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 S:PA_HNTL78 | 556 | 644 | 121.46
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BUS:230:PK-2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 BUS:230:PK-2 | 556 | 644 | 121.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | B:PACKT3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 B:PACKT3 | 556 | 644 | 121.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:78PK+THR | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:78PK+THR | 556 | 644 | 121.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NF:230:78 PK | 135303 SAWYER77 230 135415 PACKARD2 230 1 NF:230:78 PK | 556 | 644 | 121.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OE:PACK_78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 OE:PACK_78 | 556 | 644 | 121.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | 135303 SAWYER77 230 135415 PACKARD2 230 1 HUNTLEY - PACKARD 78 230 | 556 | 644 | 121.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LN:230:78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 LN:230:78 | 556 | 644 | 121.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LN:230:78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 LN:230:78 | 556 | 644 | 121.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:PK230 BS2+3 | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:PK230 BS2+3 | 556 | 644 | 118.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:PA230_R304 | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:PA230_R304 | 556 | 644 | 118.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NF:230:78 HUN | 135303 SAWYER77 230 135415 PACKARD2 230 1 NF:230:78 HUN | 556 | 644 | 116.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OE:HNTLEY_78 | 135303 SAWYER77 230 135415 PACKARD2 230 1 OE:HNTLEY_78 | 556 | 644 | 116.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:78HUN | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:78HUN | 556 | 644 | 111.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:HUNT230_R1502 | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:HUNT230_R1502 | 556 | 644 | 111.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DCT:230:78+79 | 135303 SAWYER77 230 135415 PACKARD2 230 1 DCT:230:78+79 | 556 | 644 | 111.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | T:78&79 | 135303 SAWYER77 230 135415 PACKARD2 230 1 T:78&79 | 556 | 644 | 111.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NF:230:78 HUN | 135303 SAWYER77 230 135415 PACKARD2 230 1 NF:230:78 HUN | 556 | 644 | 110.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OE:HNTLEY_78 | Any combination resulting in the loss of two out of three Sawyer transformers under N-1 (Towers 77&78, 77&80) or N-1-1 (any combination of the 77, 79, 80 lines) | 556 | 644 | 110.99
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:78HUN+THR | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:78HUN+THR | 556 | 644 | 109.96
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:78HUN | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:78HUN | 556 | 644 | 106.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:HUNT230_R1502 | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:HUNT230_R1502 | 556 | 644 | 106.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DCT:230:78+79 | 135303 SAWYER77 230 135415 PACKARD2 230 1 DCT:230:78+79 | 556 | 644 | 106.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | T:78&79 | 135303 SAWYER77 230 135415 PACKARD2 230 1 T:78&79 | 556 | 644 | 106.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:78HUN+THR | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:78HUN+THR | 556 | 644 | 105
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BUS:230:HUN-68 | 135303 SAWYER77 230 135415 PACKARD2 230 1 BUS:230:HUN-68 | 556 | 644 | 100.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | B:Hunt68 | 135303 SAWYER77 230 135415 PACKARD2 230 1 B:Hunt68 | 556 | 644 | 100.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:79HUN | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:79HUN | 556 | 644 | 100.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SB:HUNT230_R1402 | 135303 SAWYER77 230 135415 PACKARD2 230 1 SB:HUNT230_R1402 | 556 | 644 | 100.04
| 135303 SAWYER77 230 135415 PACKARD2 230 1 Max |  |  |  |  | 128.37
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NF:230:77 PK | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 NF:230:77 PK | 566 | 654 | 115.78
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OE:PACK_77 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 OE:PACK_77 | 566 | 654 | 115.78
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 HUNTLEY - PACKARD 77 230 | 566 | 654 | 115.63
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:230:77 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 LN:230:77 | 566 | 654 | 115.63
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:230:77 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 LN:230:77 | 566 | 654 | 115.63
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | BUS:230:PK-4 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 BUS:230:PK-4 | 566 | 654 | 113.28
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | B:PACKT4 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 B:PACKT4 | 566 | 654 | 113.28
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SB:77PK+THR | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 SB:77PK+THR | 566 | 654 | 113.04
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | S:PA_HNTL77 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 S:PA_HNTL77 | 566 | 654 | 111.57
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SB:PK230 BS3+4 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 SB:PK230 BS3+4 | 566 | 654 | 110
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SB:PA230_R506 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 SB:PA230_R506 | 566 | 654 | 110
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NF:230:77 PK | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 NF:230:77 PK | 566 | 654 | 109.94
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OE:PACK_77 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 OE:PACK_77 | 566 | 654 | 109.94
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:230:77 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 LN:230:77 | 566 | 654 | 109.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 HUNTLEY - PACKARD 77 230 | 566 | 654 | 109.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:230:77 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 LN:230:77 | 566 | 654 | 109.79
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SB:PA230_R3430 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 SB:PA230_R3430 | 566 | 654 | 109.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SB:77PK | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 SB:77PK | 566 | 654 | 108.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NF:230:77 HUN | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 NF:230:77 HUN | 566 | 654 | 108.43
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OE:HNTLEY_77 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 OE:HNTLEY_77 | 566 | 654 | 108.43
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | BUS:230:PK-4 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 BUS:230:PK-4 | 566 | 654 | 106.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | B:PACKT4 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 B:PACKT4 | 566 | 654 | 106.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SB:77PK+THR | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 SB:77PK+THR | 566 | 654 | 106.56
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | S:PA_HNTL77 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 S:PA_HNTL77 | 566 | 654 | 105.72
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SB:PK230 BS3+4 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 SB:PK230 BS3+4 | 566 | 654 | 103.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SB:PA230_R506 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 SB:PA230_R506 | 566 | 654 | 103.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NF:230:77 HUN | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 NF:230:77 HUN | 566 | 654 | 102.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OE:HNTLEY_77 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 OE:HNTLEY_77 | 566 | 654 | 102.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SB:PA230_R3430 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 SB:PA230_R3430 | 566 | 654 | 102.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SB:77PK | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 SB:77PK | 566 | 654 | 102.5
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 Max |  |  |  |  | 115.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | S:PA_HNTL77 | 135304 SAWYER78 230 135415 PACKARD2 230 2 S:PA_HNTL77 | 556 | 644 | 127.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NF:230:77 PK | 135304 SAWYER78 230 135415 PACKARD2 230 2 NF:230:77 PK | 556 | 644 | 127.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OE:PACK_77 | 135304 SAWYER78 230 135415 PACKARD2 230 2 OE:PACK_77 | 556 | 644 | 127.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LN:230:77 | 135304 SAWYER78 230 135415 PACKARD2 230 2 LN:230:77 | 556 | 644 | 127.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | 135304 SAWYER78 230 135415 PACKARD2 230 2 HUNTLEY - PACKARD 77 230 | 556 | 644 | 127.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LN:230:77 | 135304 SAWYER78 230 135415 PACKARD2 230 2 LN:230:77 | 556 | 644 | 127.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:PA230_R3430 | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:PA230_R3430 | 556 | 644 | 125.08
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:77PK | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:77PK | 556 | 644 | 124.98
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BUS:230:PK-4 | 135304 SAWYER78 230 135415 PACKARD2 230 2 BUS:230:PK-4 | 556 | 644 | 124.89
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | B:PACKT4 | 135304 SAWYER78 230 135415 PACKARD2 230 2 B:PACKT4 | 556 | 644 | 124.89
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:77PK+THR | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:77PK+THR | 556 | 644 | 124.71
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | S:PA_HNTL77 | 135304 SAWYER78 230 135415 PACKARD2 230 2 S:PA_HNTL77 | 556 | 644 | 121.7
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:PK230 BS3+4 | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:PK230 BS3+4 | 556 | 644 | 121.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:PA230_R506 | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:PA230_R506 | 556 | 644 | 121.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NF:230:77 PK | 135304 SAWYER78 230 135415 PACKARD2 230 2 NF:230:77 PK | 556 | 644 | 121.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OE:PACK_77 | 135304 SAWYER78 230 135415 PACKARD2 230 2 OE:PACK_77 | 556 | 644 | 121.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LN:230:77 | 135304 SAWYER78 230 135415 PACKARD2 230 2 LN:230:77 | 556 | 644 | 121.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | 135304 SAWYER78 230 135415 PACKARD2 230 2 HUNTLEY - PACKARD 77 230 | 556 | 644 | 121.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LN:230:77 | 135304 SAWYER78 230 135415 PACKARD2 230 2 LN:230:77 | 556 | 644 | 121.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:PA230_R3430 | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:PA230_R3430 | 556 | 644 | 118.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:77PK | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:77PK | 556 | 644 | 118.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BUS:230:PK-4 | 135304 SAWYER78 230 135415 PACKARD2 230 2 BUS:230:PK-4 | 556 | 644 | 118.27
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | B:PACKT4 | 135304 SAWYER78 230 135415 PACKARD2 230 2 B:PACKT4 | 556 | 644 | 118.27
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:77PK+THR | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:77PK+THR | 556 | 644 | 118.11
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NF:230:77 HUN | 135304 SAWYER78 230 135415 PACKARD2 230 2 NF:230:77 HUN | 556 | 644 | 117.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OE:HNTLEY_77 | 135304 SAWYER78 230 135415 PACKARD2 230 2 OE:HNTLEY_77 | 556 | 644 | 117.13
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:PK230 BS3+4 | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:PK230 BS3+4 | 556 | 644 | 115.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:PA230_R506 | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:PA230_R506 | 556 | 644 | 115.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | T:77&80 | 135304 SAWYER78 230 135415 PACKARD2 230 2 T:77&80 | 556 | 644 | 113.9
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DCT:230:77+80 | 135304 SAWYER78 230 135415 PACKARD2 230 2 DCT:230:77+80 | 556 | 644 | 113.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NF:230:77 HUN | 135304 SAWYER78 230 135415 PACKARD2 230 2 NF:230:77 HUN | 556 | 644 | 111.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OE:HNTLEY_77 | 135304 SAWYER78 230 135415 PACKARD2 230 2 OE:HNTLEY_77 | 556 | 644 | 111.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DCT:230:77+80+THR | 135304 SAWYER78 230 135415 PACKARD2 230 2 DCT:230:77+80+THR | 556 | 644 | 111.23
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:77HUN+THR | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:77HUN+THR | 556 | 644 | 110.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | T:77&80 | 135304 SAWYER78 230 135415 PACKARD2 230 2 T:77&80 | 556 | 644 | 109.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DCT:230:77+80 | 135304 SAWYER78 230 135415 PACKARD2 230 2 DCT:230:77+80 | 556 | 644 | 109.29
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:77HUN | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:77HUN | 556 | 644 | 108.59
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:HUNT230_R1302 | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:HUNT230_R1302 | 556 | 644 | 108.59
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DCT:230:77+80+THR | 135304 SAWYER78 230 135415 PACKARD2 230 2 DCT:230:77+80+THR | 556 | 644 | 106.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:77HUN+THR | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:77HUN+THR | 556 | 644 | 105.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:77HUN | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:77HUN | 556 | 644 | 103.76
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:HUNT230_R1302 | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:HUNT230_R1302 | 556 | 644 | 103.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SB:80HUN+THR | 135304 SAWYER78 230 135415 PACKARD2 230 2 SB:80HUN+THR | 556 | 644 | 100.88
| 135304 SAWYER78 230 135415 PACKARD2 230 2 Max |  |  |  |  | 127.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DCT:230:62+76 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 DCT:230:62+76 | 620 | 717 | 139.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | T:62&BP76 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 T:62&BP76 | 620 | 717 | 139.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SB:PA230_R506 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 SB:PA230_R506 | 620 | 717 | 124.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SB:PK230 BS3+4 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 SB:PK230 BS3+4 | 620 | 717 | 124.29
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DCT:230:62+76 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 DCT:230:62+76 | 620 | 717 | 121.06
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | T:62&BP76 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 T:62&BP76 | 620 | 717 | 121.06
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SB:PK230 BS3+4 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 SB:PK230 BS3+4 | 620 | 717 | 111.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SB:PA230_R506 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 SB:PA230_R506 | 620 | 717 | 111.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 NIAGARA - PACKARD 62 230 | 620 | 717 | 109.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:230:62 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 LN:230:62 | 620 | 717 | 109.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:230:62 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 LN:230:62 | 620 | 717 | 109.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DCT:230:27+62 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 DCT:230:27+62 | 620 | 717 | 105.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | T:62&PA27 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 T:62&PA27 | 620 | 717 | 105.85
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 Max |  |  |  |  | 139.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DCT:230:61+64 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 DCT:230:61+64 | 620 | 717 | 130.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | T:61&64 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&64 | 620 | 717 | 130.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SB:PK230 BS2+3 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 SB:PK230 BS2+3 | 620 | 717 | 115.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SB:PA230_R304 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 SB:PA230_R304 | 620 | 717 | 115.15
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DCT:230:61+64 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 DCT:230:61+64 | 620 | 717 | 112.01
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | T:61&64 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&64 | 620 | 717 | 112.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DCT:230:61+191 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 DCT:230:61+191 | 620 | 717 | 111.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | T:61&191 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 T:61&191 | 620 | 717 | 111.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 NIAGARA - PACKARD 61 230 | 620 | 717 | 109
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:230:61 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 LN:230:61 | 620 | 717 | 109
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:230:61 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 LN:230:61 | 620 | 717 | 109
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SB:PK230 BS2+3 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 SB:PK230 BS2+3 | 620 | 717 | 101.64
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SB:PA230_R304 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 SB:PA230_R304 | 620 | 717 | 101.64
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 Max |  |  |  |  | 130.75
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | T:77&78 | 135433 AMHST-38 115 135472 S129-38 115 1 T:77&78 | 145 | 151 | 100.88
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | DCT:230:77+78 | 135433 AMHST-38 115 135472 S129-38 115 1 DCT:230:77+78 | 145 | 151 | 100.87
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | DCT:230:77+78+THR | 135433 AMHST-38 115 135472 S129-38 115 1 DCT:230:77+78+THR | 145 | 151 | 100.62
| 135433 AMHST-38 115 135472 S129-38 115 1 Max |  |  |  |  | 100.88
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | T:77&78 | 135434 AMHST-39 115 135473 S129-39 115 1 T:77&78 | 145 | 151 | 100.13
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | DCT:230:77+78 | 135434 AMHST-39 115 135473 S129-39 115 1 DCT:230:77+78 | 145 | 151 | 100.12
| 135434 AMHST-39 115 135473 S129-39 115 1 Max |  |  |  |  | 100.13
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | T:77&78 | 135434 AMHST-39 115 135478 S140-39 115 1 T:77&78 | 145 | 151 | 100.13
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | DCT:230:77+78 | 135434 AMHST-39 115 135478 S140-39 115 1 DCT:230:77+78 | 145 | 151 | 100.12
| 135434 AMHST-39 115 135478 S140-39 115 1 Max |  |  |  |  | 100.13
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | DCT:230:77+78 | 135437 CLSP-181 115 135495 YNG-181 115 1 DCT:230:77+78 | 139 | 163 | 107.63
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | T:77&78 | 135437 CLSP-181 115 135495 YNG-181 115 1 T:77&78 | 139 | 163 | 107.63
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | DCT:230:77+78+THR | 135437 CLSP-181 115 135495 YNG-181 115 1 DCT:230:77+78+THR | 139 | 163 | 107.1
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | DCT:230:77+78 | 135437 CLSP-181 115 135495 YNG-181 115 1 DCT:230:77+78 | 139 | 163 | 102.69
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | T:77&78 | 135437 CLSP-181 115 135495 YNG-181 115 1 T:77&78 | 139 | 163 | 102.69
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | DCT:230:77+78+THR | 135437 CLSP-181 115 135495 YNG-181 115 1 DCT:230:77+78+THR | 139 | 163 | 102.14
| 135437 CLSP-181 115 135495 YNG-181 115 1 Max |  |  |  |  | 107.63
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | DCT:230:77+78 | 135441 FMC-39 115 135473 S129-39 115 1 DCT:230:77+78 | 145 | 151 | 102.67
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | T:77&78 | 135441 FMC-39 115 135473 S129-39 115 1 T:77&78 | 145 | 151 | 102.67
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | DCT:230:77+78+THR | 135441 FMC-39 115 135473 S129-39 115 1 DCT:230:77+78+THR | 145 | 151 | 102.33
| 135441 FMC-39 115 135473 S129-39 115 1 Max |  |  |  |  | 102.67
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | DCT:230:77+78 | 135442 ECWA-181 115 135458 NI.B-181 115 1 DCT:230:77+78 | 174 | 181 | 111.88
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | T:77&78 | 135442 ECWA-181 115 135458 NI.B-181 115 1 T:77&78 | 174 | 181 | 111.88
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | DCT:230:77+78+THR | 135442 ECWA-181 115 135458 NI.B-181 115 1 DCT:230:77+78+THR | 174 | 181 | 111.06
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | DCT:230:77+78 | 135442 ECWA-181 115 135458 NI.B-181 115 1 DCT:230:77+78 | 174 | 181 | 107.11
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | T:77&78 | 135442 ECWA-181 115 135458 NI.B-181 115 1 T:77&78 | 174 | 181 | 107.11
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | DCT:230:77+78+THR | 135442 ECWA-181 115 135458 NI.B-181 115 1 DCT:230:77+78+THR | 174 | 181 | 106.28
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | DCT:230:79+80+THR+ELM3-4 | 135442 ECWA-181 115 135458 NI.B-181 115 1 DCT:230:79+80+THR+ELM3-4 | 174 | 181 | 101.98
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | DCT:230:79+80+ELM3-4 | 135442 ECWA-181 115 135458 NI.B-181 115 1 DCT:230:79+80+ELM3-4 | 174 | 181 | 101.98
| 135442 ECWA-181 115 135458 NI.B-181 115 1 Max |  |  |  |  | 111.88
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | T:77&78 | 135442 ECWA-181 115 135495 YNG-181 115 1 T:77&78 | 174 | 181 | 111.28
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | DCT:230:77+78 | 135442 ECWA-181 115 135495 YNG-181 115 1 DCT:230:77+78 | 174 | 181 | 111.27
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | DCT:230:77+78+THR | 135442 ECWA-181 115 135495 YNG-181 115 1 DCT:230:77+78+THR | 174 | 181 | 110.44
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | T:77&78 | 135442 ECWA-181 115 135495 YNG-181 115 1 T:77&78 | 174 | 181 | 106.55
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | DCT:230:77+78 | 135442 ECWA-181 115 135495 YNG-181 115 1 DCT:230:77+78 | 174 | 181 | 106.54
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | DCT:230:77+78+THR | 135442 ECWA-181 115 135495 YNG-181 115 1 DCT:230:77+78+THR | 174 | 181 | 105.7
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | DCT:230:79+80+THR+ELM3-4 | 135442 ECWA-181 115 135495 YNG-181 115 1 DCT:230:79+80+THR+ELM3-4 | 174 | 181 | 101.46
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | DCT:230:79+80+ELM3-4 | 135442 ECWA-181 115 135495 YNG-181 115 1 DCT:230:79+80+ELM3-4 | 174 | 181 | 101.46
| 135442 ECWA-181 115 135495 YNG-181 115 1 Max |  |  |  |  | 111.28
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | DCT:230:77+78+THR | 135443 ECWA-182 115 135459 NI.B-182 115 1 DCT:230:77+78+THR | 174 | 181 | 106.01
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | T:77&78 | 135443 ECWA-182 115 135459 NI.B-182 115 1 T:77&78 | 174 | 181 | 105.6
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | DCT:230:77+78 | 135443 ECWA-182 115 135459 NI.B-182 115 1 DCT:230:77+78 | 174 | 181 | 105.59
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | DCT:230:77+78+THR | 135443 ECWA-182 115 135459 NI.B-182 115 1 DCT:230:77+78+THR | 174 | 181 | 100.6
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | T:77&78 | 135443 ECWA-182 115 135459 NI.B-182 115 1 T:77&78 | 174 | 181 | 100.25
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | DCT:230:77+78 | 135443 ECWA-182 115 135459 NI.B-182 115 1 DCT:230:77+78 | 174 | 181 | 100.24
| 135443 ECWA-182 115 135459 NI.B-182 115 1 Max |  |  |  |  | 106.01
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | DCT:230:77+78+THR | 135443 ECWA-182 115 135496 YNG-182 115 1 DCT:230:77+78+THR | 174 | 181 | 106.04
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | T:77&78 | 135443 ECWA-182 115 135496 YNG-182 115 1 T:77&78 | 174 | 181 | 105.57
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | DCT:230:77+78 | 135443 ECWA-182 115 135496 YNG-182 115 1 DCT:230:77+78 | 174 | 181 | 105.56
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | DCT:230:77+78+THR | 135443 ECWA-182 115 135496 YNG-182 115 1 DCT:230:77+78+THR | 174 | 181 | 100.6
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | T:77&78 | 135443 ECWA-182 115 135496 YNG-182 115 1 T:77&78 | 174 | 181 | 100.18
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | DCT:230:77+78 | 135443 ECWA-182 115 135496 YNG-182 115 1 DCT:230:77+78 | 174 | 181 | 100.17
| 135443 ECWA-182 115 135496 YNG-182 115 1 Max |  |  |  |  | 106.04
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | T:77&78 | 135449 GR.I-182 115 135459 NI.B-182 115 1 T:77&78 | 174 | 181 | 113.28
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | DCT:230:77+78 | 135449 GR.I-182 115 135459 NI.B-182 115 1 DCT:230:77+78 | 174 | 181 | 113.27
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | DCT:230:77+78+THR | 135449 GR.I-182 115 135459 NI.B-182 115 1 DCT:230:77+78+THR | 174 | 181 | 113.15
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | T:77&78 | 135449 GR.I-182 115 135459 NI.B-182 115 1 T:77&78 | 174 | 181 | 107.96
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | DCT:230:77+78 | 135449 GR.I-182 115 135459 NI.B-182 115 1 DCT:230:77+78 | 174 | 181 | 107.95
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | DCT:230:77+78+THR | 135449 GR.I-182 115 135459 NI.B-182 115 1 DCT:230:77+78+THR | 174 | 181 | 107.77
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | DCT:230:79+80+THR+ELM3-4 | 135449 GR.I-182 115 135459 NI.B-182 115 1 DCT:230:79+80+THR+ELM3-4 | 174 | 181 | 102.4
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | DCT:230:79+80+ELM3-4 | 135449 GR.I-182 115 135459 NI.B-182 115 1 DCT:230:79+80+ELM3-4 | 174 | 181 | 102.4
| 135449 GR.I-182 115 135459 NI.B-182 115 1 Max |  |  |  |  | 113.28
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | T:77&78 | 135449 GR.I-182 115 135538 LONG-182 115 1 T:77&78 | 200 | 208 | 110.28
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | DCT:230:77+78 | 135449 GR.I-182 115 135538 LONG-182 115 1 DCT:230:77+78 | 200 | 208 | 110.27
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | DCT:230:77+78+THR | 135449 GR.I-182 115 135538 LONG-182 115 1 DCT:230:77+78+THR | 200 | 208 | 109.76
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | T:77&78 | 135449 GR.I-182 115 135538 LONG-182 115 1 T:77&78 | 200 | 208 | 105.54
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | DCT:230:77+78 | 135449 GR.I-182 115 135538 LONG-182 115 1 DCT:230:77+78 | 200 | 208 | 105.53
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | DCT:230:77+78+THR | 135449 GR.I-182 115 135538 LONG-182 115 1 DCT:230:77+78+THR | 200 | 208 | 104.98
| 135449 GR.I-182 115 135538 LONG-182 115 1 Max |  |  |  |  | 110.28
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:77+78+THR | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:77+78+THR | 160 | 166 | 120.39
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:77+78 | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:77+78 | 160 | 166 | 120.12
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | T:77&78 | 135450 GRDNVL1 115 135453 LONG-180 115 1 T:77&78 | 160 | 166 | 120.12
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:77+78+THR | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:77+78+THR | 160 | 166 | 112.83
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | T:77&78 | 135450 GRDNVL1 115 135453 LONG-180 115 1 T:77&78 | 160 | 166 | 112.65
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:77+78 | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:77+78 | 160 | 166 | 112.64
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:79+80+THR+ELM3-4 | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:79+80+THR+ELM3-4 | 160 | 166 | 109.3
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:79+80+ELM3-4 | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:79+80+ELM3-4 | 160 | 166 | 109.3
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | SB:PK115 30+40 | 135450 GRDNVL1 115 135453 LONG-180 115 1 SB:PK115 30+40 | 160 | 166 | 106.03
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:79+80+THR+ELM1-2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:79+80+THR+ELM1-2 | 160 | 166 | 104.22
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:79+80+ELM1-2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:79+80+ELM1-2 | 160 | 166 | 104.21
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:79+80+ELM1-2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:79+80+ELM1-2 | 160 | 166 | 104.21
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:79+80 | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:79+80 | 160 | 166 | 103.17
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:79+80+THR | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:79+80+THR | 160 | 166 | 103.17
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | T:79&80 | 135450 GRDNVL1 115 135453 LONG-180 115 1 T:79&80 | 160 | 166 | 103.17
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:79+80+THR+ELM3-4 | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:79+80+THR+ELM3-4 | 160 | 166 | 101.9
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | DCT:230:79+80+ELM3-4 | 135450 GRDNVL1 115 135453 LONG-180 115 1 DCT:230:79+80+ELM3-4 | 160 | 166 | 101.9
| 135450 GRDNVL1 115 135453 LONG-180 115 1 Max |  |  |  |  | 120.39
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | T:77&78 | 135451 HUNTLEY1 115 135472 S129-38 115 1 T:77&78 | 145 | 151 | 103.68
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | DCT:230:77+78 | 135451 HUNTLEY1 115 135472 S129-38 115 1 DCT:230:77+78 | 145 | 151 | 103.67
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | DCT:230:77+78+THR | 135451 HUNTLEY1 115 135472 S129-38 115 1 DCT:230:77+78+THR | 145 | 151 | 103.31
| 135451 HUNTLEY1 115 135472 S129-38 115 1 Max |  |  |  |  | 103.68
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NF:115:133 HT | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 NF:115:133 HT | 168 | 181 | 111.17
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | DCT:230:77+78+THR | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 DCT:230:77+78+THR | 168 | 181 | 107
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | DCT:230:77+78 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 DCT:230:77+78 | 168 | 181 | 106.54
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | T:77&78 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 T:77&78 | 168 | 181 | 106.54
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NF:115:133 WL | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 NF:115:133 WL | 168 | 181 | 105.44
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 LN:115:133 | 168 | 181 | 104.48
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 LN:115:133 | 168 | 181 | 104.48
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | DCT:230:77+78+THR | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 DCT:230:77+78+THR | 168 | 181 | 102.66
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | T:77&78 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 T:77&78 | 168 | 181 | 102.35
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | DCT:230:77+78 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 DCT:230:77+78 | 168 | 181 | 102.34
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NF:115:133 HT | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 NF:115:133 HT | 168 | 181 | 102.1
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | BUS:115:PK-60 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 BUS:115:PK-60 | 168 | 181 | 101.1
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | DCT:230:79+80+THR+ELM3-4 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 DCT:230:79+80+THR+ELM3-4 | 168 | 181 | 100.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | DCT:230:79+80+ELM3-4 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 DCT:230:79+80+ELM3-4 | 168 | 181 | 100.27
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 Max |  |  |  |  | 111.17
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | DCT:230:77+78+THR | 135451 HUNTLEY1 115 135562 S214-133 115 1 DCT:230:77+78+THR | 168 | 181 | 110.3
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | T:77&78 | 135451 HUNTLEY1 115 135562 S214-133 115 1 T:77&78 | 168 | 181 | 109.99
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | DCT:230:77+78 | 135451 HUNTLEY1 115 135562 S214-133 115 1 DCT:230:77+78 | 168 | 181 | 109.98
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SB:130:PK | 135451 HUNTLEY1 115 135562 S214-133 115 1 SB:130:PK | 168 | 181 | 107.75
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | DCT:230:77+78+THR | 135451 HUNTLEY1 115 135562 S214-133 115 1 DCT:230:77+78+THR | 168 | 181 | 105.95
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | T:77&78 | 135451 HUNTLEY1 115 135562 S214-133 115 1 T:77&78 | 168 | 181 | 105.8
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | DCT:230:77+78 | 135451 HUNTLEY1 115 135562 S214-133 115 1 DCT:230:77+78 | 168 | 181 | 105.79
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | BUS:115:PK-50 | 135451 HUNTLEY1 115 135562 S214-133 115 1 BUS:115:PK-50 | 168 | 181 | 104.24
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | 135451 HUNTLEY1 115 135562 S214-133 115 1 LN:115:130 | 168 | 181 | 104.03
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | 135451 HUNTLEY1 115 135562 S214-133 115 1 LN:115:130 | 168 | 181 | 104.03
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | DCT:230:79+80+THR+ELM3-4 | 135451 HUNTLEY1 115 135562 S214-133 115 1 DCT:230:79+80+THR+ELM3-4 | 168 | 181 | 103.39
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | DCT:230:79+80+ELM3-4 | 135451 HUNTLEY1 115 135562 S214-133 115 1 DCT:230:79+80+ELM3-4 | 168 | 181 | 103.39
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NF:115:130 PK | 135451 HUNTLEY1 115 135562 S214-133 115 1 NF:115:130 PK | 168 | 181 | 101.24
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | DCT:230:79+80+THR+ELM1-2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 DCT:230:79+80+THR+ELM1-2 | 168 | 181 | 100.16
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | DCT:230:79+80+ELM1-2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 DCT:230:79+80+ELM1-2 | 168 | 181 | 100.16
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | DCT:230:79+80+ELM1-2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 DCT:230:79+80+ELM1-2 | 168 | 181 | 100.16
| 135451 HUNTLEY1 115 135562 S214-133 115 1 Max |  |  |  |  | 110.3
Dispatch 2 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | SB:37:LP | 135452 LOCKPORT 115 135510 SHAW-102 115 1 SB:37:LP | 233 | 253 | 103.25
| 135452 LOCKPORT 115 135510 SHAW-102 115 1 Max |  |  |  |  | 103.25
Dispatch 2 | 135453 LONG-180 115 147850 NIAG115E 115 1 | DCT:230:77+78 | 135453 LONG-180 115 147850 NIAG115E 115 1 DCT:230:77+78 | 200 | 208 | 101.41
Dispatch 2 | 135453 LONG-180 115 147850 NIAG115E 115 1 | T:77&78 | 135453 LONG-180 115 147850 NIAG115E 115 1 T:77&78 | 200 | 208 | 101.41
Dispatch 2 | 135453 LONG-180 115 147850 NIAG115E 115 1 | DCT:230:77+78+THR | 135453 LONG-180 115 147850 NIAG115E 115 1 DCT:230:77+78+THR | 200 | 208 | 101.38
Dispatch 2 | 135453 LONG-180 115 147850 NIAG115E 115 1 | SB:PK115 30+40 | 135453 LONG-180 115 147850 NIAG115E 115 1 SB:PK115 30+40 | 200 | 208 | 100.34
| 135453 LONG-180 115 147850 NIAG115E 115 1 Max |  |  |  |  | 101.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:77+78 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:77+78 | 160 | 166 | 132.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | T:77&78 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 T:77&78 | 160 | 166 | 132.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:77+78+THR | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:77+78+THR | 160 | 166 | 131.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | T:77&78 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 T:77&78 | 160 | 166 | 126.93
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:77+78 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:77+78 | 160 | 166 | 126.92
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:77+78+THR | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:77+78+THR | 160 | 166 | 125.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:180+182N | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:115:180+182N | 160 | 166 | 121.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+THR+ELM3-4 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80+THR+ELM3-4 | 160 | 166 | 120.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+ELM3-4 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80+ELM3-4 | 160 | 166 | 120.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:180+182S | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:115:180+182S | 160 | 166 | 119.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:54+182S | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:115:54+182S | 160 | 166 | 118.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+THR+ELM1-2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80+THR+ELM1-2 | 160 | 166 | 115.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+ELM1-2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80+ELM1-2 | 160 | 166 | 115.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+ELM1-2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80+ELM1-2 | 160 | 166 | 115.48
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+THR+ELM3-4 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80+THR+ELM3-4 | 160 | 166 | 115.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+ELM3-4 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80+ELM3-4 | 160 | 166 | 115.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | T:79&80 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 T:79&80 | 160 | 166 | 114.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80 | 160 | 166 | 114.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+THR | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80+THR | 160 | 166 | 114.79
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:54+182S | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:115:54+182S | 160 | 166 | 112.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:180+182N | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:115:180+182N | 160 | 166 | 111.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:180+182S | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:115:180+182S | 160 | 166 | 110.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SB:GI115 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 SB:GI115 | 160 | 166 | 110.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+THR+ELM1-2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80+THR+ELM1-2 | 160 | 166 | 110.44
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+ELM1-2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80+ELM1-2 | 160 | 166 | 110.43
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+ELM1-2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80+ELM1-2 | 160 | 166 | 110.43
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80 | 160 | 166 | 109.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:230:79+80+THR | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:230:79+80+THR | 160 | 166 | 109.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | T:79&80 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 T:79&80 | 160 | 166 | 109.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | 135458 NI.B-181 115 135460 PACK(N)E 115 1 LN:115:182S | 160 | 166 | 109.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | 135458 NI.B-181 115 135460 PACK(N)E 115 1 LN:115:182S | 160 | 166 | 109.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | 135458 NI.B-181 115 135460 PACK(N)E 115 1 LN:115:182N | 160 | 166 | 107.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | 135458 NI.B-181 115 135460 PACK(N)E 115 1 LN:115:182N | 160 | 166 | 107.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SB:182N:PK | 135458 NI.B-181 115 135460 PACK(N)E 115 1 SB:182N:PK | 160 | 166 | 107.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NF:115:182 GI-N | 135458 NI.B-181 115 135460 PACK(N)E 115 1 NF:115:182 GI-N | 160 | 166 | 107.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NF:115:182 PK | 135458 NI.B-181 115 135460 PACK(N)E 115 1 NF:115:182 PK | 160 | 166 | 107.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | BUS:115:PK-30 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 BUS:115:PK-30 | 160 | 166 | 106.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NF:115:182 GI-S | 135458 NI.B-181 115 135460 PACK(N)E 115 1 NF:115:182 GI-S | 160 | 166 | 104.3
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SB:GI115 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 SB:GI115 | 160 | 166 | 102.95
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | 135458 NI.B-181 115 135460 PACK(N)E 115 1 LN:115:182S | 160 | 166 | 101.47
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | 135458 NI.B-181 115 135460 PACK(N)E 115 1 LN:115:182S | 160 | 166 | 101.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DCT:115:102+180 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 DCT:115:102+180 | 160 | 166 | 100.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NF:115:54 GV | 135458 NI.B-181 115 135460 PACK(N)E 115 1 NF:115:54 GV | 160 | 166 | 100.31
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 Max |  |  |  |  | 132.29
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | T:77&78 | 135460 PACK(N)E 115 135538 LONG-182 115 1 T:77&78 | 200 | 208 | 114.81
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | DCT:230:77+78 | 135460 PACK(N)E 115 135538 LONG-182 115 1 DCT:230:77+78 | 200 | 208 | 114.8
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | DCT:230:77+78+THR | 135460 PACK(N)E 115 135538 LONG-182 115 1 DCT:230:77+78+THR | 200 | 208 | 114.15
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | T:77&78 | 135460 PACK(N)E 115 135538 LONG-182 115 1 T:77&78 | 200 | 208 | 110.17
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | DCT:230:77+78 | 135460 PACK(N)E 115 135538 LONG-182 115 1 DCT:230:77+78 | 200 | 208 | 110.16
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | DCT:230:77+78+THR | 135460 PACK(N)E 115 135538 LONG-182 115 1 DCT:230:77+78+THR | 200 | 208 | 109.46
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | DCT:115:180+181/922 | 135460 PACK(N)E 115 135538 LONG-182 115 1 DCT:115:180+181/922 | 200 | 208 | 104.48
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | DCT:230:79+80+THR+ELM3-4 | 135460 PACK(N)E 115 135538 LONG-182 115 1 DCT:230:79+80+THR+ELM3-4 | 200 | 208 | 103.93
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | DCT:230:79+80+ELM3-4 | 135460 PACK(N)E 115 135538 LONG-182 115 1 DCT:230:79+80+ELM3-4 | 200 | 208 | 103.93
| 135460 PACK(N)E 115 135538 LONG-182 115 1 Max |  |  |  |  | 114.81
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 1 | DCT:115:192+195 | 135460 PACK(N)E 115 147850 NIAG115E 115 1 DCT:115:192+195 | 273 | 301 | 107.3
| 135460 PACK(N)E 115 147850 NIAG115E 115 1 Max |  |  |  |  | 107.3
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | DCT:115:101+191 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 DCT:115:101+191 | 247 | 275 | 129.06
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | DCT:230:61+191 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 DCT:230:61+191 | 247 | 275 | 122.82
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | T:61&191 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 T:61&191 | 247 | 275 | 122.82
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | DCT:115:101+191 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 DCT:115:101+191 | 247 | 275 | 105.37
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | DCT:230:61+191 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 DCT:230:61+191 | 247 | 275 | 101.19
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | T:61&191 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 T:61&191 | 247 | 275 | 101.19
| 135460 PACK(N)E 115 147850 NIAG115E 115 2 Max |  |  |  |  | 129.06
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | DCT:115:193+194 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 DCT:115:193+194 | 273 | 299 | 149.88
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | DCT:115:193+194 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 DCT:115:193+194 | 273 | 299 | 126.88
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | SB:129:PK | 135461 PACK(S)W 115 147851 NIAG115W 115 3 SB:129:PK | 273 | 299 | 125.72
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | BUS:115:PK-60 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 BUS:115:PK-60 | 273 | 299 | 124.26
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | SB:129:PK | 135461 PACK(S)W 115 147851 NIAG115W 115 3 SB:129:PK | 273 | 299 | 115.24
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | BUS:115:PK-60 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 BUS:115:PK-60 | 273 | 299 | 113.33
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 Max |  |  |  |  | 149.88
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:77+78+THR | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:77+78+THR | 168 | 185 | 111.27
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:77+78 | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:77+78 | 168 | 185 | 111.07
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | T:77&78 | 135497 ZRMN-133 115 135562 S214-133 115 1 T:77&78 | 168 | 185 | 111.07
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SB:130:PK | 135497 ZRMN-133 115 135562 S214-133 115 1 SB:130:PK | 168 | 185 | 108.29
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:77+78+THR | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:77+78+THR | 168 | 185 | 106.99
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | T:77&78 | 135497 ZRMN-133 115 135562 S214-133 115 1 T:77&78 | 168 | 185 | 106.94
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:77+78 | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:77+78 | 168 | 185 | 106.93
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | BUS:115:PK-50 | 135497 ZRMN-133 115 135562 S214-133 115 1 BUS:115:PK-50 | 168 | 185 | 104.97
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | 135497 ZRMN-133 115 135562 S214-133 115 1 LN:115:130 | 168 | 185 | 104.66
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | 135497 ZRMN-133 115 135562 S214-133 115 1 LN:115:130 | 168 | 185 | 104.66
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:79+80+THR+ELM3-4 | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:79+80+THR+ELM3-4 | 168 | 185 | 104.35
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:79+80+ELM3-4 | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:79+80+ELM3-4 | 168 | 185 | 104.35
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NF:115:130 PK | 135497 ZRMN-133 115 135562 S214-133 115 1 NF:115:130 PK | 168 | 185 | 102.03
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:79+80+THR+ELM1-2 | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:79+80+THR+ELM1-2 | 168 | 185 | 101.11
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:79+80+ELM1-2 | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:79+80+ELM1-2 | 168 | 185 | 101.11
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:79+80+ELM1-2 | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:79+80+ELM1-2 | 168 | 185 | 101.11
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:79+80 | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:79+80 | 168 | 185 | 100.43
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:79+80+THR | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:79+80+THR | 168 | 185 | 100.43
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | T:79&80 | 135497 ZRMN-133 115 135562 S214-133 115 1 T:79&80 | 168 | 185 | 100.43
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SB:130:PK | 135497 ZRMN-133 115 135562 S214-133 115 1 SB:130:PK | 168 | 185 | 100.19
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:79+80+THR+ELM3-4 | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:79+80+THR+ELM3-4 | 168 | 185 | 100.01
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | DCT:230:79+80+ELM3-4 | 135497 ZRMN-133 115 135562 S214-133 115 1 DCT:230:79+80+ELM3-4 | 168 | 185 | 100.01
| 135497 ZRMN-133 115 135562 S214-133 115 1 Max |  |  |  |  | 111.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | DCT:230:77+78+THR | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 DCT:230:77+78+THR | 192 | 239 | 123.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | T:77&78 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 T:77&78 | 192 | 239 | 121.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | DCT:230:77+78 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 DCT:230:77+78 | 192 | 239 | 121.88
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | DCT:230:79+80+THR+ELM3-4 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 DCT:230:79+80+THR+ELM3-4 | 192 | 239 | 112.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | DCT:230:79+80+ELM3-4 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 DCT:230:79+80+ELM3-4 | 192 | 239 | 112.56
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | DCT:230:79+80+THR+ELM1-2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 DCT:230:79+80+THR+ELM1-2 | 192 | 239 | 107.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | DCT:230:79+80+ELM1-2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 DCT:230:79+80+ELM1-2 | 192 | 239 | 107.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | DCT:230:79+80+ELM1-2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 DCT:230:79+80+ELM1-2 | 192 | 239 | 107.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | DCT:230:79+80 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 DCT:230:79+80 | 192 | 239 | 105.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | T:79&80 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 T:79&80 | 192 | 239 | 105.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | DCT:230:79+80+THR | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 DCT:230:79+80+THR | 192 | 239 | 105.72
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 Max |  |  |  |  | 123.34
| Grand Max |  |  |  |  | 149.88

## N-2_NTC_OH_1000_Fixed
SERIES REACTORS ON 77 AND 78 LINES BY-PASSED
Niagara Dispatch | Monitored Facility | First Contingency | Second Contingency | Rate Base (MVA) | Rate Cont (MVA) | Final AC %Loading
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:77&78 | 474 | 478 | 150.28
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:77&78 | 474 | 478 | 146.85
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 474 | 478 | 144.11
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 474 | 478 | 143
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 474 | 478 | 142.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 474 | 478 | 142.66
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 474 | 478 | 139.55
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 474 | 478 | 138.05
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 474 | 478 | 138.05
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 474 | 478 | 137.18
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 474 | 478 | 135.36
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 474 | 478 | 134.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 474 | 478 | 133.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | T:77&78 | 474 | 478 | 133.5
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 474 | 478 | 130.97
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 474 | 478 | 130.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 474 | 478 | 130.8
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 474 | 478 | 130.8
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | T:77&78 | 474 | 478 | 130.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 474 | 478 | 129.8
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 127.41
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | T:77&78 | 474 | 478 | 126.94
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - HOMERCTY | T:77&78 | 474 | 478 | 126.68
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:79&80 | 474 | 478 | 126.43
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | T:77&78 | 474 | 478 | 125.65
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - HOMERCTY | T:77&78 | 474 | 478 | 124.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | T:77&78 | 474 | 478 | 124
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | T:77&78 | 474 | 478 | 123.55
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 123.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:79&80 | 474 | 478 | 122.53
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 1TR | T:77&78 | 474 | 478 | 122.38
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 474 | 478 | 122.29
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | T:77&78 | 474 | 478 | 122.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 474 | 478 | 121.64
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 474 | 478 | 121.51
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 3TR | T:77&78 | 474 | 478 | 121.44
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SHLDON - STONYCR 230 | T:77&78 | 474 | 478 | 121.36
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | T:77&78 | 474 | 478 | 120.84
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS1 | T:77&78 | 474 | 478 | 119.77
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:INDEK-OL | T:77&78 | 474 | 478 | 119.11
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN7 | T:77&78 | 474 | 478 | 118.49
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SHLDON - STONYCR 230 | T:77&78 | 474 | 478 | 118.22
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 474 | 478 | 118.17
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 474 | 478 | 118.1
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 4 | T:77&78 | 474 | 478 | 117.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 5 | T:77&78 | 474 | 478 | 117.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 6 | T:77&78 | 474 | 478 | 117.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 7 | T:77&78 | 474 | 478 | 117.79
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ERIE E - 4 MILE 230 | T:77&78 | 474 | 478 | 117.62
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 474 | 478 | 117.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 474 | 478 | 117.24
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 3TR | T:77&78 | 474 | 478 | 117.22
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 474 | 478 | 117.06
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 4 MILE - ERIE SE 230 | T:77&78 | 474 | 478 | 117.02
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 1TR | T:77&78 | 474 | 478 | 116.96
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 474 | 478 | 116.93
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 474 | 478 | 116.92
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE 345/115 1TR | T:77&78 | 474 | 478 | 116.91
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R506 | 474 | 478 | 116.88
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS2 | T:77&78 | 474 | 478 | 116.85
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:DUPONT46 | T:77&78 | 474 | 478 | 116.82
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 2TR | T:77&78 | 474 | 478 | 116.79
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAG - KINTIGH 345 | T:77&78 | 474 | 478 | 116.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 474 | 478 | 116.44
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS1 | T:77&78 | 474 | 478 | 116.42
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 4TR | T:77&78 | 474 | 478 | 116.36
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 3 | T:77&78 | 474 | 478 | 116.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 1 | T:77&78 | 474 | 478 | 116.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 2 | T:77&78 | 474 | 478 | 116.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:OXBOWNUG | T:77&78 | 474 | 478 | 116.26
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ERIE E - 4 MILE 230 | T:77&78 | 474 | 478 | 115.93
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 474 | 478 | 115.82
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 474 | 478 | 115.82
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 474 | 478 | 115.82
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 115.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 115.81
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:INDEK-OL | T:77&78 | 474 | 478 | 115.72
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 474 | 478 | 115.65
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 474 | 478 | 115.59
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 115.43
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 115.42
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN7 | T:77&78 | 474 | 478 | 115.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 4 | T:77&78 | 474 | 478 | 114.75
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 5 | T:77&78 | 474 | 478 | 114.75
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 6 | T:77&78 | 474 | 478 | 114.75
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 7 | T:77&78 | 474 | 478 | 114.74
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 3TR | T:77&78 | 474 | 478 | 114.07
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:GINNA | T:77&78 | 474 | 478 | 114.05
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 474 | 478 | 113.78
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:OSWEGO 5 | T:77&78 | 474 | 478 | 113.77
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:OSWEGO 6 | T:77&78 | 474 | 478 | 113.72
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:SITHE 1 | T:77&78 | 474 | 478 | 113.56
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:SITHE 2 | Any combination resulting in the loss of two out of three Sawyer transformers under N-1 (Towers 77&78, 77&80) or N-1-1 (any combination of the 77, 79, 80 lines) | 474 | 478 | 113.56
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 4 MILE - ERIE SE 230 | T:77&78 | 474 | 478 | 113.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL - CLAY PC-1 345 | T:77&78 | 474 | 478 | 113.48
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL - CLAY PC-2 345 | T:77&78 | 474 | 478 | 113.48
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE 345/115 1TR | T:77&78 | 474 | 478 | 113.42
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 474 | 478 | 113.41
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAG - KINTIGH 345 | T:77&78 | 474 | 478 | 113.41
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS2 | T:77&78 | 474 | 478 | 113.37
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - PANNELL RP-2 345 | T:77&78 | 474 | 478 | 113.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDL - FRASER 32 345 | T:77&78 | 474 | 478 | 113.33
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 13 345 | T:77&78 | 474 | 478 | 113.29
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:DUPONT46 | T:77&78 | 474 | 478 | 113.28
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DEWITT3 - LAFAYTTE 345 | T:77&78 | 474 | 478 | 113.23
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - EDIC 2-15 345 | T:77&78 | 474 | 478 | 113.22
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 3TR | T:77&78 | 474 | 478 | 113.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - 9MI1 9 345 | T:77&78 | 474 | 478 | 113.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA 345/115 1TR | T:77&78 | 474 | 478 | 113.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA 345/115 2TR | T:77&78 | 474 | 478 | 113.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK - SRIPL 68 230 | T:77&78 | 474 | 478 | 113.02
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 3 115 | T:77&78 | 474 | 478 | 113.02
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LHH - CLAY 7 115 | T:77&78 | 474 | 478 | 113.02
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - TEAL 11 115 | T:77&78 | 474 | 478 | 113.02
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - IND 25 345 | T:77&78 | 474 | 478 | 113.02
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 112.98
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - FARMVLY | T:77&78 | 474 | 478 | 112.86
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 2TR | T:77&78 | 474 | 478 | 112.85
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 3 | T:77&78 | 474 | 478 | 112.75
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | T:77&78 | 474 | 478 | 112.73
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 1 | T:77&78 | 474 | 478 | 112.73
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 2 | T:77&78 | 474 | 478 | 112.73
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | T:77&78 | 474 | 478 | 112.72
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 474 | 478 | 112.68
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R506 | 474 | 478 | 112.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 112.45
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 474 | 478 | 112.42
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 474 | 478 | 112.3
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 474 | 478 | 112.23
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 474 | 478 | 112.22
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 112.21
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:79&80 | 474 | 478 | 111.51
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 111.5
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 111.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 111.49
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 474 | 478 | 110.87
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:GINNA | T:77&78 | 474 | 478 | 110.53
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | T:79&80 | 474 | 478 | 110.25
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - FARMVLY | T:77&78 | 474 | 478 | 109.55
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 108.33
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:79&80 | 474 | 478 | 107.28
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 107.16
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | T:79&80 | 474 | 478 | 106.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 474 | 478 | 106.12
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1302 | 474 | 478 | 104.78
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 474 | 478 | 104.24
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 474 | 478 | 104.09
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:77&80 | 474 | 478 | 103.94
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:78&79 | 474 | 478 | 103.79
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1502 | 474 | 478 | 103.68
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-WC_30&W-F_171 | T:77&78 | 474 | 478 | 103.65
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_NEW | 474 | 478 | 103.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 474 | 478 | 103.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 103.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | T:77&78 | 474 | 478 | 102.61
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1302 | 474 | 478 | 102.44
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1402 | 474 | 478 | 102.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 474 | 478 | 102.2
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt68 | 474 | 478 | 102.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HCWC/NWES | T:77&78 | 474 | 478 | 102.15
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:MBWC/NWES | T:77&78 | 474 | 478 | 102.15
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt67 | 474 | 478 | 101.99
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1202 | 474 | 478 | 101.89
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | T:79&80 | 474 | 478 | 101.63
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:77&80 | 474 | 478 | 101.47
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:78&79 | 474 | 478 | 101.33
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1502 | 474 | 478 | 101.22
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 474 | 478 | 101.22
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 474 | 478 | 101.18
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | DCT:230:79+80+ELM1-2 | 474 | 478 | 101.17
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_NEW | 474 | 478 | 101.15
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 474 | 478 | 101.14
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 474 | 478 | 101.05
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 474 | 478 | 100.94
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:PA230_R304 | 474 | 478 | 100.64
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:PA230_R506 | 474 | 478 | 100.06
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-MB_30&W-F_171 | T:77&78 | 474 | 478 | 100.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-WC_30&W-F_171 | T:77&78 | 474 | 478 | 100.02
| 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  |  |  | 150.28
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAGARA 230/115 1TR | T:77&78 | 496 | 550 | 122.5
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 496 | 550 | 119.47
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 496 | 550 | 119.34
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 496 | 550 | 119.04
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 496 | 550 | 118.34
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 496 | 550 | 117.98
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | PACKARD 230/115 3TR | T:77&78 | 496 | 550 | 117.93
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 496 | 550 | 117.68
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 496 | 550 | 117.68
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 496 | 550 | 116.35
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 496 | 550 | 116.31
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 496 | 550 | 115.99
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - NEWROCH 1 345 | T:79&80 | 496 | 550 | 115.86
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:LOCKPORT | T:77&78 | 496 | 550 | 115.51
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - KINTIGH 345 | T:77&78 | 496 | 550 | 115.4
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 496 | 550 | 115.17
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 496 | 550 | 114.99
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 496 | 550 | 114.37
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 496 | 550 | 114.37
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 496 | 550 | 113.93
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 496 | 550 | 113.69
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 496 | 550 | 112.96
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 496 | 550 | 112.92
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 496 | 550 | 112.84
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | FARMVLY - HOMERCTY | T:77&78 | 496 | 550 | 112.71
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R506 | 496 | 550 | 112.57
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 496 | 550 | 112.03
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 496 | 550 | 111.92
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAGARA 230/115 2TR | T:77&78 | 496 | 550 | 111.52
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | ROCH 345/115 5TR | T:77&78 | 496 | 550 | 111.35
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 496 | 550 | 111.21
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 496 | 550 | 111.21
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:BLISS1 | T:77&78 | 496 | 550 | 111.21
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | PACKARD 230/115 4TR | T:77&78 | 496 | 550 | 111.06
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 496 | 550 | 110.95
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 496 | 550 | 110.95
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:INDEK-OL | T:77&78 | 496 | 550 | 110.95
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 496 | 550 | 110.94
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 496 | 550 | 110.94
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | CLAY - DEW 13 345 | T:77&78 | 496 | 550 | 110.93
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 496 | 550 | 110.9
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | ERIE E - 4 MILE 230 | T:77&78 | 496 | 550 | 110.89
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 496 | 550 | 110.89
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HILLSIDE - WATERCURE 69 230 | T:77&78 | 496 | 550 | 110.77
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HILLSIDE - ETWANDA 70 230 | T:77&78 | 496 | 550 | 110.77
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 496 | 550 | 110.64
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:JAMESGN7 | T:77&78 | 496 | 550 | 110.64
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HILLSIDE 230/115 3TR | T:77&78 | 496 | 550 | 110.49
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 496 | 550 | 110.47
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAGARA 345/230 4TR | T:77&78 | 496 | 550 | 110.44
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | ROCH - PANNELL RP-2 345 | T:77&78 | 496 | 550 | 110.44
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | ROCH - PANNELL RP-1 345 | T:77&78 | 496 | 550 | 110.43
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | DEWITT3 - LAFAYTTE 345 | T:77&78 | 496 | 550 | 110.41
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | PANL - CLAY PC-2 345 | T:77&78 | 496 | 550 | 110.4
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | PANL - CLAY PC-1 345 | T:77&78 | 496 | 550 | 110.39
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAGARA 230/115 1TR | T:77&78 | 496 | 550 | 110.32
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 496 | 550 | 110.08
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 496 | 550 | 110.07
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 496 | 550 | 110.06
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 496 | 550 | 109.88
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 496 | 550 | 109.78
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 496 | 550 | 109.48
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 496 | 550 | 108.75
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 496 | 550 | 108.67
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 496 | 550 | 108.67
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | PACKARD 230/115 3TR | T:77&78 | 496 | 550 | 108.51
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 496 | 550 | 108.46
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAGARA - PACKARD 61 230 | T:62&BP76 | 496 | 550 | 108.46
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | GEN:OSWEGO 6 | T:77&78 | 496 | 550 | 108.43
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:9MIPT1 | T:77&78 | 496 | 550 | 108.19
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SHLDON - STONYCR 230 | T:77&78 | 496 | 550 | 108
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:LOCKPORT | T:77&78 | 496 | 550 | 107.96
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 496 | 550 | 107.86
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:LEW 1-3 | T:77&78 | 496 | 550 | 107.74
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:LEW 4-6 | T:77&78 | 496 | 550 | 107.73
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:LEW 7-9 | T:77&78 | 496 | 550 | 107.73
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:LEW 10-12 | T:77&78 | 496 | 550 | 107.73
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HILLSIDE 230/115 4TR | T:77&78 | 496 | 550 | 107.56
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - KINTIGH 345 | T:77&78 | 496 | 550 | 107.53
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 496 | 550 | 107.53
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:NIAG. 1 | T:77&78 | 496 | 550 | 107.18
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:NIAG. 2 | T:77&78 | 496 | 550 | 107.18
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:NIAG. 3 | T:77&78 | 496 | 550 | 107.18
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - NEWROCH 1 345 | T:79&80 | 496 | 550 | 106.88
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | STNYRDG - HILLSIDE 68B 230 | T:77&78 | 496 | 550 | 106.84
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAGARA 230/115 1TR | DCT:230:79+80+ELM1-2 | 496 | 550 | 106.7
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | OAKDL - FRASER 32 345 | T:77&78 | 496 | 550 | 106.67
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:GINNA | T:77&78 | 496 | 550 | 106.6
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:HC-WC_30&W-F_171 | T:77&78 | 496 | 550 | 106.01
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | MEYER - CANDQUA 60 230 | T:77&78 | 496 | 550 | 105.57
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 496 | 550 | 105.46
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | FARMVLY - HOMERCTY | T:77&78 | 496 | 550 | 105.45
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:HCWC/NWES | T:77&78 | 496 | 550 | 105.45
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:MBWC/NWES | T:77&78 | 496 | 550 | 105.45
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - GARDENVILL 80 230 | T:77&78 | 496 | 550 | 105.23
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:HC-MB_30&W-F_171 | T:77&78 | 496 | 550 | 105.21
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 496 | 550 | 105.05
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 496 | 550 | 104.94
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAGARA 230/115 1TR | T:79&80 | 496 | 550 | 104.89
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | R:HCMB/NWES | T:77&78 | 496 | 550 | 104.74
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 496 | 550 | 104.66
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 496 | 550 | 104.29
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 496 | 550 | 104.11
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | CLAY - DEW 13 345 | T:77&78 | 496 | 550 | 104.09
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | ERIE E - 4 MILE 230 | T:77&78 | 496 | 550 | 103.92
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R506 | 496 | 550 | 103.85
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:BLISS1 | T:77&78 | 496 | 550 | 103.62
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | ROCH 345/115 5TR | T:77&78 | 496 | 550 | 103.57
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | ROCH - PANNELL RP-2 345 | T:77&78 | 496 | 550 | 103.55
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:NIAG. 8 | T:77&78 | 496 | 550 | 103.54
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:NIAG. 9 | T:77&78 | 496 | 550 | 103.54
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:NIAG. 10 | T:77&78 | 496 | 550 | 103.53
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | DEWITT3 - LAFAYTTE 345 | T:77&78 | 496 | 550 | 103.49
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:NIAG. 11 | T:77&78 | 496 | 550 | 103.49
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:NIAG. 12 | T:77&78 | 496 | 550 | 103.49
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:NIAG. 13 | T:77&78 | 496 | 550 | 103.49
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | PANL - CLAY PC-1 345 | T:77&78 | 496 | 550 | 103.48
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | PANL - CLAY PC-2 345 | T:77&78 | 496 | 550 | 103.48
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:INDEK-OL | T:77&78 | 496 | 550 | 103.35
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | CLAY - EDIC 2-15 345 | T:77&78 | 496 | 550 | 103.34
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 496 | 550 | 103.29
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 496 | 550 | 103.25
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 496 | 550 | 103.2
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 496 | 550 | 103.19
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 496 | 550 | 103.19
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | EDIC - FITZ 345 | T:77&78 | 496 | 550 | 103.15
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | OS - EL - LFYTE 17 345 | T:77&78 | 496 | 550 | 103.1
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HILLSIDE - WATERCURE 69 230 | T:77&78 | 496 | 550 | 103.07
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HILLSIDE - ETWANDA 70 230 | T:77&78 | 496 | 550 | 103.07
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | DUNKIRK - SRIPL 68 230 | T:77&78 | 496 | 550 | 103.05
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:JAMESGN7 | T:77&78 | 496 | 550 | 103.04
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 496 | 550 | 103.02
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 496 | 550 | 103.01
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | PANL 345/115 1TR | T:77&78 | 496 | 550 | 102.92
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | PANL 345/115 2TR | T:77&78 | 496 | 550 | 102.92
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | PANL 345/115 3TR | T:77&78 | 496 | 550 | 102.9
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | VOL - MARCY 19 345 | T:77&78 | 496 | 550 | 102.86
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SRIPL - ERIE E 69 230 | T:77&78 | 496 | 550 | 102.85
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HILLSIDE 230/115 3TR | T:77&78 | 496 | 550 | 102.8
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | ROCH - PANNELL RP-1 345 | T:77&78 | 496 | 550 | 102.78
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | T:77&78 | 496 | 550 | 102.7
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAGARA 345/230 4TR | T:77&78 | 496 | 550 | 102.69
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | T:77&78 | 496 | 550 | 102.68
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 496 | 550 | 102.53
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 496 | 550 | 102.52
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | STONYCR - WTHRS 230 | T:77&78 | 496 | 550 | 102.43
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | PACKARD 230/115 3TR | DCT:230:79+80+ELM1-2 | 496 | 550 | 102.1
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 496 | 550 | 102.05
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 496 | 550 | 101.87
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 496 | 550 | 101.86
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 496 | 550 | 101.83
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 496 | 550 | 101.78
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 496 | 550 | 101.71
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 496 | 550 | 101.42
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 496 | 550 | 100.81
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:9MIPT1 | T:77&78 | 496 | 550 | 100.59
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | PACKARD 230/115 3TR | T:79&80 | 496 | 550 | 100.44
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:LOCKPORT | DCT:230:79+80+ELM1-2 | 496 | 550 | 100.4
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SHLDON - STONYCR 230 | T:77&78 | 496 | 550 | 100.38
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 496 | 550 | 100.34
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:LEW 1-3 | T:77&78 | 496 | 550 | 100.2
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:LEW 4-6 | T:77&78 | 496 | 550 | 100.2
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:LEW 7-9 | T:77&78 | 496 | 550 | 100.19
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | G:LEW 10-12 | T:77&78 | 496 | 550 | 100.19
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | HILLSIDE 230/115 4TR | T:77&78 | 496 | 550 | 100.06
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - KINTIGH 345 | DCT:230:79+80+ELM1-2 | 496 | 550 | 100.05
| 130766 ROBIN230 230 147841 NIAGAR2E 230 1 Max |  |  |  |  | 122.5
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 124 | 159 | 109.24
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 124 | 159 | 105.82
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 124 | 159 | 105.25
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 124 | 159 | 100.79
| 130799 ERIE 115 115 130834 N.BRW115 115 1 Max |  |  |  |  | 109.24
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 238 | 306 | 109.46
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 238 | 306 | 109.36
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 238 | 306 | 108.08
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 238 | 306 | 106.49
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | WTHRS - MEYER 230 | SB:GARD230_T7-12 | 238 | 306 | 103.43
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 238 | 306 | 102.39
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | B:MEYER | 238 | 306 | 101.45
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | WTHRS - MEYER 230 | 238 | 306 | 101.4
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 238 | 306 | 100.61
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 238 | 306 | 100.5
| 130815 HINMN115 115 131611 HARIS115 115 1 Max |  |  |  |  | 109.46
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 220 | 280 | 106.01
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 220 | 280 | 105.88
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 220 | 280 | 105.31
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | WTHRS - MEYER 230 | SB:GARD230_T7-12 | 220 | 280 | 101.93
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 220 | 280 | 100.94
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 220 | 280 | 100.75
| 130815 HINMN115 115 135452 LOCKPORT 115 1 Max |  |  |  |  | 106.01
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 139 | 181 | 123.81
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 139 | 181 | 121.54
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 139 | 181 | 119.93
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 139 | 181 | 114.94
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 139 | 181 | 113.54
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 139 | 181 | 110.99
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 139 | 181 | 107.65
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 139 | 181 | 107.63
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 139 | 181 | 107.32
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 139 | 181 | 107.3
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 139 | 181 | 107.15
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | FARMVLY - HOMERCTY | T:77&78 | 139 | 181 | 106.44
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 139 | 181 | 105.62
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 139 | 181 | 105.53
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 139 | 181 | 104.82
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 139 | 181 | 104.67
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 139 | 181 | 104.67
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 139 | 181 | 104.31
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 139 | 181 | 103.91
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 139 | 181 | 103.9
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 139 | 181 | 103.67
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 139 | 181 | 103.67
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 139 | 181 | 103.45
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 139 | 181 | 103.26
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 139 | 181 | 102.89
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 139 | 181 | 102.35
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 139 | 181 | 102.09
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | FARMVLY - HOMERCTY | T:77&78 | 139 | 181 | 101.69
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 139 | 181 | 100.23
| 130834 N.BRW115 115 135437 CLSP-181 115 1 Max |  |  |  |  | 123.81
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 108 | 102.68
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 108 | 102.1
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 108 | 101.59
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 108 | 100.98
| 135268 CLVB-141 115 135483 S55-141 115 1 Max |  |  |  |  | 102.68
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 108 | 104.89
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 108 | 104.3
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 108 | 103.88
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 108 | 103.25
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LFYTE - CLARKCRNS 36A 345 | T:73&74 | 88 | 108 | 101.84
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:73&74 | 88 | 108 | 101.7
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 108 | 101.53
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 108 | 100.95
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 108 | 100.95
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 108 | 100.35
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 108 | 100.33
| 135269 CLVB-142 115 135445 FORD-142 115 1 Max |  |  |  |  | 104.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 566 | 654 | 140.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 566 | 654 | 137.9
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R304 | 566 | 654 | 136.91
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 136.73
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 230 | 566 | 654 | 136.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3230 | 566 | 654 | 136.04
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 566 | 654 | 135.95
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 566 | 654 | 135.93
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 134.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 566 | 654 | 134.8
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 134.01
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 566 | 654 | 133.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 133.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 133.1
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 566 | 654 | 133.01
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R304 | 566 | 654 | 132.97
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL78 | 566 | 654 | 132.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3230 | 566 | 654 | 131.79
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_T7-12 | 566 | 654 | 131.7
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R304 | 566 | 654 | 131.52
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 566 | 654 | 131.12
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 566 | 654 | 130.93
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 130.61
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3230 | 566 | 654 | 130.54
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 566 | 654 | 130.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 566 | 654 | 129.91
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 566 | 654 | 129.39
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R304 | 566 | 654 | 129.28
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 129.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 230 | 566 | 654 | 128.98
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 566 | 654 | 128.98
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3230 | 566 | 654 | 128.75
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B302 | 566 | 654 | 128.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAG345_3108 | 566 | 654 | 128.54
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - NEWROCH 1 345 | 566 | 654 | 128.49
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 566 | 654 | 128.48
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 128.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 128.21
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R304 | 566 | 654 | 127.92
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 127.47
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 566 | 654 | 127.42
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B202 | 566 | 654 | 127.12
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | B:PACKT3 | 566 | 654 | 127.1
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SOMERSET - NEWROCH 1 345 | 566 | 654 | 127.04
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 127
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R304 | 566 | 654 | 126.99
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3230 | 566 | 654 | 126.84
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 126.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 566 | 654 | 126.5
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 566 | 654 | 126.43
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3230 | 566 | 654 | 126.19
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 566 | 654 | 125.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R304 | 566 | 654 | 125.59
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_T7-12 | 566 | 654 | 125.56
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL78 | 566 | 654 | 124.94
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 124.38
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R304 | 566 | 654 | 124.32
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3230 | 566 | 654 | 124.23
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:40&41 | 566 | 654 | 124.16
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 566 | 654 | 124.11
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | B:PACKT3 | 566 | 654 | 123.83
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | SB:PA230_R304 | 566 | 654 | 123.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 566 | 654 | 123.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3230 | 566 | 654 | 123.13
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - HOMERCTY | 566 | 654 | 122.97
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 566 | 654 | 122.96
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT3 | 566 | 654 | 122.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | SB:PA230_R3230 | 566 | 654 | 122.84
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-FV_37&W-F_171 | 566 | 654 | 122.84
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:41&33 | 566 | 654 | 122.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B302 | 566 | 654 | 122.71
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 122.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAG345_3108 | 566 | 654 | 122.62
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 566 | 654 | 122.61
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - NEWROCH 1 345 | 566 | 654 | 122.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAW230_2014 | 566 | 654 | 122.56
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R304 | 566 | 654 | 122
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:34&42 | 566 | 654 | 121.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 121.88
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA 230/115 1TR | 566 | 654 | 121.77
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 121.76
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_2 | 566 | 654 | 121.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_1 | 566 | 654 | 121.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | LFYTE - CLARKCRNS 36A 345 | 566 | 654 | 121.47
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAFA_ELB | 566 | 654 | 121.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAFAYETT | 566 | 654 | 121.41
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3230 | 566 | 654 | 121.33
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 121.11
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B202 | 566 | 654 | 121.1
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SOMERSET - NEWROCH 1 345 | 566 | 654 | 121.02
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_4 | 566 | 654 | 120.84
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_3 | 566 | 654 | 120.84
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | PACKARD 230/115 3TR | 566 | 654 | 120.83
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B5 | 566 | 654 | 120.68
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B6 | 566 | 654 | 120.65
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - CLARKCRNS 36B 345 | 566 | 654 | 120.65
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE_B | 566 | 654 | 120.51
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R304 | 566 | 654 | 120.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-FV_37&W-F_171 | B:PACKT3 | 566 | 654 | 120.29
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 566 | 654 | 120.23
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - HOMERCTY | B:PACKT3 | 566 | 654 | 120.22
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:31&41 | 566 | 654 | 120.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - KINTIGH 345 | B:PACKT3 | 566 | 654 | 120.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_42-4182 | 566 | 654 | 120.05
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 119.97
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3208 | 566 | 654 | 119.83
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R915 | 566 | 654 | 119.79
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:MP11&41 | 566 | 654 | 119.77
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_4182 | 566 | 654 | 119.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3202 | 566 | 654 | 119.66
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - COOPERS 345 SC | 566 | 654 | 119.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3230 | 566 | 654 | 119.54
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R304 | 566 | 654 | 119.52
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:30&40 | 566 | 654 | 119.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R304 | 566 | 654 | 119.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS1 | B:PACKT3 | 566 | 654 | 119.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAG345_3308 | 566 | 654 | 119.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:77&76 | 566 | 654 | 119.26
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - KINTIGH 345 | 566 | 654 | 119.24
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R400 | 566 | 654 | 119.23
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R935 | 566 | 654 | 119.03
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FRASER 345 SC | 566 | 654 | 119.01
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:FRAS345_B1-4062 | 566 | 654 | 119.01
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:INDEK-OL | B:PACKT3 | 566 | 654 | 119.01
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:FRAS345_40-B262 | 566 | 654 | 118.99
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 118.95
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 78 230 | 566 | 654 | 118.92
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3230 | 566 | 654 | 118.69
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 118.68
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:69J&70K | 566 | 654 | 118.65
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:170 | 566 | 654 | 118.63
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:180 | 566 | 654 | 118.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R3230 | 566 | 654 | 118.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._99 | 566 | 654 | 118.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._77 | 566 | 654 | 118.5
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL78 | 566 | 654 | 118.5
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3308 | 566 | 654 | 118.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:MP12&18 | 566 | 654 | 118.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:JAMESGN7 | B:PACKT3 | 566 | 654 | 118.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:160 | 566 | 654 | 118.48
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:150 | 566 | 654 | 118.48
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:40&41 | 566 | 654 | 118.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_3414 | 566 | 654 | 118.44
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_3514 | 566 | 654 | 118.44
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:PECHBTM2 | 566 | 654 | 118.42
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:W89&W90 | 566 | 654 | 118.42
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-SR_37&W-F_171 | B:PACKT3 | 566 | 654 | 118.38
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:FV-5M_37&W-F_171 | B:PACKT3 | 566 | 654 | 118.38
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R140 | 566 | 654 | 118.38
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:90 | 566 | 654 | 118.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3314 | 566 | 654 | 118.34
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - N.SCOT99 I8 345 | 566 | 654 | 118.34
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | B:PACKT3 | 566 | 654 | 118.33
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:F38&F39 | 566 | 654 | 118.33
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS1 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 118.32
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE | 566 | 654 | 118.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:SUSQ1 | 566 | 654 | 118.24
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_2T8082 | 566 | 654 | 118.23
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 13 345 | B:PACKT3 | 566 | 654 | 118.21
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3108 | 566 | 654 | 118.2
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - N.SCOT77 I4 345 | 566 | 654 | 118.19
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:F30&F31 | 566 | 654 | 118.17
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_376512 | 566 | 654 | 118.15
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_31153 | 566 | 654 | 118.12
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_34XC | 566 | 654 | 118.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 118.06
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R935 | 566 | 654 | 118.06
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - 5MILE 345 | 566 | 654 | 118.06
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PV345_RNS5 | 566 | 654 | 118.06
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - 5MILE 345 | B:PACKT3 | 566 | 654 | 118.05
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:FV-5M_37&W-F_171 | 566 | 654 | 118.05
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-SR_37&W-F_171 | 566 | 654 | 118.05
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R945 | 566 | 654 | 118.05
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PV345_RNS4 | 566 | 654 | 118.03
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LEEDS345_R9293 | 566 | 654 | 117.98
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:SALEMG1 | 566 | 654 | 117.96
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:HOPECG1 | 566 | 654 | 117.96
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:LIMERCK2 | 566 | 654 | 117.95
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_3456 | 566 | 654 | 117.92
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_34-B382 | 566 | 654 | 117.88
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_B2-3482 | 566 | 654 | 117.88
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:INDEK-OL | HUNTLEY - PACKARD 78 230 | 566 | 654 | 117.88
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CMT/MTR-34 345 | 566 | 654 | 117.87
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | HURLEY - ROCKT CMT/MTR-34 345 | 566 | 654 | 117.87
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 4 | B:PACKT3 | 566 | 654 | 117.86
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 5 | B:PACKT3 | 566 | 654 | 117.86
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 6 | B:PACKT3 | 566 | 654 | 117.86
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 7 | B:PACKT3 | 566 | 654 | 117.85
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS2 | B:PACKT3 | 566 | 654 | 117.82
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R150 | 566 | 654 | 117.8
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3908 | 566 | 654 | 117.8
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R160 | 566 | 654 | 117.8
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3808 | 566 | 654 | 117.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 566 | 654 | 117.77
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - DEW 13 345 | 566 | 654 | 117.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LEEDS345_R94301 | 566 | 654 | 117.72
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DEWITT3 - LAFAYTTE 345 | B:PACKT3 | 566 | 654 | 117.72
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3230 | 566 | 654 | 117.71
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT3 | 566 | 654 | 117.71
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R110 | 566 | 654 | 117.7
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - WATERCURE 69 230 | B:PACKT3 | 566 | 654 | 117.7
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - ETWANDA 70 230 | B:PACKT3 | 566 | 654 | 117.7
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_4255 | 566 | 654 | 117.69
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R150 | 566 | 654 | 117.68
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R160 | 566 | 654 | 117.68
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_B2-4282 | 566 | 654 | 117.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 566 | 654 | 117.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 566 | 654 | 117.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 1-16 345 | 566 | 654 | 117.66
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 566 | 654 | 117.66
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 566 | 654 | 117.66
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - BECK_TSA 345 | B:PACKT3 | 566 | 654 | 117.64
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - BECK_TSB 345 | B:PACKT3 | 566 | 654 | 117.64
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DUNW345_3 | 566 | 654 | 117.64
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R10 | 566 | 654 | 117.64
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH 345/115 5TR | B:PACKT3 | 566 | 654 | 117.63
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 566 | 654 | 117.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 566 | 654 | 117.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LEEDS345_R92 | 566 | 654 | 117.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL78 | 566 | 654 | 117.61
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3102 | 566 | 654 | 117.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 566 | 654 | 117.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 566 | 654 | 117.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DUNW345_8 | 566 | 654 | 117.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - EDIC 2-15 345 | B:PACKT3 | 566 | 654 | 117.58
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FITZ 345 | 566 | 654 | 117.57
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FITZ - EDIC FEI 345 | 566 | 654 | 117.57
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:5M-SR_37&W-F_171 | B:PACKT3 | 566 | 654 | 117.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DEWI345_R915 | 566 | 654 | 117.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 5 MILE - STOLLE 37A 345 | B:PACKT3 | 566 | 654 | 117.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DEWI345_R130 | 566 | 654 | 117.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DEWI345_R220 | 566 | 654 | 117.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-2 345 | B:PACKT3 | 566 | 654 | 117.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HOMERCTY - STOLLRD 37 345 | B:PACKT3 | 566 | 654 | 117.54
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-1 345 | B:PACKT3 | 566 | 654 | 117.54
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PACKARD 230/115 4TR | B:PACKT3 | 566 | 654 | 117.53
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | VOL - MARCY 19 345 | 566 | 654 | 117.53
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | VOLNEY - MARCY I9 345 | 566 | 654 | 117.53
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:VOLN_R925 | 566 | 654 | 117.52
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3914 | 566 | 654 | 117.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3814 | 566 | 654 | 117.49
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT3 | 566 | 654 | 117.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:JAMESGN7 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 117.35
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - HOMERCTY | 566 | 654 | 117.21
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-FV_37&W-F_171 | 566 | 654 | 117.09
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 117.08
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 117.07
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:41&33 | 566 | 654 | 117.04
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R304 | 566 | 654 | 117.01
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | S:PA_HNTL78 | 566 | 654 | 116.99
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - HOMERCTY | SB:PA230_R304 | 566 | 654 | 116.91
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 116.83
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 116.83
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - KINTIGH 345 | SB:PA230_R304 | 566 | 654 | 116.71
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS2 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 116.68
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 116.65
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 116.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 116.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 116.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 116.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-1 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 116.39
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 116.39
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:34&42 | 566 | 654 | 116.16
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS1 | SB:PA230_R304 | 566 | 654 | 116.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R3230 | 566 | 654 | 116.04
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - HOMERCTY | SB:PA230_R3230 | 566 | 654 | 115.95
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDL - FRASER 32 345 | 566 | 654 | 115.91
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FRASER - OAKDLE 32 345 | 566 | 654 | 115.91
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT2 | 566 | 654 | 115.9
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RAIN345_1W | 566 | 654 | 115.9
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RAIN345_9W | 566 | 654 | 115.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 2TR | B:PACKT3 | 566 | 654 | 115.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:FRAS345_B1-3262 | 566 | 654 | 115.88
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: RAVENSWOOD | 566 | 654 | 115.87
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:30 | 566 | 654 | 115.87
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | BWLN - WHAV -LDN 67 345 | 566 | 654 | 115.87
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT1 | 566 | 654 | 115.87
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PACKARD 230/115 3TR | S:PA_HNTL78 | 566 | 654 | 115.85
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B2 | 566 | 654 | 115.84
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - KINTIGH 345 | SB:PA230_R3230 | 566 | 654 | 115.81
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - FARMVLY | B:PACKT3 | 566 | 654 | 115.8
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROSE345_30553 | 566 | 654 | 115.76
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_4-56-2 | 566 | 654 | 115.76
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M7TR | B:PACKT3 | 566 | 654 | 115.76
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 2TR | 566 | 654 | 115.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_1-56-2 | 566 | 654 | 115.72
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_6-56-2 | 566 | 654 | 115.7
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_1 | 566 | 654 | 115.69
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_2 | 566 | 654 | 115.69
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAFA_ELB | 566 | 654 | 115.69
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | LFYTE - CLARKCRNS 36A 345 | 566 | 654 | 115.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - WTRCR 31 345 | 566 | 654 | 115.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B3 | 566 | 654 | 115.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_3-56-2 | 566 | 654 | 115.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:NOEND | 566 | 654 | 115.66
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:INDEK-OL | SB:PA230_R304 | 566 | 654 | 115.66
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROSE345_30551 | 566 | 654 | 115.63
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROSE345_31152 | 566 | 654 | 115.62
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAFAYETT | 566 | 654 | 115.61
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RMP345_T1500 | 566 | 654 | 115.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M7TR | 566 | 654 | 115.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 7-9 | B:PACKT3 | 566 | 654 | 115.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 10-12 | B:PACKT3 | 566 | 654 | 115.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | RAMAPO - BRNCHBRG 5018 345 | 566 | 654 | 115.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON2 | 566 | 654 | 115.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 1-3 | B:PACKT3 | 566 | 654 | 115.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 4-6 | B:PACKT3 | 566 | 654 | 115.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WATRC345_31-2 | 566 | 654 | 115.58
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2208 | 566 | 654 | 115.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RMP345_1500-2X | 566 | 654 | 115.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2214 | 566 | 654 | 115.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS17-20 | 566 | 654 | 115.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2224 | 566 | 654 | 115.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M6TR | B:PACKT3 | 566 | 654 | 115.54
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M8TR | B:PACKT3 | 566 | 654 | 115.54
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1724 | 566 | 654 | 115.53
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1714 | 566 | 654 | 115.53
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1524 | 566 | 654 | 115.53
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1514 | 566 | 654 | 115.53
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1508 | 566 | 654 | 115.52
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2514 | 566 | 654 | 115.52
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2524 | 566 | 654 | 115.52
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS21-24 | 566 | 654 | 115.52
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2508 | 566 | 654 | 115.52
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON1 | 566 | 654 | 115.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3208 | 566 | 654 | 115.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M8TR | 566 | 654 | 115.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M6TR | 566 | 654 | 115.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:AT_R6361 | 566 | 654 | 115.32
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BESICORP | 566 | 654 | 115.31
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:EMPIRE | 566 | 654 | 115.31
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 73 230 | B:PACKT3 | 566 | 654 | 115.31
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R304 | 566 | 654 | 115.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R304 | 566 | 654 | 115.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 74 230 | B:PACKT3 | 566 | 654 | 115.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STNYRDG - HILLSIDE 68B 230 | B:PACKT3 | 566 | 654 | 115.28
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | B:PACKT3 | 566 | 654 | 115.27
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | S:EMPIRE | 566 | 654 | 115.24
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS1 | SB:PA230_R3230 | 566 | 654 | 115.18
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: IND PT 2 | 566 | 654 | 115.16
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN GILBOA #3&4 | 566 | 654 | 115.14
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:JAMESGN7 | SB:PA230_R304 | 566 | 654 | 115.14
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3302 | 566 | 654 | 115.13
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN GILBOA #1&2 | 566 | 654 | 115.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3202 | 566 | 654 | 115.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3308 | 566 | 654 | 115.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHN_11 | 566 | 654 | 115.07
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHN_9 | 566 | 654 | 115.07
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:72&69 | 566 | 654 | 115.06
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:NTHF3&4 | 566 | 654 | 115.06
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHN_7 | 566 | 654 | 115.04
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - FARMVLY | 566 | 654 | 115.03
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_3 | 566 | 654 | 115.02
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_4 | 566 | 654 | 115.02
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R304 | 566 | 654 | 115
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | BECK - PACKARD BP76 230 | 566 | 654 | 115
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: IND PT 3 | 566 | 654 | 114.98
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - ELM 70 230 | B:PACKT3 | 566 | 654 | 114.94
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHS_3 | 566 | 654 | 114.93
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHS_1 | 566 | 654 | 114.93
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 1 | B:PACKT3 | 566 | 654 | 114.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 2 | B:PACKT3 | 566 | 654 | 114.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 3 | B:PACKT3 | 566 | 654 | 114.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 13 345 | SB:PA230_R304 | 566 | 654 | 114.88
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R304 | 566 | 654 | 114.87
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B5 | 566 | 654 | 114.86
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:67&68&BW | 566 | 654 | 114.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B6 | 566 | 654 | 114.83
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - CLARKCRNS 36B 345 | 566 | 654 | 114.83
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-FV_37&W-F_171 | S:PA_HNTL78 | 566 | 654 | 114.8
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - HOMERCTY | S:PA_HNTL78 | 566 | 654 | 114.79
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | HILLSIDE 230/115 4TR | 566 | 654 | 114.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:HILLSIDE | 566 | 654 | 114.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:HILL_B412 | 566 | 654 | 114.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:INDEK-OL | SB:PA230_R3230 | 566 | 654 | 114.74
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE_B | 566 | 654 | 114.73
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - FARMVLY | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.73
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:SITHE 1 | 566 | 654 | 114.73
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:SITHE 2 | 566 | 654 | 114.73
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:BETHSTM | 566 | 654 | 114.72
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 2TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.72
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HCWC/NWES | 566 | 654 | 114.66
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:MBWC/NWES | 566 | 654 | 114.66
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - ELM 70 230 | 566 | 654 | 114.64
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | WTRCR - MAINSBRG 30A 345 | 566 | 654 | 114.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WATRC345_30-3142 | 566 | 654 | 114.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WATRC345_B1-3042 | 566 | 654 | 114.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:130 | 566 | 654 | 114.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:120_130 | 566 | 654 | 114.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:W97&W98 | 566 | 654 | 114.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M7TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - KINTIGH 345 | S:PA_HNTL78 | 566 | 654 | 114.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:HILL_68-B412 | 566 | 654 | 114.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | STNYRDG - HILLSIDE 68B 230 | 566 | 654 | 114.51
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS2 | SB:PA230_R304 | 566 | 654 | 114.5
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-WC_30&W-F_171 | 566 | 654 | 114.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 1-3 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 4-6 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 7-9 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 10-12 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | BECK - PACKARD BP76 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.48
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 4 | SB:PA230_R304 | 566 | 654 | 114.46
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 5 | SB:PA230_R304 | 566 | 654 | 114.46
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 6 | SB:PA230_R304 | 566 | 654 | 114.46
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 7 | SB:PA230_R304 | 566 | 654 | 114.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1502 | 566 | 654 | 114.43
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:5M-SR_37&W-F_171 | SB:PA230_R304 | 566 | 654 | 114.41
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R304 | 566 | 654 | 114.41
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R304 | 566 | 654 | 114.39
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R304 | 566 | 654 | 114.39
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M6TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M8TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R304 | 566 | 654 | 114.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 5 MILE - STOLLE 37A 345 | SB:PA230_R304 | 566 | 654 | 114.35
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R304 | 566 | 654 | 114.34
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HCMB/NWES | 566 | 654 | 114.33
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - WTRCR 31 345 | B:PACKT3 | 566 | 654 | 114.33
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MEYER - CANDQUA 60 230 | B:PACKT3 | 566 | 654 | 114.31
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH 345/115 5TR | SB:PA230_R304 | 566 | 654 | 114.31
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:31&41 | 566 | 654 | 114.28
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | MAINSBRG - HOMERCITY 30B 345 | 566 | 654 | 114.28
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL - DUNKIRK 73 230 | 566 | 654 | 114.26
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - EDIC 2-15 345 | SB:PA230_R304 | 566 | 654 | 114.26
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_42-4182 | 566 | 654 | 114.24
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL - DUNKIRK 74 230 | 566 | 654 | 114.24
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-2 345 | SB:PA230_R304 | 566 | 654 | 114.24
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:DUNKG3 | 566 | 654 | 114.23
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-1 345 | SB:PA230_R304 | 566 | 654 | 114.23
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS1 | S:PA_HNTL78 | 566 | 654 | 114.2
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:JAMESGN7 | SB:PA230_R3230 | 566 | 654 | 114.19
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-MB_30&W-F_171 | 566 | 654 | 114.16
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:KINT_39-B112 | 566 | 654 | 114.16
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R3230 | 566 | 654 | 114.1
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R3230 | 566 | 654 | 114.1
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:KINT_B1-3812 | 566 | 654 | 114.1
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 73 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.1
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STNYRDG - HILLSIDE 68B 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.1
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 74 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 114.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R304 | 566 | 654 | 114.07
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:PA27&BP76 | 566 | 654 | 114.03
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3208 | 566 | 654 | 114.02
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | T:78&79 | 566 | 654 | 114.02
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3230 | 566 | 654 | 114
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | BECK - PACKARD BP76 230 | B:PACKT3 | 566 | 654 | 114
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R915 | 566 | 654 | 113.98
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:MP11&41 | 566 | 654 | 113.97
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 1 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 113.97
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 2 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 113.97
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 3 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 113.97
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 13 345 | SB:PA230_R3230 | 566 | 654 | 113.95
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL78 | 566 | 654 | 113.89
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_4182 | 566 | 654 | 113.86
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:61&191 | 566 | 654 | 113.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3202 | 566 | 654 | 113.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - COOPERS 345 SC | 566 | 654 | 113.81
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R3230 | 566 | 654 | 113.75
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:INDEK-OL | S:PA_HNTL78 | 566 | 654 | 113.75
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDL - FRASER 32 345 | B:PACKT3 | 566 | 654 | 113.73
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:GINNA | B:PACKT3 | 566 | 654 | 113.72
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - ELM 70 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 113.7
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:30&40 | 566 | 654 | 113.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-FV_37&W-F_171 | B:PACKT3 | 566 | 654 | 113.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - PACKARD 62 230 | 566 | 654 | 113.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 4 | SB:PA230_R3230 | 566 | 654 | 113.61
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 5 | SB:PA230_R3230 | 566 | 654 | 113.61
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 6 | SB:PA230_R3230 | 566 | 654 | 113.61
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 7 | SB:PA230_R3230 | 566 | 654 | 113.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - PACKARD 61 230 | 566 | 654 | 113.59
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | PACKARD 230/115 3TR | 566 | 654 | 113.58
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - HOMERCTY | B:PACKT3 | 566 | 654 | 113.57
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS2 | SB:PA230_R3230 | 566 | 654 | 113.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R955 | 566 | 654 | 113.52
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:62&PA27 | 566 | 654 | 113.5
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:OSWEGO 5 | 566 | 654 | 113.5
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R965 | 566 | 654 | 113.48
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ERIE E - 4 MILE 230 | B:PACKT3 | 566 | 654 | 113.46
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:77&76 | 566 | 654 | 113.44
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R3230 | 566 | 654 | 113.44
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R3230 | 566 | 654 | 113.43
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R3230 | 566 | 654 | 113.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R400 | 566 | 654 | 113.42
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1502 | 566 | 654 | 113.41
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - BECK_TSA 345 | SB:PA230_R3230 | 566 | 654 | 113.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - BECK_TSB 345 | SB:PA230_R3230 | 566 | 654 | 113.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:MLS3&OMS | 566 | 654 | 113.35
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:MILLST3 | 566 | 654 | 113.35
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:250 | 566 | 654 | 113.35
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH 345/115 5TR | SB:PA230_R3230 | 566 | 654 | 113.35
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAG345_3308 | 566 | 654 | 113.34
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CNDGUA | 566 | 654 | 113.32
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA 230/115 1TR | 566 | 654 | 113.31
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - EDIC 2-15 345 | SB:PA230_R3230 | 566 | 654 | 113.31
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | MEYER - CANDQUA 60 230 | 566 | 654 | 113.3
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-2 345 | SB:PA230_R3230 | 566 | 654 | 113.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-1 345 | SB:PA230_R3230 | 566 | 654 | 113.28
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PACKARD 230/115 4TR | SB:PA230_R3230 | 566 | 654 | 113.26
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - KINTIGH 345 | 566 | 654 | 113.24
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SHLDON - STONYCR 230 | B:PACKT3 | 566 | 654 | 113.24
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R935 | 566 | 654 | 113.22
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:FRGT/WRFL | 566 | 654 | 113.21
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:JAMESGN7 | S:PA_HNTL78 | 566 | 654 | 113.21
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R925 | 566 | 654 | 113.2
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FRASER 345 SC | 566 | 654 | 113.19
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:FRAS345_B1-4062 | 566 | 654 | 113.19
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - WTRCR 31 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 113.19
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:FRAS345_40-B262 | 566 | 654 | 113.18
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:OSWEGO 6 | 566 | 654 | 113.18
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 113.17
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:9MIPT1 | 566 | 654 | 113.16
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R935 | 566 | 654 | 113.15
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - KINTIGH 345 | B:PACKT3 | 566 | 654 | 113.14
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 78 230 | 566 | 654 | 113.12
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MEYER - CANDQUA 60 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 113.12
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R3230 | 566 | 654 | 113.05
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | T:78&79 | 566 | 654 | 113.03
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL78 | 566 | 654 | 112.95
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:FITZPATR | 566 | 654 | 112.95
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 13 345 | S:PA_HNTL78 | 566 | 654 | 112.94
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:SEAB&OMS | 566 | 654 | 112.88
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:SEABROOK | 566 | 654 | 112.88
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:69J&70K | 566 | 654 | 112.82
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 112.81
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:170 | 566 | 654 | 112.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:180 | 566 | 654 | 112.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS1 | B:PACKT3 | 566 | 654 | 112.77
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:90 | 566 | 654 | 112.76
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC_765_7402 | 566 | 654 | 112.76
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MSU1_7202>7214>7208>7214 | 566 | 654 | 112.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._99 | 566 | 654 | 112.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | HQ-NY 765 | 566 | 654 | 112.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SRIPL - ERIE E 69 230 | B:PACKT3 | 566 | 654 | 112.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DUNKIRK - SRIPL 68 230 | B:PACKT3 | 566 | 654 | 112.73
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - PACKARD 61 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 112.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE | 566 | 654 | 112.7
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._77 | 566 | 654 | 112.68
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-SR_37&W-F_171 | S:PA_HNTL78 | 566 | 654 | 112.68
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:FV-5M_37&W-F_171 | S:PA_HNTL78 | 566 | 654 | 112.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 112.67
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3308 | 566 | 654 | 112.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:MP12&18 | 566 | 654 | 112.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 112.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:160 | 566 | 654 | 112.65
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:150 | 566 | 654 | 112.65
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_3414 | 566 | 654 | 112.64
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_3514 | 566 | 654 | 112.64
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 2TR | SB:PA230_R304 | 566 | 654 | 112.62
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:PECHBTM2 | 566 | 654 | 112.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:GINNA | HUNTLEY - PACKARD 78 230 | 566 | 654 | 112.59
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:W89&W90 | 566 | 654 | 112.58
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 13 345 | B:PACKT3 | 566 | 654 | 112.58
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDL - FRASER 32 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 112.58
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - FARMVLY | SB:PA230_R304 | 566 | 654 | 112.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS2 | S:PA_HNTL78 | 566 | 654 | 112.56
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R140 | 566 | 654 | 112.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL78 | 566 | 654 | 112.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 11 | B:PACKT3 | 566 | 654 | 112.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 12 | B:PACKT3 | 566 | 654 | 112.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 13 | B:PACKT3 | 566 | 654 | 112.55
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAW230_2014 | 566 | 654 | 112.54
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 8 | B:PACKT3 | 566 | 654 | 112.54
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 9 | B:PACKT3 | 566 | 654 | 112.54
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SHLDON - STONYCR 230 | 566 | 654 | 112.53
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 10 | B:PACKT3 | 566 | 654 | 112.53
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3314 | 566 | 654 | 112.51
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - N.SCOT99 I8 345 | 566 | 654 | 112.51
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:F38&F39 | 566 | 654 | 112.5
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS1 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 112.5
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M7TR | SB:PA230_R304 | 566 | 654 | 112.5
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - 5MILE 345 | S:PA_HNTL78 | 566 | 654 | 112.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL78 | 566 | 654 | 112.46
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_2T8082 | 566 | 654 | 112.45
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 112.43
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - WATERCURE 69 230 | S:PA_HNTL78 | 566 | 654 | 112.42
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - ETWANDA 70 230 | S:PA_HNTL78 | 566 | 654 | 112.42
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:SUSQ1 | 566 | 654 | 112.41
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:PACKT3 | 566 | 654 | 112.4
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3108 | 566 | 654 | 112.38
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - N.SCOT77 I4 345 | 566 | 654 | 112.36
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:F30&F31 | 566 | 654 | 112.34
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 112.33
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:INDEK-OL | B:PACKT3 | 566 | 654 | 112.33
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_376512 | 566 | 654 | 112.31
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - EDIC 2-15 345 | S:PA_HNTL78 | 566 | 654 | 112.31
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_34XC | 566 | 654 | 112.3
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_31153 | 566 | 654 | 112.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M6TR | SB:PA230_R304 | 566 | 654 | 112.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M8TR | SB:PA230_R304 | 566 | 654 | 112.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 7-9 | SB:PA230_R304 | 566 | 654 | 112.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 10-12 | SB:PA230_R304 | 566 | 654 | 112.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 1-3 | SB:PA230_R304 | 566 | 654 | 112.28
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 4-6 | SB:PA230_R304 | 566 | 654 | 112.28
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-1 345 | S:PA_HNTL78 | 566 | 654 | 112.26
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-2 345 | S:PA_HNTL78 | 566 | 654 | 112.26
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:STONY230 | 566 | 654 | 112.24
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SANDY_DC | 566 | 654 | 112.23
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SANDY_DC&OMS | 566 | 654 | 112.23
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PV345_RNS5 | 566 | 654 | 112.22
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - 5MILE 345 | 566 | 654 | 112.21
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R935 | 566 | 654 | 112.2
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PV345_RNS4 | 566 | 654 | 112.2
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R945 | 566 | 654 | 112.19
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:FV-5M_37&W-F_171 | 566 | 654 | 112.18
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-SR_37&W-F_171 | 566 | 654 | 112.18
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | SB:PA230_R304 | 566 | 654 | 112.16
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LEEDS345_R9293 | 566 | 654 | 112.15
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:SALEMG1 | 566 | 654 | 112.14
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:HOPECG1 | 566 | 654 | 112.13
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:LIMERCK2 | 566 | 654 | 112.12
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R304 | 566 | 654 | 112.09
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_3456 | 566 | 654 | 112.08
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ERIE E - 4 MILE 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 112.08
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R304 | 566 | 654 | 112.08
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R304 | 566 | 654 | 112.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DEWITT3 - LAFAYTTE 345 | B:PACKT3 | 566 | 654 | 112.07
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:INDEK-OL | HUNTLEY - PACKARD 78 230 | 566 | 654 | 112.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_34-B382 | 566 | 654 | 112.04
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_B2-3482 | 566 | 654 | 112.04
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | HURLEY - ROCKT CMT/MTR-34 345 | 566 | 654 | 112.03
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CMT/MTR-34 345 | 566 | 654 | 112.03
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R150 | 566 | 654 | 111.96
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SHLDON - STONYCR 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.96
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R160 | 566 | 654 | 111.95
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3908 | 566 | 654 | 111.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3808 | 566 | 654 | 111.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - EDIC 2-15 345 | B:PACKT3 | 566 | 654 | 111.92
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - DEW 13 345 | 566 | 654 | 111.89
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LEEDS345_R94301 | 566 | 654 | 111.88
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-2 345 | B:PACKT3 | 566 | 654 | 111.87
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R110 | 566 | 654 | 111.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_4255 | 566 | 654 | 111.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R150 | 566 | 654 | 111.84
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R160 | 566 | 654 | 111.83
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_B2-4282 | 566 | 654 | 111.83
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 566 | 654 | 111.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 566 | 654 | 111.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 1-16 345 | 566 | 654 | 111.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:JAMESGN7 | B:PACKT3 | 566 | 654 | 111.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 566 | 654 | 111.81
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 566 | 654 | 111.81
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R10 | 566 | 654 | 111.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DUNW345_3 | 566 | 654 | 111.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LEEDS345_R92 | 566 | 654 | 111.78
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 566 | 654 | 111.78
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 566 | 654 | 111.78
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3102 | 566 | 654 | 111.77
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1502 | 566 | 654 | 111.77
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 566 | 654 | 111.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 566 | 654 | 111.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL - CLAY PC-1 345 | B:PACKT3 | 566 | 654 | 111.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL - CLAY PC-2 345 | B:PACKT3 | 566 | 654 | 111.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DUNW345_8 | 566 | 654 | 111.75
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FITZ 345 | 566 | 654 | 111.73
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FITZ - EDIC FEI 345 | 566 | 654 | 111.73
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DEWI345_R915 | 566 | 654 | 111.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DEWI345_R130 | 566 | 654 | 111.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DEWI345_R220 | 566 | 654 | 111.71
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - ELM 70 230 | SB:PA230_R304 | 566 | 654 | 111.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | VOLNEY - MARCY I9 345 | 566 | 654 | 111.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | VOL - MARCY 19 345 | 566 | 654 | 111.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:VOLN_R925 | 566 | 654 | 111.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-SR_37&W-F_171 | B:PACKT3 | 566 | 654 | 111.64
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:FV-5M_37&W-F_171 | B:PACKT3 | 566 | 654 | 111.64
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:GINNA | 566 | 654 | 111.64
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3914 | 566 | 654 | 111.62
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3814 | 566 | 654 | 111.62
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ROCH 345/115 5TR | 566 | 654 | 111.61
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 2TR | SB:PA230_R3230 | 566 | 654 | 111.59
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:JAMESGN7 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - FARMVLY | SB:PA230_R3230 | 566 | 654 | 111.53
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | EDIC - FITZ 345 | B:PACKT3 | 566 | 654 | 111.52
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL - CLAY PC-2 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.51
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 11 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.51
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 12 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.51
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 13 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.51
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 8 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.51
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 9 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.51
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL - CLAY PC-1 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.5
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M7TR | SB:PA230_R3230 | 566 | 654 | 111.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 10 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 1 | SB:PA230_R304 | 566 | 654 | 111.43
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 2 | SB:PA230_R304 | 566 | 654 | 111.43
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 3 | SB:PA230_R304 | 566 | 654 | 111.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 4 | B:PACKT3 | 566 | 654 | 111.41
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 5 | B:PACKT3 | 566 | 654 | 111.41
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 6 | B:PACKT3 | 566 | 654 | 111.41
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 7 | B:PACKT3 | 566 | 654 | 111.4
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | T:78&79 | 566 | 654 | 111.38
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OS - EL - LFYTE 17 345 | B:PACKT3 | 566 | 654 | 111.37
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - 5MILE 345 | B:PACKT3 | 566 | 654 | 111.35
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SRIPL - ERIE E 69 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.35
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DUNKIRK - SRIPL 68 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.34
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 7-9 | SB:PA230_R3230 | 566 | 654 | 111.34
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 10-12 | SB:PA230_R3230 | 566 | 654 | 111.34
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 1-3 | SB:PA230_R3230 | 566 | 654 | 111.33
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 4-6 | SB:PA230_R3230 | 566 | 654 | 111.33
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 1TR | B:PACKT3 | 566 | 654 | 111.29
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 2TR | B:PACKT3 | 566 | 654 | 111.29
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 3TR | B:PACKT3 | 566 | 654 | 111.28
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | EDIC - FITZ 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.27
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M6TR | SB:PA230_R3230 | 566 | 654 | 111.27
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M8TR | SB:PA230_R3230 | 566 | 654 | 111.27
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY 345/115 1TR | B:PACKT3 | 566 | 654 | 111.22
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY 345/115 2TR | B:PACKT3 | 566 | 654 | 111.22
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | VOL - MARCY 19 345 | B:PACKT3 | 566 | 654 | 111.22
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.16
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MEYER - CANDQUA 60 230 | SB:PA230_R304 | 566 | 654 | 111.14
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MASS_765_7108 | 566 | 654 | 111.13
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - WTRCR 31 345 | SB:PA230_R304 | 566 | 654 | 111.13
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 3 115 | B:PACKT3 | 566 | 654 | 111.12
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - TEAL 10 115 | B:PACKT3 | 566 | 654 | 111.12
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - TEAL 11 115 | B:PACKT3 | 566 | 654 | 111.12
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OS - EL - LFYTE 17 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.11
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:5M-SR_37&W-F_171 | B:PACKT3 | 566 | 654 | 111.1
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.1
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.1
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 5 115 | B:PACKT3 | 566 | 654 | 111.1
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - LM 14 115 | B:PACKT3 | 566 | 654 | 111.1
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LHH - CLAY 7 115 | B:PACKT3 | 566 | 654 | 111.09
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS2 | B:PACKT3 | 566 | 654 | 111.09
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FUL - CLAY 4 115 | B:PACKT3 | 566 | 654 | 111.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - WOOD 17 115 | B:PACKT3 | 566 | 654 | 111.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - VOL 21 345 | B:PACKT3 | 566 | 654 | 111.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA 345/115 1TR | B:PACKT3 | 566 | 654 | 111.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA 345/115 2TR | B:PACKT3 | 566 | 654 | 111.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 5 MILE - STOLLE 37A 345 | B:PACKT3 | 566 | 654 | 111.07
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HOMERCTY - STOLLRD 37 345 | B:PACKT3 | 566 | 654 | 111.07
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - 9MI1 9 345 | B:PACKT3 | 566 | 654 | 111.07
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - VOL 20 345 | B:PACKT3 | 566 | 654 | 111.07
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW - VOL 11 345 | B:PACKT3 | 566 | 654 | 111.05
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW - VOL 12 345 | B:PACKT3 | 566 | 654 | 111.05
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - IND 25 345 | B:PACKT3 | 566 | 654 | 111.05
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW 345/115 1TR | B:PACKT3 | 566 | 654 | 111.04
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R3230 | 566 | 654 | 111.03
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 1TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.02
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 2TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.02
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - FITZ 10 345 | B:PACKT3 | 566 | 654 | 111.02
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 3TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.01
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R3230 | 566 | 654 | 111.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | SB:PA230_R3230 | 566 | 654 | 111
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | EDIC - MRCY ue 1-7 345 | B:PACKT3 | 566 | 654 | 111
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - WATERCURE 69 230 | B:PACKT3 | 566 | 654 | 110.99
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - ETWANDA 70 230 | B:PACKT3 | 566 | 654 | 110.99
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | VOL - MARCY 19 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.98
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R3230 | 566 | 654 | 110.97
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY 345/115 1TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.96
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY 345/115 2TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.96
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CANDQUA - STNYRDG 68A 230 | 566 | 654 | 110.96
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | S:AVOCA | 566 | 654 | 110.96
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MASS_765_7102 | 566 | 654 | 110.93
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:STONYRIDGE | 566 | 654 | 110.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - BECK_TSA 345 | B:PACKT3 | 566 | 654 | 110.92
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - BECK_TSB 345 | B:PACKT3 | 566 | 654 | 110.92
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH 345/115 5TR | B:PACKT3 | 566 | 654 | 110.91
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.88
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 3 115 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - TEAL 10 115 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - TEAL 11 115 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS2 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 5 115 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.84
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - LM 14 115 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.84
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LHH - CLAY 7 115 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.83
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-1 345 | B:PACKT3 | 566 | 654 | 110.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FUL - CLAY 4 115 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - WOOD 17 115 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - VOL 20 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - VOL 21 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA 345/115 1TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA 345/115 2TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - 9MI1 9 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.81
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LOCKPORT | B:PACKT3 | 566 | 654 | 110.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - IND 25 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW - VOL 11 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW - VOL 12 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW 345/115 1TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.78
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - FITZ 10 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.75
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.75
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:OSWEGO 5 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.74
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:SITHE 1 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.74
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:SITHE 2 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.74
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | EDIC - MRCY ue 1-7 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - ELM 70 230 | SB:PA230_R3230 | 566 | 654 | 110.64
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 1 | SB:PA230_R3230 | 566 | 654 | 110.64
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 2 | SB:PA230_R3230 | 566 | 654 | 110.64
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 3 | SB:PA230_R3230 | 566 | 654 | 110.64
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 5 MILE - STOLLE 37A 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ERIE E - 4 MILE 230 | 566 | 654 | 110.62
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HOMERCTY - STOLLRD 37 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.61
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:5M-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - FARMVLY | S:PA_HNTL78 | 566 | 654 | 110.6
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 2TR | S:PA_HNTL78 | 566 | 654 | 110.57
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH 345/115 5TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 110.56
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R304 | 566 | 654 | 110.53
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDL - FRASER 32 345 | SB:PA230_R304 | 566 | 654 | 110.53
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:GINNA | SB:PA230_R304 | 566 | 654 | 110.52
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:62&BP76 | 566 | 654 | 110.51
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M7TR | S:PA_HNTL78 | 566 | 654 | 110.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ERIE E - 4 MILE 230 | SB:PA230_R304 | 566 | 654 | 110.44
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - HOMERCTY | SB:PA230_R304 | 566 | 654 | 110.41
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 1-3 | S:PA_HNTL78 | 566 | 654 | 110.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 4-6 | S:PA_HNTL78 | 566 | 654 | 110.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 7-9 | S:PA_HNTL78 | 566 | 654 | 110.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 10-12 | S:PA_HNTL78 | 566 | 654 | 110.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | BECK - PACKARD BP76 230 | S:PA_HNTL78 | 566 | 654 | 110.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-WC_30&W-F_171 | B:PACKT3 | 566 | 654 | 110.22
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M6TR | S:PA_HNTL78 | 566 | 654 | 110.22
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M8TR | S:PA_HNTL78 | 566 | 654 | 110.22
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STONYCR - WTHRS 230 | B:PACKT3 | 566 | 654 | 110.21
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SHLDON - STONYCR 230 | SB:PA230_R304 | 566 | 654 | 110.19
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTRCR - MAINSBRG 30A 345 | B:PACKT3 | 566 | 654 | 110.14
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCWC/NWES | B:PACKT3 | 566 | 654 | 110.12
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:MBWC/NWES | B:PACKT3 | 566 | 654 | 110.12
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | B:Hunt68 | 566 | 654 | 110.11
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - WTRCR 31 345 | SB:PA230_R3230 | 566 | 654 | 110.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RAIN345_1W | 566 | 654 | 110.04
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT2 | 566 | 654 | 110.04
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDL - FRASER 32 345 | 566 | 654 | 110.04
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FRASER - OAKDLE 32 345 | 566 | 654 | 110.04
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RAIN345_9W | 566 | 654 | 110.03
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MEYER - CANDQUA 60 230 | SB:PA230_R3230 | 566 | 654 | 110.03
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: RAVENSWOOD | 566 | 654 | 110.02
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:FRAS345_B1-3262 | 566 | 654 | 110.02
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:30 | 566 | 654 | 110.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | BWLN - WHAV -LDN 67 345 | 566 | 654 | 110.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT1 | 566 | 654 | 110.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 2TR | 566 | 654 | 109.96
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B2 | 566 | 654 | 109.95
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL78 | 566 | 654 | 109.95
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL78 | 566 | 654 | 109.94
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - KINTIGH 345 | SB:PA230_R304 | 566 | 654 | 109.93
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL78 | 566 | 654 | 109.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROSE345_30553 | 566 | 654 | 109.9
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_4-56-2 | 566 | 654 | 109.9
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:SCRIBA_R925 | 566 | 654 | 109.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:9 MI PT2 | 566 | 654 | 109.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:SCRIBA_R230 | 566 | 654 | 109.89
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_1-56-2 | 566 | 654 | 109.86
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 1 | S:PA_HNTL78 | 566 | 654 | 109.86
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 2 | S:PA_HNTL78 | 566 | 654 | 109.86
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 3 | S:PA_HNTL78 | 566 | 654 | 109.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M7TR | 566 | 654 | 109.84
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_6-56-2 | 566 | 654 | 109.84
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_3-56-2 | 566 | 654 | 109.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:NOEND | 566 | 654 | 109.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - WTRCR 31 345 | 566 | 654 | 109.78
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B3 | 566 | 654 | 109.78
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROSE345_30551 | 566 | 654 | 109.77
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROSE345_31152 | 566 | 654 | 109.75
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SRIPL - ERIE E 69 230 | SB:PA230_R304 | 566 | 654 | 109.74
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RMP345_T1500 | 566 | 654 | 109.73
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON2 | 566 | 654 | 109.72
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | BECK - PACKARD BP76 230 | SB:PA230_R3230 | 566 | 654 | 109.72
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DUNKIRK - SRIPL 68 230 | SB:PA230_R304 | 566 | 654 | 109.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | RAMAPO - BRNCHBRG 5018 345 | 566 | 654 | 109.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WATRC345_31-2 | 566 | 654 | 109.69
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2208 | 566 | 654 | 109.69
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RMP345_1500-2X | 566 | 654 | 109.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2214 | 566 | 654 | 109.67
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS17-20 | 566 | 654 | 109.67
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2224 | 566 | 654 | 109.67
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1724 | 566 | 654 | 109.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1714 | 566 | 654 | 109.66
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1402 | 566 | 654 | 109.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1524 | 566 | 654 | 109.65
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1514 | 566 | 654 | 109.65
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1508 | 566 | 654 | 109.65
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2524 | 566 | 654 | 109.64
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2514 | 566 | 654 | 109.64
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS21-24 | 566 | 654 | 109.64
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2508 | 566 | 654 | 109.64
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M8TR | 566 | 654 | 109.64
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M6TR | 566 | 654 | 109.64
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON1 | 566 | 654 | 109.58
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS1 | SB:PA230_R304 | 566 | 654 | 109.57
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - ELM 70 230 | S:PA_HNTL78 | 566 | 654 | 109.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/NWES | 566 | 654 | 109.53
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SRIPL - ERIE E 69 230 | 566 | 654 | 109.5
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3208 | 566 | 654 | 109.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | DUNKIRK - SRIPL 68 230 | 566 | 654 | 109.47
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:SRIPLEY | 566 | 654 | 109.47
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:AT_R6361 | 566 | 654 | 109.45
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BESICORP | 566 | 654 | 109.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:GINNA | SB:PA230_R3230 | 566 | 654 | 109.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDL - FRASER 32 345 | SB:PA230_R3230 | 566 | 654 | 109.45
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:EMPIRE | 566 | 654 | 109.44
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | S:EMPIRE | 566 | 654 | 109.38
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 13 345 | SB:PA230_R304 | 566 | 654 | 109.38
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R3230 | 566 | 654 | 109.36
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: IND PT 2 | 566 | 654 | 109.3
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R304 | 566 | 654 | 109.3
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - HOMERCTY | SB:PA230_R3230 | 566 | 654 | 109.27
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN GILBOA #3&4 | 566 | 654 | 109.27
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3302 | 566 | 654 | 109.26
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:72&69 | 566 | 654 | 109.25
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 2TR | B:PACKT3 | 566 | 654 | 109.24
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN GILBOA #1&2 | 566 | 654 | 109.22
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3202 | 566 | 654 | 109.22
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3308 | 566 | 654 | 109.22
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHN_11 | 566 | 654 | 109.21
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | BECK - PACKARD BP76 230 | 566 | 654 | 109.21
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHN_9 | 566 | 654 | 109.21
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:NTHF3&4 | 566 | 654 | 109.19
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHN_7 | 566 | 654 | 109.18
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ERIE E - 4 MILE 230 | SB:PA230_R3230 | 566 | 654 | 109.18
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 11 | SB:PA230_R304 | 566 | 654 | 109.17
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 12 | SB:PA230_R304 | 566 | 654 | 109.17
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 13 | SB:PA230_R304 | 566 | 654 | 109.17
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | STONYCR - WTHRS 230 | 566 | 654 | 109.16
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 8 | SB:PA230_R304 | 566 | 654 | 109.16
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 9 | SB:PA230_R304 | 566 | 654 | 109.16
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M7TR | B:PACKT3 | 566 | 654 | 109.15
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 10 | SB:PA230_R304 | 566 | 654 | 109.15
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:INDEK-OL | SB:PA230_R304 | 566 | 654 | 109.14
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - FARMVLY | 566 | 654 | 109.13
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: IND PT 3 | 566 | 654 | 109.12
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHS_3 | 566 | 654 | 109.07
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHS_1 | 566 | 654 | 109.07
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-WC_30&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 109.07
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - WTRCR 31 345 | S:PA_HNTL78 | 566 | 654 | 109.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-FV_37&W-F_171 | S:PA_HNTL78 | 566 | 654 | 109.05
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:KINTIGH | B:PACKT3 | 566 | 654 | 109.04
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - FARMVLY | B:PACKT3 | 566 | 654 | 109.03
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTRCR - MAINSBRG 30A 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 109.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - HOMERCTY | S:PA_HNTL78 | 566 | 654 | 109
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:67&68&BW | 566 | 654 | 108.99
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCWC/NWES | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.99
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:MBWC/NWES | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.99
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SHLDON - STONYCR 230 | SB:PA230_R3230 | 566 | 654 | 108.98
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MEYER - CANDQUA 60 230 | S:PA_HNTL78 | 566 | 654 | 108.98
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 2TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.97
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M6TR | B:PACKT3 | 566 | 654 | 108.97
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M8TR | B:PACKT3 | 566 | 654 | 108.97
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 2TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.91
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | HILLSIDE 230/115 4TR | 566 | 654 | 108.9
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:HILLSIDE | 566 | 654 | 108.9
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:HILL_B412 | 566 | 654 | 108.9
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STONYCR - WTHRS 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.9
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - KINTIGH 345 | SB:PA230_R3230 | 566 | 654 | 108.88
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R304 | 566 | 654 | 108.88
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - FARMVLY | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.87
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - ELM 70 230 | 566 | 654 | 108.87
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | B:Hunt68 | 566 | 654 | 108.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:SITHE 1 | 566 | 654 | 108.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:SITHE 2 | 566 | 654 | 108.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:BETHSTM | 566 | 654 | 108.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M7TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 1-3 | B:PACKT3 | 566 | 654 | 108.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 7-9 | B:PACKT3 | 566 | 654 | 108.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 10-12 | B:PACKT3 | 566 | 654 | 108.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 4-6 | B:PACKT3 | 566 | 654 | 108.84
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HCWC/NWES | 566 | 654 | 108.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:MBWC/NWES | 566 | 654 | 108.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - WTRCR 31 345 | B:PACKT3 | 566 | 654 | 108.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - EDIC 2-15 345 | SB:PA230_R304 | 566 | 654 | 108.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WTHERS230 | 566 | 654 | 108.74
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:120_130 | 566 | 654 | 108.73
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:130 | 566 | 654 | 108.73
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:W97&W98 | 566 | 654 | 108.73
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R304 | 566 | 654 | 108.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R304 | 566 | 654 | 108.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WATRC345_30-3142 | 566 | 654 | 108.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | WTRCR - MAINSBRG 30A 345 | 566 | 654 | 108.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:HILL_68-B412 | 566 | 654 | 108.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WATRC345_B1-3042 | 566 | 654 | 108.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | BECK - PACKARD BP76 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.7
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | STNYRDG - HILLSIDE 68B 230 | 566 | 654 | 108.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-2 345 | SB:PA230_R304 | 566 | 654 | 108.68
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - PACKARD 62 230 | S:PA_HNTL78 | 566 | 654 | 108.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M6TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M8TR | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 1-3 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 4-6 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 7-9 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 10-12 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.66
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:JAMESGN7 | SB:PA230_R304 | 566 | 654 | 108.65
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCMB/NWES | B:PACKT3 | 566 | 654 | 108.64
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STNYRDG - HILLSIDE 68B 230 | B:PACKT3 | 566 | 654 | 108.63
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 73 230 | B:PACKT3 | 566 | 654 | 108.62
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 74 230 | B:PACKT3 | 566 | 654 | 108.61
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-WC_30&W-F_171 | 566 | 654 | 108.6
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:61&191 | 566 | 654 | 108.59
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL - CLAY PC-2 345 | SB:PA230_R304 | 566 | 654 | 108.59
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - PACKARD 61 230 | S:PA_HNTL78 | 566 | 654 | 108.59
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL - CLAY PC-1 345 | SB:PA230_R304 | 566 | 654 | 108.58
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-MB_30&W-F_171 | B:PACKT3 | 566 | 654 | 108.58
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PACKARD 230/115 3TR | S:PA_HNTL78 | 566 | 654 | 108.55
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - KINTIGH 345 | S:PA_HNTL78 | 566 | 654 | 108.52
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - WTRCR 31 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.51
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS1 | SB:PA230_R3230 | 566 | 654 | 108.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MAINSBRG - HOMERCITY 30B 345 | B:PACKT3 | 566 | 654 | 108.48
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:GINNA | S:PA_HNTL78 | 566 | 654 | 108.47
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1402 | 566 | 654 | 108.46
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SRIPL - ERIE E 69 230 | SB:PA230_R3230 | 566 | 654 | 108.46
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDL - FRASER 32 345 | S:PA_HNTL78 | 566 | 654 | 108.46
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HCMB/NWES | 566 | 654 | 108.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DUNKIRK - SRIPL 68 230 | SB:PA230_R3230 | 566 | 654 | 108.45
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL - DUNKIRK 73 230 | 566 | 654 | 108.44
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:DUNKG3 | 566 | 654 | 108.42
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL - DUNKIRK 74 230 | 566 | 654 | 108.41
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | MAINSBRG - HOMERCITY 30B 345 | 566 | 654 | 108.4
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - PACKARD 62 230 | 566 | 654 | 108.37
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS1 | S:PA_HNTL78 | 566 | 654 | 108.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:DUNKG4 | 566 | 654 | 108.36
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | EDIC - FITZ 345 | SB:PA230_R304 | 566 | 654 | 108.35
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R304 | 566 | 654 | 108.33
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STNYRDG - HILLSIDE 68B 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.32
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - ELM 70 230 | B:PACKT3 | 566 | 654 | 108.31
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 73 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.31
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - PACKARD 61 230 | 566 | 654 | 108.3
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 13 345 | SB:PA230_R3230 | 566 | 654 | 108.3
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | S:PA_HNTL78 | 566 | 654 | 108.29
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-MB_30&W-F_171 | 566 | 654 | 108.29
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 74 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 11 | SB:PA230_R3230 | 566 | 654 | 108.28
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 12 | SB:PA230_R3230 | 566 | 654 | 108.28
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 13 | SB:PA230_R3230 | 566 | 654 | 108.28
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 8 | SB:PA230_R3230 | 566 | 654 | 108.27
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 9 | SB:PA230_R3230 | 566 | 654 | 108.27
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 10 | SB:PA230_R3230 | 566 | 654 | 108.26
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:PA27&BP76 | 566 | 654 | 108.2
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OS - EL - LFYTE 17 345 | SB:PA230_R304 | 566 | 654 | 108.2
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 13 345 | S:PA_HNTL78 | 566 | 654 | 108.19
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:KINTIGH | HUNTLEY - PACKARD 78 230 | 566 | 654 | 108.19
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:62&PA27 | 566 | 654 | 108.17
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 1TR | SB:PA230_R304 | 566 | 654 | 108.14
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 2TR | SB:PA230_R304 | 566 | 654 | 108.14
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 4 | SB:PA230_R304 | 566 | 654 | 108.14
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 5 | SB:PA230_R304 | 566 | 654 | 108.14
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 6 | SB:PA230_R304 | 566 | 654 | 108.14
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 3TR | SB:PA230_R304 | 566 | 654 | 108.13
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 7 | SB:PA230_R304 | 566 | 654 | 108.13
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:KINT_39-B112 | 566 | 654 | 108.1
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDL - FRASER 32 345 | B:PACKT3 | 566 | 654 | 108.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R3230 | 566 | 654 | 108.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY 345/115 1TR | SB:PA230_R304 | 566 | 654 | 108.07
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY 345/115 2TR | SB:PA230_R304 | 566 | 654 | 108.07
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:5M-SR_37&W-F_171 | SB:PA230_R304 | 566 | 654 | 108.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | VOL - MARCY 19 345 | SB:PA230_R304 | 566 | 654 | 108.06
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1502 | 566 | 654 | 108.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1502 | 566 | 654 | 108.03
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:INDEK-OL | SB:PA230_R3230 | 566 | 654 | 108.03
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/WF/NWES | 566 | 654 | 108.03
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 5 MILE - STOLLE 37A 345 | SB:PA230_R304 | 566 | 654 | 108.02
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/WRFL | 566 | 654 | 108.02
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R304 | 566 | 654 | 108.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:KINT_B1-3812 | 566 | 654 | 108.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1502 | 566 | 654 | 108
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:DKSR/WRFL | 566 | 654 | 108
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 3 115 | SB:PA230_R304 | 566 | 654 | 107.97
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - TEAL 10 115 | SB:PA230_R304 | 566 | 654 | 107.97
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - TEAL 11 115 | SB:PA230_R304 | 566 | 654 | 107.97
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - ELM 70 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 107.96
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 5 115 | SB:PA230_R304 | 566 | 654 | 107.95
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - LM 14 115 | SB:PA230_R304 | 566 | 654 | 107.95
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LHH - CLAY 7 115 | SB:PA230_R304 | 566 | 654 | 107.94
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - WOOD 17 115 | SB:PA230_R304 | 566 | 654 | 107.94
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - VOL 21 345 | SB:PA230_R304 | 566 | 654 | 107.94
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS2 | SB:PA230_R304 | 566 | 654 | 107.94
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:INDEK-OL | S:PA_HNTL78 | 566 | 654 | 107.94
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FUL - CLAY 4 115 | SB:PA230_R304 | 566 | 654 | 107.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - VOL 20 345 | SB:PA230_R304 | 566 | 654 | 107.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA 345/115 1TR | SB:PA230_R304 | 566 | 654 | 107.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA 345/115 2TR | SB:PA230_R304 | 566 | 654 | 107.93
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ERIE E - 4 MILE 230 | S:PA_HNTL78 | 566 | 654 | 107.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - 9MI1 9 345 | SB:PA230_R304 | 566 | 654 | 107.92
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - IND 25 345 | SB:PA230_R304 | 566 | 654 | 107.91
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW - VOL 11 345 | SB:PA230_R304 | 566 | 654 | 107.9
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW - VOL 12 345 | SB:PA230_R304 | 566 | 654 | 107.9
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW 345/115 1TR | SB:PA230_R304 | 566 | 654 | 107.9
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - FITZ 10 345 | SB:PA230_R304 | 566 | 654 | 107.87
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDL - FRASER 32 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 107.87
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R304 | 566 | 654 | 107.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R304 | 566 | 654 | 107.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | EDIC - MRCY ue 1-7 345 | SB:PA230_R304 | 566 | 654 | 107.86
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SHLDON - STONYCR 230 | S:PA_HNTL78 | 566 | 654 | 107.84
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R3230 | 566 | 654 | 107.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R304 | 566 | 654 | 107.77
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH 345/115 5TR | SB:PA230_R304 | 566 | 654 | 107.75
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL78 | 566 | 654 | 107.69
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | T:78&79 | 566 | 654 | 107.69
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-1 345 | SB:PA230_R304 | 566 | 654 | 107.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | T:78&79 | 566 | 654 | 107.67
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | T:78&79 | 566 | 654 | 107.67
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - EDIC 2-15 345 | SB:PA230_R3230 | 566 | 654 | 107.64
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R955 | 566 | 654 | 107.63
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:OSWEGO 5 | 566 | 654 | 107.61
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R965 | 566 | 654 | 107.59
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-2 345 | SB:PA230_R3230 | 566 | 654 | 107.59
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MEYER - CANDQUA 60 230 | B:PACKT3 | 566 | 654 | 107.58
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 1 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 107.56
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 2 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 107.56
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 3 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 107.56
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - EDIC 2-15 345 | S:PA_HNTL78 | 566 | 654 | 107.54
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:JAMESGN7 | SB:PA230_R3230 | 566 | 654 | 107.52
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 107.49
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL - CLAY PC-2 345 | SB:PA230_R3230 | 566 | 654 | 107.49
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL - CLAY PC-1 345 | SB:PA230_R3230 | 566 | 654 | 107.48
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:MLS3&OMS | 566 | 654 | 107.47
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:MILLST3 | 566 | 654 | 107.47
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:250 | 566 | 654 | 107.47
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-2 345 | S:PA_HNTL78 | 566 | 654 | 107.47
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCMB/NWES | HUNTLEY - PACKARD 78 230 | 566 | 654 | 107.47
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CNDGUA | 566 | 654 | 107.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | B:Hunt68 | 566 | 654 | 107.44
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | BECK - PACKARD BP76 230 | B:PACKT3 | 566 | 654 | 107.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - PACKARD 61 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 107.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | MEYER - CANDQUA 60 230 | 566 | 654 | 107.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 1 | B:PACKT3 | 566 | 654 | 107.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 2 | B:PACKT3 | 566 | 654 | 107.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 3 | B:PACKT3 | 566 | 654 | 107.43
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:KINTIGH | 566 | 654 | 107.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:JAMESGN7 | S:PA_HNTL78 | 566 | 654 | 107.42
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:68&160 | 566 | 654 | 107.4
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-MB_30&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 107.39
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 11 | S:PA_HNTL78 | 566 | 654 | 107.39
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 12 | S:PA_HNTL78 | 566 | 654 | 107.39
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 13 | S:PA_HNTL78 | 566 | 654 | 107.39
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 8 | S:PA_HNTL78 | 566 | 654 | 107.38
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 9 | S:PA_HNTL78 | 566 | 654 | 107.38
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL - CLAY PC-1 345 | S:PA_HNTL78 | 566 | 654 | 107.37
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL - CLAY PC-2 345 | S:PA_HNTL78 | 566 | 654 | 107.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 10 | S:PA_HNTL78 | 566 | 654 | 107.37
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:FRGT/WRFL | 566 | 654 | 107.32
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R3230 | 566 | 654 | 107.31
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R3230 | 566 | 654 | 107.31
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R925 | 566 | 654 | 107.3
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MAINSBRG - HOMERCITY 30B 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 107.3
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:OSWEGO 6 | 566 | 654 | 107.29
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MEYER - CANDQUA 60 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 107.28
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:9MIPT1 | 566 | 654 | 107.27
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R935 | 566 | 654 | 107.26
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STONYCR - WTHRS 230 | SB:PA230_R304 | 566 | 654 | 107.26
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | EDIC - FITZ 345 | SB:PA230_R3230 | 566 | 654 | 107.24
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SRIPL - ERIE E 69 230 | S:PA_HNTL78 | 566 | 654 | 107.21
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DUNKIRK - SRIPL 68 230 | S:PA_HNTL78 | 566 | 654 | 107.19
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-WC_30&W-F_171 | SB:PA230_R304 | 566 | 654 | 107.14
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | EDIC - FITZ 345 | S:PA_HNTL78 | 566 | 654 | 107.13
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 4 | SB:PA230_R3230 | 566 | 654 | 107.13
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 5 | SB:PA230_R3230 | 566 | 654 | 107.13
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 6 | SB:PA230_R3230 | 566 | 654 | 107.13
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 7 | SB:PA230_R3230 | 566 | 654 | 107.12
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OS - EL - LFYTE 17 345 | SB:PA230_R3230 | 566 | 654 | 107.1
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:FITZPATR | 566 | 654 | 107.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 11 | B:PACKT3 | 566 | 654 | 107.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 12 | B:PACKT3 | 566 | 654 | 107.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 13 | B:PACKT3 | 566 | 654 | 107.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 8 | B:PACKT3 | 566 | 654 | 107.05
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 9 | B:PACKT3 | 566 | 654 | 107.05
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 10 | B:PACKT3 | 566 | 654 | 107.04
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R3230 | 566 | 654 | 107.03
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R304 | 566 | 654 | 107.03
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCWC/NWES | SB:PA230_R304 | 566 | 654 | 107.02
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:MBWC/NWES | SB:PA230_R304 | 566 | 654 | 107.02
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1402 | 566 | 654 | 107.02
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 1TR | SB:PA230_R3230 | 566 | 654 | 107.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 2TR | SB:PA230_R3230 | 566 | 654 | 107.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:SEABROOK | 566 | 654 | 107
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:SEAB&OMS | 566 | 654 | 107
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 3TR | SB:PA230_R3230 | 566 | 654 | 107
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL78 | 566 | 654 | 106.99
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OS - EL - LFYTE 17 345 | S:PA_HNTL78 | 566 | 654 | 106.98
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:GINNA | B:PACKT3 | 566 | 654 | 106.96
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | VOL - MARCY 19 345 | SB:PA230_R3230 | 566 | 654 | 106.95
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:73&74 | 566 | 654 | 106.95
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-SR_37&W-F_171 | S:PA_HNTL78 | 566 | 654 | 106.94
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:FV-5M_37&W-F_171 | S:PA_HNTL78 | 566 | 654 | 106.94
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY 345/115 1TR | SB:PA230_R3230 | 566 | 654 | 106.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY 345/115 2TR | SB:PA230_R3230 | 566 | 654 | 106.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 11 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 106.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 12 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 106.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 13 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 106.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 10 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 106.92
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 8 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 106.92
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 9 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 106.92
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 1TR | S:PA_HNTL78 | 566 | 654 | 106.9
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 2TR | S:PA_HNTL78 | 566 | 654 | 106.9
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC_765_7402 | 566 | 654 | 106.89
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MSU1_7202>7214>7208>7214 | 566 | 654 | 106.89
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PANL 345/115 3TR | S:PA_HNTL78 | 566 | 654 | 106.89
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | HQ-NY 765 | 566 | 654 | 106.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY 345/115 1TR | S:PA_HNTL78 | 566 | 654 | 106.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY 345/115 2TR | S:PA_HNTL78 | 566 | 654 | 106.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 3 115 | SB:PA230_R3230 | 566 | 654 | 106.84
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - TEAL 10 115 | SB:PA230_R3230 | 566 | 654 | 106.84
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | VOL - MARCY 19 345 | S:PA_HNTL78 | 566 | 654 | 106.84
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - LM 14 115 | SB:PA230_R3230 | 566 | 654 | 106.83
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - TEAL 11 115 | SB:PA230_R3230 | 566 | 654 | 106.83
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 5 115 | SB:PA230_R3230 | 566 | 654 | 106.81
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS2 | SB:PA230_R3230 | 566 | 654 | 106.81
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LHH - CLAY 7 115 | SB:PA230_R3230 | 566 | 654 | 106.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - WOOD 17 115 | SB:PA230_R3230 | 566 | 654 | 106.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - VOL 21 345 | SB:PA230_R3230 | 566 | 654 | 106.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FUL - CLAY 4 115 | SB:PA230_R3230 | 566 | 654 | 106.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - VOL 20 345 | SB:PA230_R3230 | 566 | 654 | 106.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA 345/115 1TR | SB:PA230_R3230 | 566 | 654 | 106.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA 345/115 2TR | SB:PA230_R3230 | 566 | 654 | 106.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - 9MI1 9 345 | SB:PA230_R3230 | 566 | 654 | 106.78
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - IND 25 345 | SB:PA230_R3230 | 566 | 654 | 106.77
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW - VOL 11 345 | SB:PA230_R3230 | 566 | 654 | 106.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW - VOL 12 345 | SB:PA230_R3230 | 566 | 654 | 106.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW 345/115 1TR | SB:PA230_R3230 | 566 | 654 | 106.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - TEAL 11 115 | S:PA_HNTL78 | 566 | 654 | 106.75
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:GINNA | HUNTLEY - PACKARD 78 230 | 566 | 654 | 106.74
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 3 115 | S:PA_HNTL78 | 566 | 654 | 106.74
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - TEAL 10 115 | S:PA_HNTL78 | 566 | 654 | 106.74
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - LM 14 115 | S:PA_HNTL78 | 566 | 654 | 106.73
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - FITZ 10 345 | SB:PA230_R3230 | 566 | 654 | 106.73
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - 5MILE 345 | S:PA_HNTL78 | 566 | 654 | 106.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 5 115 | S:PA_HNTL78 | 566 | 654 | 106.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LHH - CLAY 7 115 | S:PA_HNTL78 | 566 | 654 | 106.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | EDIC - MRCY ue 1-7 345 | SB:PA230_R3230 | 566 | 654 | 106.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS2 | S:PA_HNTL78 | 566 | 654 | 106.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:5M-SR_37&W-F_171 | SB:PA230_R3230 | 566 | 654 | 106.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R3230 | 566 | 654 | 106.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R3230 | 566 | 654 | 106.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FUL - CLAY 4 115 | S:PA_HNTL78 | 566 | 654 | 106.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - WOOD 17 115 | S:PA_HNTL78 | 566 | 654 | 106.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - VOL 21 345 | S:PA_HNTL78 | 566 | 654 | 106.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA 345/115 1TR | S:PA_HNTL78 | 566 | 654 | 106.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA 345/115 2TR | S:PA_HNTL78 | 566 | 654 | 106.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ERIE E - 4 MILE 230 | B:PACKT3 | 566 | 654 | 106.7
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - 9MI1 9 345 | S:PA_HNTL78 | 566 | 654 | 106.7
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - VOL 20 345 | S:PA_HNTL78 | 566 | 654 | 106.7
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 5 MILE - STOLLE 37A 345 | SB:PA230_R3230 | 566 | 654 | 106.69
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL78 | 566 | 654 | 106.69
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R3230 | 566 | 654 | 106.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW - VOL 11 345 | S:PA_HNTL78 | 566 | 654 | 106.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW - VOL 12 345 | S:PA_HNTL78 | 566 | 654 | 106.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - IND 25 345 | S:PA_HNTL78 | 566 | 654 | 106.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OSW 345/115 1TR | S:PA_HNTL78 | 566 | 654 | 106.67
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SCRIBA - FITZ 10 345 | S:PA_HNTL78 | 566 | 654 | 106.65
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - BECK_TSA 345 | SB:PA230_R3230 | 566 | 654 | 106.63
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - BECK_TSB 345 | SB:PA230_R3230 | 566 | 654 | 106.63
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | EDIC - MRCY ue 1-7 345 | S:PA_HNTL78 | 566 | 654 | 106.63
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH 345/115 5TR | SB:PA230_R3230 | 566 | 654 | 106.62
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:SITHE 1 | S:PA_HNTL78 | 566 | 654 | 106.62
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:SITHE 2 | S:PA_HNTL78 | 566 | 654 | 106.62
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - WATERCURE 69 230 | S:PA_HNTL78 | 566 | 654 | 106.61
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - ETWANDA 70 230 | S:PA_HNTL78 | 566 | 654 | 106.61
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:OSWEGO 5 | S:PA_HNTL78 | 566 | 654 | 106.61
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SHLDON - STONYCR 230 | 566 | 654 | 106.57
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LOCKPORT | SB:PA230_R3230 | 566 | 654 | 106.53
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-1 345 | SB:PA230_R3230 | 566 | 654 | 106.53
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1502 | 566 | 654 | 106.5
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH 345/115 5TR | S:PA_HNTL78 | 566 | 654 | 106.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-1 345 | S:PA_HNTL78 | 566 | 654 | 106.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SHLDON - STONYCR 230 | B:PACKT3 | 566 | 654 | 106.4
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SANDY_DC&OMS | 566 | 654 | 106.35
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SANDY_DC | 566 | 654 | 106.35
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:STONY230 | 566 | 654 | 106.29
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ERIE E - 4 MILE 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 106.25
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | T:78&79 | 566 | 654 | 106.15
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 2TR | SB:PA230_R304 | 566 | 654 | 106.14
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DUNK230_R1312 | 566 | 654 | 106.1
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTHRS - MEYER 230 | B:PACKT3 | 566 | 654 | 106.1
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M7TR | SB:PA230_R304 | 566 | 654 | 106.07
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1502 | 566 | 654 | 106.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SHLDON - STONYCR 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 106.05
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:KINTIGH | SB:PA230_R304 | 566 | 654 | 106.03
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-WC_30&W-F_171 | SB:PA230_R3230 | 566 | 654 | 105.96
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - FARMVLY | SB:PA230_R304 | 566 | 654 | 105.95
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DUNKIRK - SRIPL 68 230 | B:PACKT3 | 566 | 654 | 105.95
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SRIPL - ERIE E 69 230 | B:PACKT3 | 566 | 654 | 105.94
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STONYCR - WTHRS 230 | SB:PA230_R3230 | 566 | 654 | 105.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PACKARD 230/115 4TR | SB:PA230_R304 | 566 | 654 | 105.92
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M6TR | SB:PA230_R304 | 566 | 654 | 105.9
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M8TR | SB:PA230_R304 | 566 | 654 | 105.9
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R3230 | 566 | 654 | 105.88
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCWC/NWES | SB:PA230_R3230 | 566 | 654 | 105.86
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:MBWC/NWES | SB:PA230_R3230 | 566 | 654 | 105.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:GINNA | 566 | 654 | 105.78
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:PACKT3 | 566 | 654 | 105.73
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | T:78&79 | 566 | 654 | 105.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 1-3 | SB:PA230_R304 | 566 | 654 | 105.7
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 7-9 | SB:PA230_R304 | 566 | 654 | 105.7
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 10-12 | SB:PA230_R304 | 566 | 654 | 105.7
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 4-6 | SB:PA230_R304 | 566 | 654 | 105.69
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - WTRCR 31 345 | SB:PA230_R304 | 566 | 654 | 105.68
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R304 | 566 | 654 | 105.58
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCMB/NWES | SB:PA230_R304 | 566 | 654 | 105.58
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R304 | 566 | 654 | 105.57
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R304 | 566 | 654 | 105.56
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-MB_30&W-F_171 | SB:PA230_R304 | 566 | 654 | 105.54
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DUNKIRK - SRIPL 68 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 105.49
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SRIPL - ERIE E 69 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 105.47
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:62&BP76 | 566 | 654 | 105.43
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R304 | 566 | 654 | 105.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 105.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:BRUCE5 | 566 | 654 | 105.33
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - ELM 70 230 | SB:PA230_R304 | 566 | 654 | 105.24
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MASS_765_7108 | 566 | 654 | 105.22
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CANDQUA - STNYRDG 68A 230 | 566 | 654 | 105.13
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | S:AVOCA | 566 | 654 | 105.13
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:STONYRIDGE | 566 | 654 | 105.11
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDL - FRASER 32 345 | SB:PA230_R304 | 566 | 654 | 105.02
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MASS_765_7102 | 566 | 654 | 105.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 2TR | SB:PA230_R3230 | 566 | 654 | 104.94
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-WC_30&W-F_171 | S:PA_HNTL78 | 566 | 654 | 104.94
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTRCR - MAINSBRG 30A 345 | S:PA_HNTL78 | 566 | 654 | 104.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCWC/NWES | S:PA_HNTL78 | 566 | 654 | 104.87
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:MBWC/NWES | S:PA_HNTL78 | 566 | 654 | 104.87
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M7TR | SB:PA230_R3230 | 566 | 654 | 104.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 2TR | S:PA_HNTL78 | 566 | 654 | 104.81
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 2TR | S:PA_HNTL78 | 566 | 654 | 104.8
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:KINTIGH | SB:PA230_R3230 | 566 | 654 | 104.78
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - FARMVLY | SB:PA230_R3230 | 566 | 654 | 104.75
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STONYCR - WTHRS 230 | S:PA_HNTL78 | 566 | 654 | 104.75
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - FARMVLY | S:PA_HNTL78 | 566 | 654 | 104.74
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M7TR | S:PA_HNTL78 | 566 | 654 | 104.73
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ERIE E - 4 MILE 230 | 566 | 654 | 104.71
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | WTHRS - MEYER 230 | 566 | 654 | 104.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M6TR | SB:PA230_R3230 | 566 | 654 | 104.67
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M8TR | SB:PA230_R3230 | 566 | 654 | 104.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 104.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:MEYER | 566 | 654 | 104.65
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MEYER - CANDQUA 60 230 | SB:PA230_R304 | 566 | 654 | 104.58
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 1-3 | SB:PA230_R3230 | 566 | 654 | 104.57
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 4-6 | SB:PA230_R3230 | 566 | 654 | 104.57
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 7-9 | SB:PA230_R3230 | 566 | 654 | 104.57
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 10-12 | SB:PA230_R3230 | 566 | 654 | 104.57
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | BECK - PACKARD BP76 230 | S:PA_HNTL78 | 566 | 654 | 104.56
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M6TR | S:PA_HNTL78 | 566 | 654 | 104.53
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M8TR | S:PA_HNTL78 | 566 | 654 | 104.53
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 7-9 | S:PA_HNTL78 | 566 | 654 | 104.53
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 10-12 | S:PA_HNTL78 | 566 | 654 | 104.53
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 1-3 | S:PA_HNTL78 | 566 | 654 | 104.52
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 4-6 | S:PA_HNTL78 | 566 | 654 | 104.52
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - WTRCR 31 345 | SB:PA230_R3230 | 566 | 654 | 104.48
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - WTRCR 31 345 | S:PA_HNTL78 | 566 | 654 | 104.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCMB/NWES | SB:PA230_R3230 | 566 | 654 | 104.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:DARLIN1 | 566 | 654 | 104.36
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R3230 | 566 | 654 | 104.33
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R3230 | 566 | 654 | 104.32
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R3230 | 566 | 654 | 104.31
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-MB_30&W-F_171 | SB:PA230_R3230 | 566 | 654 | 104.31
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R3230 | 566 | 654 | 104.21
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL78 | 566 | 654 | 104.16
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL78 | 566 | 654 | 104.15
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL78 | 566 | 654 | 104.14
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 1 | SB:PA230_R304 | 566 | 654 | 104.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 2 | SB:PA230_R304 | 566 | 654 | 104.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 3 | SB:PA230_R304 | 566 | 654 | 104.08
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:KINTIGH | S:PA_HNTL78 | 566 | 654 | 104.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - ELM 70 230 | SB:PA230_R3230 | 566 | 654 | 104.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:SCRIBA_R925 | 566 | 654 | 103.98
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:SCRIBA_R230 | 566 | 654 | 103.98
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:9 MI PT2 | 566 | 654 | 103.98
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | B:Hunt68 | 566 | 654 | 103.97
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:GINNA | SB:PA230_R304 | 566 | 654 | 103.93
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 11 | SB:PA230_R304 | 566 | 654 | 103.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 12 | SB:PA230_R304 | 566 | 654 | 103.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 13 | SB:PA230_R304 | 566 | 654 | 103.86
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ERIE E - 4 MILE 230 | SB:PA230_R304 | 566 | 654 | 103.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 8 | SB:PA230_R304 | 566 | 654 | 103.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 9 | SB:PA230_R304 | 566 | 654 | 103.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 10 | SB:PA230_R304 | 566 | 654 | 103.84
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - ELM 70 230 | S:PA_HNTL78 | 566 | 654 | 103.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDL - FRASER 32 345 | SB:PA230_R3230 | 566 | 654 | 103.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | B:Hunt68 | 566 | 654 | 103.78
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDL - FRASER 32 345 | S:PA_HNTL78 | 566 | 654 | 103.73
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/NWES | 566 | 654 | 103.6
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SRIPL - ERIE E 69 230 | 566 | 654 | 103.57
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1402 | 566 | 654 | 103.56
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | DUNKIRK - SRIPL 68 230 | 566 | 654 | 103.55
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:SRIPLEY | 566 | 654 | 103.55
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SHLDON - STONYCR 230 | SB:PA230_R304 | 566 | 654 | 103.51
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | B:Hunt68 | 566 | 654 | 103.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 1 | S:PA_HNTL78 | 566 | 654 | 103.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 2 | S:PA_HNTL78 | 566 | 654 | 103.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 3 | S:PA_HNTL78 | 566 | 654 | 103.43
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STONYCR - WTHRS 230 | B:PACKT3 | 566 | 654 | 103.41
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1402 | 566 | 654 | 103.39
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCMB/NWES | S:PA_HNTL78 | 566 | 654 | 103.39
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - PACKARD 62 230 | S:PA_HNTL78 | 566 | 654 | 103.38
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-WC_30&W-F_171 | B:PACKT3 | 566 | 654 | 103.36
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - PACKARD 61 230 | S:PA_HNTL78 | 566 | 654 | 103.31
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-MB_30&W-F_171 | S:PA_HNTL78 | 566 | 654 | 103.3
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MEYER - CANDQUA 60 230 | SB:PA230_R3230 | 566 | 654 | 103.29
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTRCR - MAINSBRG 30A 345 | B:PACKT3 | 566 | 654 | 103.27
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTHRS - MEYER 230 | SB:PA230_R304 | 566 | 654 | 103.27
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCWC/NWES | B:PACKT3 | 566 | 654 | 103.24
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:MBWC/NWES | B:PACKT3 | 566 | 654 | 103.24
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | STONYCR - WTHRS 230 | 566 | 654 | 103.23
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MAINSBRG - HOMERCITY 30B 345 | S:PA_HNTL78 | 566 | 654 | 103.23
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | BECK - PACKARD BP76 230 | SB:PA230_R3230 | 566 | 654 | 103.16
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 1 | SB:PA230_R3230 | 566 | 654 | 103.16
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 2 | SB:PA230_R3230 | 566 | 654 | 103.16
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 3 | SB:PA230_R3230 | 566 | 654 | 103.16
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MEYER - CANDQUA 60 230 | S:PA_HNTL78 | 566 | 654 | 103.15
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-WC_30&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 103.14
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DUNKIRK - SRIPL 68 230 | SB:PA230_R304 | 566 | 654 | 103.12
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SRIPL - ERIE E 69 230 | SB:PA230_R304 | 566 | 654 | 103.1
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1402 | 566 | 654 | 103.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTRCR - MAINSBRG 30A 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 103.04
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCWC/NWES | HUNTLEY - PACKARD 78 230 | 566 | 654 | 103.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:MBWC/NWES | HUNTLEY - PACKARD 78 230 | 566 | 654 | 103.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STONYCR - WTHRS 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 103
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1502 | 566 | 654 | 102.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WTHERS230 | 566 | 654 | 102.81
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R304 | 566 | 654 | 102.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 11 | S:PA_HNTL78 | 566 | 654 | 102.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 12 | S:PA_HNTL78 | 566 | 654 | 102.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 13 | S:PA_HNTL78 | 566 | 654 | 102.79
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 8 | S:PA_HNTL78 | 566 | 654 | 102.78
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 9 | S:PA_HNTL78 | 566 | 654 | 102.78
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 10 | S:PA_HNTL78 | 566 | 654 | 102.77
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 11 | SB:PA230_R3230 | 566 | 654 | 102.77
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 12 | SB:PA230_R3230 | 566 | 654 | 102.77
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 13 | SB:PA230_R3230 | 566 | 654 | 102.77
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 8 | SB:PA230_R3230 | 566 | 654 | 102.77
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 9 | SB:PA230_R3230 | 566 | 654 | 102.77
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 10 | SB:PA230_R3230 | 566 | 654 | 102.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:GINNA | SB:PA230_R3230 | 566 | 654 | 102.7
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:GINNA | S:PA_HNTL78 | 566 | 654 | 102.6
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | T:78&79 | 566 | 654 | 102.51
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:DUNKG4 | 566 | 654 | 102.5
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ERIE E - 4 MILE 230 | SB:PA230_R3230 | 566 | 654 | 102.42
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:KINTIGH | HUNTLEY - PACKARD 78 230 | 566 | 654 | 102.31
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | B:Hunt68 | 566 | 654 | 102.17
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SHLDON - STONYCR 230 | SB:PA230_R3230 | 566 | 654 | 102.14
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GEN:KINTIGH | B:PACKT3 | 566 | 654 | 102.12
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ERIE E - 4 MILE 230 | S:PA_HNTL78 | 566 | 654 | 102.1
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/WF/NWES | 566 | 654 | 102.07
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:DKSR/WRFL | 566 | 654 | 102.07
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/WRFL | 566 | 654 | 102.06
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 80 230 | B:PACKT3 | 566 | 654 | 102.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SHLDON - STONYCR 230 | S:PA_HNTL78 | 566 | 654 | 101.94
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | B:Hunt68 | 566 | 654 | 101.94
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1402 | 566 | 654 | 101.8
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | B:PACKT3 | 566 | 654 | 101.79
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTHRS - MEYER 230 | SB:PA230_R3230 | 566 | 654 | 101.77
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCMB/NWES | B:PACKT3 | 566 | 654 | 101.76
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-MB_30&W-F_171 | B:PACKT3 | 566 | 654 | 101.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DUNKIRK - SRIPL 68 230 | SB:PA230_R3230 | 566 | 654 | 101.67
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SRIPL - ERIE E 69 230 | SB:PA230_R3230 | 566 | 654 | 101.65
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MAINSBRG - HOMERCITY 30B 345 | B:PACKT3 | 566 | 654 | 101.61
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1402 | 566 | 654 | 101.56
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCMB/NWES | HUNTLEY - PACKARD 78 230 | 566 | 654 | 101.54
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-MB_30&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 101.47
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:KINTIGH | 566 | 654 | 101.47
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:68&160 | 566 | 654 | 101.45
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R3230 | 566 | 654 | 101.4
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | MAINSBRG - HOMERCITY 30B 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 101.39
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SRIPL - ERIE E 69 230 | S:PA_HNTL78 | 566 | 654 | 101.35
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DUNKIRK - SRIPL 68 230 | S:PA_HNTL78 | 566 | 654 | 101.34
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_R833 | 566 | 654 | 101.25
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:GARD72&79 | 566 | 654 | 101.22
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL78 | 566 | 654 | 101.19
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:73&74 | 566 | 654 | 101.14
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1502 | 566 | 654 | 101.13
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1502 | 566 | 654 | 100.84
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | T:78&79 | 566 | 654 | 100.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STONYCR - WTHRS 230 | SB:PA230_R304 | 566 | 654 | 100.61
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTHRS - MEYER 230 | S:PA_HNTL78 | 566 | 654 | 100.55
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | T:78&79 | 566 | 654 | 100.54
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-WC_30&W-F_171 | SB:PA230_R304 | 566 | 654 | 100.44
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1502 | 566 | 654 | 100.38
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R304 | 566 | 654 | 100.33
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DUNK230_R1312 | 566 | 654 | 100.32
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HCWC/NWES | SB:PA230_R304 | 566 | 654 | 100.3
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:MBWC/NWES | SB:PA230_R304 | 566 | 654 | 100.3
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | SB:HUNT230_R1502 | 566 | 654 | 100.21
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:78&79 | 566 | 654 | 100.05
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 140.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3230 | 556 | 644 | 152.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 556 | 644 | 152.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 556 | 644 | 149.92
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL78 | 556 | 644 | 148.94
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R304 | 556 | 644 | 148.79
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 148.69
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 230 | 556 | 644 | 148.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3230 | 556 | 644 | 148.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 556 | 644 | 147.9
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 556 | 644 | 147.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3230 | 556 | 644 | 146.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 556 | 644 | 146.82
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 556 | 644 | 146.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 556 | 644 | 146.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 145.91
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 556 | 644 | 145.33
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3230 | 556 | 644 | 145.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 556 | 644 | 145.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 556 | 644 | 145.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 145
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 556 | 644 | 144.98
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R304 | 556 | 644 | 144.76
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_T7-12 | 556 | 644 | 143.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R304 | 556 | 644 | 143.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3230 | 556 | 644 | 143.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 556 | 644 | 142.97
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 556 | 644 | 142.96
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 556 | 644 | 142.84
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3230 | 556 | 644 | 142.72
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 142.58
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 556 | 644 | 142.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 556 | 644 | 141.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL78 | 556 | 644 | 141.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R304 | 556 | 644 | 141.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 140.91
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 230 | 556 | 644 | 140.83
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3230 | 556 | 644 | 140.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 556 | 644 | 140.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B302 | 556 | 644 | 140.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAG345_3108 | 556 | 644 | 140.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - NEWROCH 1 345 | 556 | 644 | 140.37
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 556 | 644 | 140.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 556 | 644 | 140.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 140.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R304 | 556 | 644 | 139.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 556 | 644 | 139.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3230 | 556 | 644 | 139.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 139.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 556 | 644 | 139.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B202 | 556 | 644 | 139
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | SB:PA230_R3230 | 556 | 644 | 138.95
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SOMERSET - NEWROCH 1 345 | 556 | 644 | 138.91
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R304 | 556 | 644 | 138.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 556 | 644 | 138.85
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 556 | 644 | 138.81
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | B:PACKT3 | 556 | 644 | 138.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 138.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 556 | 644 | 138.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3230 | 556 | 644 | 137.8
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 556 | 644 | 137.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_T7-12 | 556 | 644 | 137.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R304 | 556 | 644 | 137.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 556 | 644 | 136.61
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 136.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R304 | 556 | 644 | 136.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:40&41 | 556 | 644 | 135.97
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3230 | 556 | 644 | 135.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | B:PACKT3 | 556 | 644 | 135.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | SB:PA230_R304 | 556 | 644 | 135.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3230 | 556 | 644 | 135.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 556 | 644 | 134.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R3230 | 556 | 644 | 134.74
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - HOMERCTY | 556 | 644 | 134.72
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL78 | 556 | 644 | 134.69
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-FV_37&W-F_171 | 556 | 644 | 134.61
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:41&33 | 556 | 644 | 134.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT3 | 556 | 644 | 134.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B302 | 556 | 644 | 134.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAG345_3108 | 556 | 644 | 134.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - NEWROCH 1 345 | 556 | 644 | 134.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 134.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAW230_2014 | 556 | 644 | 134.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 556 | 644 | 134.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R304 | 556 | 644 | 133.76
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL78 | 556 | 644 | 133.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 133.68
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:34&42 | 556 | 644 | 133.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 133.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA 230/115 1TR | 556 | 644 | 133.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_2 | 556 | 644 | 133.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_1 | 556 | 644 | 133.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | LFYTE - CLARKCRNS 36A 345 | 556 | 644 | 133.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAFA_ELB | 556 | 644 | 133.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAFAYETT | 556 | 644 | 133.1
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | S:PA_HNTL78 | 556 | 644 | 132.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B202 | 556 | 644 | 132.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SOMERSET - NEWROCH 1 345 | 556 | 644 | 132.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 132.72
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_3 | 556 | 644 | 132.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_4 | 556 | 644 | 132.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | PACKARD 230/115 3TR | 556 | 644 | 132.46
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B5 | 556 | 644 | 132.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B6 | 556 | 644 | 132.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - CLARKCRNS 36B 345 | 556 | 644 | 132.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE_B | 556 | 644 | 132.25
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R3230 | 556 | 644 | 132.15
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | SB:PA230_R3230 | 556 | 644 | 132
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R304 | 556 | 644 | 131.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | B:PACKT3 | 556 | 644 | 131.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | S:PA_HNTL78 | 556 | 644 | 131.84
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | SB:PA230_R3230 | 556 | 644 | 131.81
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | B:PACKT3 | 556 | 644 | 131.78
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:31&41 | 556 | 644 | 131.74
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_42-4182 | 556 | 644 | 131.7
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | B:PACKT3 | 556 | 644 | 131.63
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 131.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3208 | 556 | 644 | 131.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R915 | 556 | 644 | 131.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:MP11&41 | 556 | 644 | 131.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_4182 | 556 | 644 | 131.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3202 | 556 | 644 | 131.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - COOPERS 345 SC | 556 | 644 | 131.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R304 | 556 | 644 | 131.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:30&40 | 556 | 644 | 131.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | SB:PA230_R3230 | 556 | 644 | 131.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R304 | 556 | 644 | 131.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAG345_3308 | 556 | 644 | 130.97
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1502 | 556 | 644 | 130.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | B:PACKT3 | 556 | 644 | 130.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | S:PA_HNTL78 | 556 | 644 | 130.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:77&76 | 556 | 644 | 130.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R400 | 556 | 644 | 130.86
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - KINTIGH 345 | 556 | 644 | 130.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | S:PA_HNTL78 | 556 | 644 | 130.82
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | SB:PA230_R3230 | 556 | 644 | 130.69
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R935 | 556 | 644 | 130.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FRASER 345 SC | 556 | 644 | 130.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:FRAS345_B1-4062 | 556 | 644 | 130.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:FRAS345_40-B262 | 556 | 644 | 130.61
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 130.59
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | T:78&79 | 556 | 644 | 130.59
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | S:PA_HNTL78 | 556 | 644 | 130.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 78 230 | 556 | 644 | 130.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | B:PACKT3 | 556 | 644 | 130.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R3230 | 556 | 644 | 130.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R3230 | 556 | 644 | 130.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 130.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:69J&70K | 556 | 644 | 130.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3230 | 556 | 644 | 130.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:170 | 556 | 644 | 130.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:180 | 556 | 644 | 130.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | SB:PA230_R3230 | 556 | 644 | 130.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:40&41 | 556 | 644 | 130.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:90 | 556 | 644 | 130.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._99 | 556 | 644 | 130.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | S:PA_HNTL78 | 556 | 644 | 130.15
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE | 556 | 644 | 130.11
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._77 | 556 | 644 | 130.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL78 | 556 | 644 | 130.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3308 | 556 | 644 | 130.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:MP12&18 | 556 | 644 | 130.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:160 | 556 | 644 | 130.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:150 | 556 | 644 | 130.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_3414 | 556 | 644 | 130.03
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_3514 | 556 | 644 | 130.03
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | B:PACKT3 | 556 | 644 | 130.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | B:PACKT3 | 556 | 644 | 130.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:PECHBTM2 | 556 | 644 | 130.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:W89&W90 | 556 | 644 | 130.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | B:PACKT3 | 556 | 644 | 130.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | B:PACKT3 | 556 | 644 | 129.98
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R140 | 556 | 644 | 129.97
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1502 | 556 | 644 | 129.95
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3314 | 556 | 644 | 129.92
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - N.SCOT99 I8 345 | 556 | 644 | 129.92
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:F38&F39 | 556 | 644 | 129.92
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | SB:PA230_R3230 | 556 | 644 | 129.91
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 129.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R3230 | 556 | 644 | 129.86
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SUSQ1 | 556 | 644 | 129.82
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_2T8082 | 556 | 644 | 129.81
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3108 | 556 | 644 | 129.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - N.SCOT77 I4 345 | 556 | 644 | 129.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 129.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:F30&F31 | 556 | 644 | 129.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-SR_37&W-F_171 | 556 | 644 | 129.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:FV-5M_37&W-F_171 | 556 | 644 | 129.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_376512 | 556 | 644 | 129.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | SB:PA230_R3230 | 556 | 644 | 129.71
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - 5MILE 345 | 556 | 644 | 129.71
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_31153 | 556 | 644 | 129.7
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | B:PACKT3 | 556 | 644 | 129.7
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | S:PA_HNTL78 | 556 | 644 | 129.7
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_34XC | 556 | 644 | 129.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R935 | 556 | 644 | 129.64
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | SB:PA230_R3230 | 556 | 644 | 129.63
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R945 | 556 | 644 | 129.63
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PV345_RNS5 | 556 | 644 | 129.63
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | B:PACKT3 | 556 | 644 | 129.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R3230 | 556 | 644 | 129.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PV345_RNS4 | 556 | 644 | 129.61
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | T:78&79 | 556 | 644 | 129.6
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LEEDS345_R9293 | 556 | 644 | 129.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SALEMG1 | 556 | 644 | 129.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 4 | SB:PA230_R3230 | 556 | 644 | 129.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 5 | SB:PA230_R3230 | 556 | 644 | 129.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 6 | SB:PA230_R3230 | 556 | 644 | 129.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:HOPECG1 | 556 | 644 | 129.53
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 7 | SB:PA230_R3230 | 556 | 644 | 129.53
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:LIMERCK2 | 556 | 644 | 129.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_3456 | 556 | 644 | 129.5
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | SB:PA230_R3230 | 556 | 644 | 129.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_34-B382 | 556 | 644 | 129.45
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_B2-3482 | 556 | 644 | 129.45
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HURLEY - ROCKT CMT/MTR-34 345 | 556 | 644 | 129.45
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CMT/MTR-34 345 | 556 | 644 | 129.45
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | HUNTLEY - PACKARD 78 230 | 556 | 644 | 129.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R3230 | 556 | 644 | 129.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R3230 | 556 | 644 | 129.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R150 | 556 | 644 | 129.37
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3908 | 556 | 644 | 129.37
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R160 | 556 | 644 | 129.37
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R3230 | 556 | 644 | 129.37
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3808 | 556 | 644 | 129.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | B:PACKT3 | 556 | 644 | 129.34
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 4 | B:PACKT3 | 556 | 644 | 129.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 5 | B:PACKT3 | 556 | 644 | 129.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 6 | B:PACKT3 | 556 | 644 | 129.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 7 | B:PACKT3 | 556 | 644 | 129.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | B:PACKT3 | 556 | 644 | 129.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | B:PACKT3 | 556 | 644 | 129.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - DEW 13 345 | 556 | 644 | 129.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LEEDS345_R94301 | 556 | 644 | 129.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | B:PACKT3 | 556 | 644 | 129.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - BECK_TSA 345 | SB:PA230_R3230 | 556 | 644 | 129.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - BECK_TSB 345 | SB:PA230_R3230 | 556 | 644 | 129.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R110 | 556 | 644 | 129.27
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH 345/115 5TR | SB:PA230_R3230 | 556 | 644 | 129.27
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_4255 | 556 | 644 | 129.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3230 | 556 | 644 | 129.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT3 | 556 | 644 | 129.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R150 | 556 | 644 | 129.25
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | SB:PA230_R3230 | 556 | 644 | 129.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R3230 | 556 | 644 | 129.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R160 | 556 | 644 | 129.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_B2-4282 | 556 | 644 | 129.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 644 | 129.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 644 | 129.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 1-16 345 | 556 | 644 | 129.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 556 | 644 | 129.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 556 | 644 | 129.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | SB:PA230_R3230 | 556 | 644 | 129.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R10 | 556 | 644 | 129.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DUNW345_3 | 556 | 644 | 129.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | SB:PA230_R3230 | 556 | 644 | 129.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | B:PACKT3 | 556 | 644 | 129.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | B:PACKT3 | 556 | 644 | 129.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | B:PACKT3 | 556 | 644 | 129.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | S:PA_HNTL78 | 556 | 644 | 129.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 4TR | SB:PA230_R3230 | 556 | 644 | 129.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 556 | 644 | 129.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LEEDS345_R92 | 556 | 644 | 129.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 556 | 644 | 129.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3102 | 556 | 644 | 129.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LOCKPORT | SB:PA230_R3230 | 556 | 644 | 129.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 556 | 644 | 129.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 556 | 644 | 129.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DUNW345_8 | 556 | 644 | 129.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FITZ 345 | 556 | 644 | 129.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FITZ - EDIC FEI 345 | 556 | 644 | 129.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DEWI345_R915 | 556 | 644 | 129.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DEWI345_R130 | 556 | 644 | 129.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DEWI345_R220 | 556 | 644 | 129.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - BECK_TSA 345 | B:PACKT3 | 556 | 644 | 129.1
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - BECK_TSB 345 | B:PACKT3 | 556 | 644 | 129.1
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH 345/115 5TR | B:PACKT3 | 556 | 644 | 129.1
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | VOLNEY - MARCY I9 345 | 556 | 644 | 129.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | VOL - MARCY 19 345 | 556 | 644 | 129.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:VOLN_R925 | 556 | 644 | 129.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL78 | 556 | 644 | 129.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | B:PACKT3 | 556 | 644 | 129.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3914 | 556 | 644 | 129.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3814 | 556 | 644 | 129.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | B:PACKT3 | 556 | 644 | 129.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | B:PACKT3 | 556 | 644 | 129.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 4TR | B:PACKT3 | 556 | 644 | 129
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT3 | 556 | 644 | 128.98
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 128.92
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | S:PA_HNTL78 | 556 | 644 | 128.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - HOMERCTY | 556 | 644 | 128.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | S:PA_HNTL78 | 556 | 644 | 128.82
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | S:PA_HNTL78 | 556 | 644 | 128.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-FV_37&W-F_171 | 556 | 644 | 128.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 128.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:41&33 | 556 | 644 | 128.69
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 128.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | S:PA_HNTL78 | 556 | 644 | 128.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R304 | 556 | 644 | 128.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 128.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 128.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | S:PA_HNTL78 | 556 | 644 | 128.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | SB:PA230_R304 | 556 | 644 | 128.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL78 | 556 | 644 | 128.39
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | S:PA_HNTL78 | 556 | 644 | 128.38
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | S:PA_HNTL78 | 556 | 644 | 128.38
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1502 | 556 | 644 | 128.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 128.25
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | S:PA_HNTL78 | 556 | 644 | 128.25
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | S:PA_HNTL78 | 556 | 644 | 128.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | S:PA_HNTL78 | 556 | 644 | 128.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | S:PA_HNTL78 | 556 | 644 | 128.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 128.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | S:PA_HNTL78 | 556 | 644 | 128.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | S:PA_HNTL78 | 556 | 644 | 128.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | SB:PA230_R304 | 556 | 644 | 128.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 128.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 128.11
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 128.11
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 127.98
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | T:78&79 | 556 | 644 | 127.92
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 127.92
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 127.91
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:34&42 | 556 | 644 | 127.77
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | SB:PA230_R3230 | 556 | 644 | 127.53
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | SB:PA230_R304 | 556 | 644 | 127.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDL - FRASER 32 345 | 556 | 644 | 127.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FRASER - OAKDLE 32 345 | 556 | 644 | 127.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | SB:PA230_R3230 | 556 | 644 | 127.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT2 | 556 | 644 | 127.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RAIN345_1W | 556 | 644 | 127.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:FRAS345_B1-3262 | 556 | 644 | 127.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RAIN345_9W | 556 | 644 | 127.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | SB:PA230_R3230 | 556 | 644 | 127.39
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: RAVENSWOOD | 556 | 644 | 127.38
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:30 | 556 | 644 | 127.38
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | BWLN - WHAV -LDN 67 345 | 556 | 644 | 127.38
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT1 | 556 | 644 | 127.38
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B2 | 556 | 644 | 127.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | B:PACKT3 | 556 | 644 | 127.35
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAFA_ELB | 556 | 644 | 127.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_2 | 556 | 644 | 127.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_1 | 556 | 644 | 127.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 2TR | 556 | 644 | 127.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | LFYTE - CLARKCRNS 36A 345 | 556 | 644 | 127.27
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROSE345_30553 | 556 | 644 | 127.27
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_4-56-2 | 556 | 644 | 127.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_1-56-2 | 556 | 644 | 127.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | B:PACKT3 | 556 | 644 | 127.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAFAYETT | 556 | 644 | 127.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | B:PACKT3 | 556 | 644 | 127.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_6-56-2 | 556 | 644 | 127.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | SB:PA230_R3230 | 556 | 644 | 127.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | SB:PA230_R3230 | 556 | 644 | 127.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | SB:PA230_R3230 | 556 | 644 | 127.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | SB:PA230_R3230 | 556 | 644 | 127.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | SB:PA230_R3230 | 556 | 644 | 127.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | SB:PA230_R3230 | 556 | 644 | 127.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - WTRCR 31 345 | 556 | 644 | 127.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B3 | 556 | 644 | 127.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_3-56-2 | 556 | 644 | 127.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:NOEND | 556 | 644 | 127.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROSE345_30551 | 556 | 644 | 127.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M7TR | 556 | 644 | 127.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROSE345_31152 | 556 | 644 | 127.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RMP345_T1500 | 556 | 644 | 127.1
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WATRC345_31-2 | 556 | 644 | 127.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | RAMAPO - BRNCHBRG 5018 345 | 556 | 644 | 127.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON2 | 556 | 644 | 127.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | SB:PA230_R304 | 556 | 644 | 127.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2208 | 556 | 644 | 127.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RMP345_1500-2X | 556 | 644 | 127.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2214 | 556 | 644 | 127.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS17-20 | 556 | 644 | 127.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2224 | 556 | 644 | 127.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1724 | 556 | 644 | 127.03
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1714 | 556 | 644 | 127.03
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1524 | 556 | 644 | 127.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1514 | 556 | 644 | 127.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1508 | 556 | 644 | 127.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2524 | 556 | 644 | 127.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2514 | 556 | 644 | 127.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS21-24 | 556 | 644 | 127.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2508 | 556 | 644 | 127.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | B:PACKT3 | 556 | 644 | 127.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | B:PACKT3 | 556 | 644 | 127.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | B:PACKT3 | 556 | 644 | 127.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | B:PACKT3 | 556 | 644 | 127
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | B:PACKT3 | 556 | 644 | 126.99
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | B:PACKT3 | 556 | 644 | 126.99
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R3230 | 556 | 644 | 126.99
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R3230 | 556 | 644 | 126.97
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R3230 | 556 | 644 | 126.96
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | SB:PA230_R3230 | 556 | 644 | 126.94
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON1 | 556 | 644 | 126.94
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M8TR | 556 | 644 | 126.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M6TR | 556 | 644 | 126.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3208 | 556 | 644 | 126.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R304 | 556 | 644 | 126.84
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R304 | 556 | 644 | 126.84
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:AT_R6361 | 556 | 644 | 126.81
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BESICORP | 556 | 644 | 126.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:EMPIRE | 556 | 644 | 126.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | B:PACKT3 | 556 | 644 | 126.77
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | B:PACKT3 | 556 | 644 | 126.76
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | B:PACKT3 | 556 | 644 | 126.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | B:PACKT3 | 556 | 644 | 126.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:EMPIRE | 556 | 644 | 126.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: IND PT 2 | 556 | 644 | 126.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN GILBOA #3&4 | 556 | 644 | 126.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3302 | 556 | 644 | 126.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:72&69 | 556 | 644 | 126.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_3 | 556 | 644 | 126.59
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_4 | 556 | 644 | 126.59
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R304 | 556 | 644 | 126.58
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN GILBOA #1&2 | 556 | 644 | 126.58
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3202 | 556 | 644 | 126.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3308 | 556 | 644 | 126.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | SB:PA230_R304 | 556 | 644 | 126.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHN_11 | 556 | 644 | 126.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHN_9 | 556 | 644 | 126.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:NTHF3&4 | 556 | 644 | 126.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHN_7 | 556 | 644 | 126.53
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | SB:PA230_R3230 | 556 | 644 | 126.53
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - FARMVLY | 556 | 644 | 126.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | S:PA_HNTL78 | 556 | 644 | 126.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | BECK - PACKARD BP76 230 | 556 | 644 | 126.49
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | SB:PA230_R3230 | 556 | 644 | 126.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | SB:PA230_R3230 | 556 | 644 | 126.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | SB:PA230_R3230 | 556 | 644 | 126.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | S:PA_HNTL78 | 556 | 644 | 126.46
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: IND PT 3 | 556 | 644 | 126.46
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B5 | 556 | 644 | 126.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHS_1 | 556 | 644 | 126.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHS_3 | 556 | 644 | 126.41
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B6 | 556 | 644 | 126.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - CLARKCRNS 36B 345 | 556 | 644 | 126.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE_B | 556 | 644 | 126.38
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | B:PACKT3 | 556 | 644 | 126.37
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R304 | 556 | 644 | 126.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | S:PA_HNTL78 | 556 | 644 | 126.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:67&68&BW | 556 | 644 | 126.33
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | SB:PA230_R304 | 556 | 644 | 126.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | B:PACKT3 | 556 | 644 | 126.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | B:PACKT3 | 556 | 644 | 126.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | B:PACKT3 | 556 | 644 | 126.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HILLSIDE 230/115 4TR | 556 | 644 | 126.27
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:HILLSIDE | 556 | 644 | 126.27
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:HILL_B412 | 556 | 644 | 126.27
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 126.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | S:PA_HNTL78 | 556 | 644 | 126.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | S:PA_HNTL78 | 556 | 644 | 126.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | S:PA_HNTL78 | 556 | 644 | 126.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | S:PA_HNTL78 | 556 | 644 | 126.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | S:PA_HNTL78 | 556 | 644 | 126.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | HUNTLEY - PACKARD 78 230 | 556 | 644 | 126.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:SITHE 2 | 556 | 644 | 126.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:SITHE 1 | 556 | 644 | 126.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:BETHSTM | 556 | 644 | 126.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - ELM 70 230 | 556 | 644 | 126.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | S:PA_HNTL78 | 556 | 644 | 126.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | S:PA_HNTL78 | 556 | 644 | 126.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | SB:PA230_R304 | 556 | 644 | 126.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HCWC/NWES | 556 | 644 | 126.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:MBWC/NWES | 556 | 644 | 126.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | WTRCR - MAINSBRG 30A 345 | 556 | 644 | 126.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WATRC345_30-3142 | 556 | 644 | 126.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 126.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WATRC345_B1-3042 | 556 | 644 | 126.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:HILL_68-B412 | 556 | 644 | 126.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:130 | 556 | 644 | 126.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:120_130 | 556 | 644 | 126.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:W97&W98 | 556 | 644 | 126.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | SB:PA230_R304 | 556 | 644 | 126.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R304 | 556 | 644 | 126.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STNYRDG - HILLSIDE 68B 230 | 556 | 644 | 126.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-WC_30&W-F_171 | 556 | 644 | 125.98
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL78 | 556 | 644 | 125.92
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | SB:PA230_R3230 | 556 | 644 | 125.9
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | SB:PA230_R3230 | 556 | 644 | 125.9
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL78 | 556 | 644 | 125.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL78 | 556 | 644 | 125.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | SB:PA230_R304 | 556 | 644 | 125.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 4 | SB:PA230_R304 | 556 | 644 | 125.84
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 5 | SB:PA230_R304 | 556 | 644 | 125.84
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 6 | SB:PA230_R304 | 556 | 644 | 125.84
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 7 | SB:PA230_R304 | 556 | 644 | 125.84
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:31&41 | 556 | 644 | 125.83
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R304 | 556 | 644 | 125.82
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R304 | 556 | 644 | 125.81
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R304 | 556 | 644 | 125.81
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_42-4182 | 556 | 644 | 125.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HCMB/NWES | 556 | 644 | 125.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R304 | 556 | 644 | 125.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL - DUNKIRK 73 230 | 556 | 644 | 125.78
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:DUNKG3 | 556 | 644 | 125.76
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL - DUNKIRK 74 230 | 556 | 644 | 125.76
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MAINSBRG - HOMERCITY 30B 345 | 556 | 644 | 125.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | B:PACKT3 | 556 | 644 | 125.71
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | B:PACKT3 | 556 | 644 | 125.71
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH 345/115 5TR | SB:PA230_R304 | 556 | 644 | 125.69
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | S:PA_HNTL78 | 556 | 644 | 125.69
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | S:PA_HNTL78 | 556 | 644 | 125.69
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | S:PA_HNTL78 | 556 | 644 | 125.69
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | SB:PA230_R304 | 556 | 644 | 125.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-MB_30&W-F_171 | 556 | 644 | 125.64
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.64
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | SB:PA230_R304 | 556 | 644 | 125.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | SB:PA230_R304 | 556 | 644 | 125.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.61
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R304 | 556 | 644 | 125.6
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.6
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:KINT_39-B112 | 556 | 644 | 125.59
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3208 | 556 | 644 | 125.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | SB:PA230_R3230 | 556 | 644 | 125.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:KINT_B1-3812 | 556 | 644 | 125.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R915 | 556 | 644 | 125.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:MP11&41 | 556 | 644 | 125.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:PA27&BP76 | 556 | 644 | 125.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R3230 | 556 | 644 | 125.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | S:PA_HNTL78 | 556 | 644 | 125.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_4182 | 556 | 644 | 125.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3202 | 556 | 644 | 125.39
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | B:PACKT3 | 556 | 644 | 125.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - COOPERS 345 SC | 556 | 644 | 125.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:61&191 | 556 | 644 | 125.34
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | SB:PA230_R3230 | 556 | 644 | 125.33
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | SB:PA230_R3230 | 556 | 644 | 125.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | SB:PA230_R3230 | 556 | 644 | 125.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:30&40 | 556 | 644 | 125.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | B:PACKT3 | 556 | 644 | 125.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 125.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - PACKARD 62 230 | 556 | 644 | 125.13
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | PACKARD 230/115 3TR | 556 | 644 | 125.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | SB:PA230_R3230 | 556 | 644 | 125.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | S:PA_HNTL78 | 556 | 644 | 125.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | B:PACKT3 | 556 | 644 | 125.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | B:PACKT3 | 556 | 644 | 125.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | B:PACKT3 | 556 | 644 | 125.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - PACKARD 61 230 | 556 | 644 | 125.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | S:PA_HNTL78 | 556 | 644 | 124.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:77&76 | 556 | 644 | 124.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:62&PA27 | 556 | 644 | 124.96
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R400 | 556 | 644 | 124.95
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R955 | 556 | 644 | 124.95
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:OSWEGO 5 | 556 | 644 | 124.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R965 | 556 | 644 | 124.91
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | S:PA_HNTL78 | 556 | 644 | 124.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | SB:PA230_R3230 | 556 | 644 | 124.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | B:PACKT3 | 556 | 644 | 124.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAG345_3308 | 556 | 644 | 124.84
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | S:PA_HNTL78 | 556 | 644 | 124.84
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CNDGUA | 556 | 644 | 124.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA 230/115 1TR | 556 | 644 | 124.78
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:250 | 556 | 644 | 124.78
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:MILLST3 | 556 | 644 | 124.78
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:MLS3&OMS | 556 | 644 | 124.78
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MEYER - CANDQUA 60 230 | 556 | 644 | 124.77
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | SB:PA230_R3230 | 556 | 644 | 124.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - KINTIGH 345 | 556 | 644 | 124.74
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R935 | 556 | 644 | 124.74
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 124.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FRASER 345 SC | 556 | 644 | 124.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:FRAS345_B1-4062 | 556 | 644 | 124.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:FRAS345_40-B262 | 556 | 644 | 124.7
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1502 | 556 | 644 | 124.7
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:FRGT/WRFL | 556 | 644 | 124.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 78 230 | 556 | 644 | 124.63
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R925 | 556 | 644 | 124.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 124.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:OSWEGO 6 | 556 | 644 | 124.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | B:PACKT3 | 556 | 644 | 124.59
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | B:PACKT3 | 556 | 644 | 124.59
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:9MIPT1 | 556 | 644 | 124.58
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R935 | 556 | 644 | 124.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 124.57
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1502 | 556 | 644 | 124.5
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | S:PA_HNTL78 | 556 | 644 | 124.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1502 | 556 | 644 | 124.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | S:PA_HNTL78 | 556 | 644 | 124.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:90 | 556 | 644 | 124.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE | 556 | 644 | 124.46
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | S:PA_HNTL78 | 556 | 644 | 124.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | SB:PA230_R3230 | 556 | 644 | 124.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | S:PA_HNTL78 | 556 | 644 | 124.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:FITZPATR | 556 | 644 | 124.37
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | T:78&79 | 556 | 644 | 124.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | SB:PA230_R3230 | 556 | 644 | 124.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:69J&70K | 556 | 644 | 124.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:170 | 556 | 644 | 124.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:180 | 556 | 644 | 124.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | SB:PA230_R3230 | 556 | 644 | 124.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SEABROOK | 556 | 644 | 124.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SEAB&OMS | 556 | 644 | 124.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | SB:PA230_R3230 | 556 | 644 | 124.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | S:PA_HNTL78 | 556 | 644 | 124.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | S:PA_HNTL78 | 556 | 644 | 124.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 124.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._99 | 556 | 644 | 124.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | S:PA_HNTL78 | 556 | 644 | 124.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | T:78&79 | 556 | 644 | 124.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | B:PACKT3 | 556 | 644 | 124.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._77 | 556 | 644 | 124.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC_765_7402 | 556 | 644 | 124.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MSU1_7202>7214>7208>7214 | 556 | 644 | 124.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | T:78&79 | 556 | 644 | 124.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3308 | 556 | 644 | 124.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:MP12&18 | 556 | 644 | 124.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 124.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 124.15
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HQ-NY 765 | 556 | 644 | 124.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | S:PA_HNTL78 | 556 | 644 | 124.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:160 | 556 | 644 | 124.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:150 | 556 | 644 | 124.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_3414 | 556 | 644 | 124.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_3514 | 556 | 644 | 124.13
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 124.13
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | S:PA_HNTL78 | 556 | 644 | 124.11
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | B:PACKT3 | 556 | 644 | 124.11
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | B:PACKT3 | 556 | 644 | 124.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:PECHBTM2 | 556 | 644 | 124.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:W89&W90 | 556 | 644 | 124.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | SB:PA230_R3230 | 556 | 644 | 124.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | SB:PA230_R3230 | 556 | 644 | 124.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | SB:PA230_R3230 | 556 | 644 | 124.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | SB:PA230_R3230 | 556 | 644 | 124.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | SB:PA230_R3230 | 556 | 644 | 124.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R140 | 556 | 644 | 124.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | SB:PA230_R3230 | 556 | 644 | 124.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | B:PACKT3 | 556 | 644 | 124.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R3230 | 556 | 644 | 124.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAW230_2014 | 556 | 644 | 124.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | HUNTLEY - PACKARD 78 230 | 556 | 644 | 124
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | SB:PA230_R304 | 556 | 644 | 124
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3314 | 556 | 644 | 123.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - N.SCOT99 I8 345 | 556 | 644 | 123.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:F38&F39 | 556 | 644 | 123.99
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 123.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 123.95
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | SB:PA230_R3230 | 556 | 644 | 123.95
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_2T8082 | 556 | 644 | 123.94
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SHLDON - STONYCR 230 | 556 | 644 | 123.94
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SUSQ1 | 556 | 644 | 123.9
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | SB:PA230_R304 | 556 | 644 | 123.9
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3108 | 556 | 644 | 123.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | B:PACKT3 | 556 | 644 | 123.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | B:PACKT3 | 556 | 644 | 123.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | B:PACKT3 | 556 | 644 | 123.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | B:PACKT3 | 556 | 644 | 123.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | B:PACKT3 | 556 | 644 | 123.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 123.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | SB:PA230_R304 | 556 | 644 | 123.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | B:PACKT3 | 556 | 644 | 123.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - N.SCOT77 I4 345 | 556 | 644 | 123.84
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | B:PACKT3 | 556 | 644 | 123.83
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:F30&F31 | 556 | 644 | 123.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | S:PA_HNTL78 | 556 | 644 | 123.82
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | S:PA_HNTL78 | 556 | 644 | 123.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 123.81
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_376512 | 556 | 644 | 123.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCH_34XC | 556 | 644 | 123.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:FV-5M_37&W-F_171 | 556 | 644 | 123.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-SR_37&W-F_171 | 556 | 644 | 123.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - 5MILE 345 | 556 | 644 | 123.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_31153 | 556 | 644 | 123.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R3230 | 556 | 644 | 123.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | B:PACKT3 | 556 | 644 | 123.74
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PV345_RNS5 | 556 | 644 | 123.7
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R935 | 556 | 644 | 123.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R945 | 556 | 644 | 123.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PV345_RNS4 | 556 | 644 | 123.67
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | SB:PA230_R304 | 556 | 644 | 123.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | SB:PA230_R304 | 556 | 644 | 123.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:STONY230 | 556 | 644 | 123.64
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SANDY_DC | 556 | 644 | 123.63
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SANDY_DC&OMS | 556 | 644 | 123.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LEEDS345_R9293 | 556 | 644 | 123.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | S:PA_HNTL78 | 556 | 644 | 123.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | SB:PA230_R304 | 556 | 644 | 123.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | SB:PA230_R304 | 556 | 644 | 123.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SALEMG1 | 556 | 644 | 123.61
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | SB:PA230_R3230 | 556 | 644 | 123.61
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | SB:PA230_R304 | 556 | 644 | 123.61
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | SB:PA230_R304 | 556 | 644 | 123.61
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:HOPECG1 | 556 | 644 | 123.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:LIMERCK2 | 556 | 644 | 123.59
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL78 | 556 | 644 | 123.58
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_3456 | 556 | 644 | 123.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | SB:PA230_R3230 | 556 | 644 | 123.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 123.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | SB:PA230_R304 | 556 | 644 | 123.53
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_34-B382 | 556 | 644 | 123.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_B2-3482 | 556 | 644 | 123.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CMT/MTR-34 345 | 556 | 644 | 123.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HURLEY - ROCKT CMT/MTR-34 345 | 556 | 644 | 123.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | HUNTLEY - PACKARD 78 230 | 556 | 644 | 123.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | SB:PA230_R3230 | 556 | 644 | 123.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R3230 | 556 | 644 | 123.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R3230 | 556 | 644 | 123.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | B:PACKT3 | 556 | 644 | 123.49
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R304 | 556 | 644 | 123.49
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R304 | 556 | 644 | 123.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R304 | 556 | 644 | 123.46
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-2 345 | SB:PA230_R3230 | 556 | 644 | 123.44
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | S:PA_HNTL78 | 556 | 644 | 123.44
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R150 | 556 | 644 | 123.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-1 345 | SB:PA230_R3230 | 556 | 644 | 123.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CLAY345_R160 | 556 | 644 | 123.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3908 | 556 | 644 | 123.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3808 | 556 | 644 | 123.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - DEW 13 345 | 556 | 644 | 123.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 123.36
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LEEDS345_R94301 | 556 | 644 | 123.35
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | S:PA_HNTL78 | 556 | 644 | 123.35
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | B:PACKT3 | 556 | 644 | 123.34
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | S:PA_HNTL78 | 556 | 644 | 123.34
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R110 | 556 | 644 | 123.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROCK345_4255 | 556 | 644 | 123.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R150 | 556 | 644 | 123.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R160 | 556 | 644 | 123.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_B2-4282 | 556 | 644 | 123.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 644 | 123.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 644 | 123.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 1-16 345 | 556 | 644 | 123.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 556 | 644 | 123.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 556 | 644 | 123.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | B:PACKT3 | 556 | 644 | 123.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 123.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R10 | 556 | 644 | 123.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DUNW345_3 | 556 | 644 | 123.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | B:PACKT3 | 556 | 644 | 123.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE345 | 556 | 644 | 123.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HOMERCTY - STOLLRD 37 345 | 556 | 644 | 123.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | 5 MILE - STOLLE 37A 345 | 556 | 644 | 123.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-1 345 | S:PA_HNTL78 | 556 | 644 | 123.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-2 345 | S:PA_HNTL78 | 556 | 644 | 123.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LEEDS345_R92 | 556 | 644 | 123.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 556 | 644 | 123.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 556 | 644 | 123.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | SB:PA230_R3230 | 556 | 644 | 123.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3102 | 556 | 644 | 123.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:67&37A | 556 | 644 | 123.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 556 | 644 | 123.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 556 | 644 | 123.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DUNW345_8 | 556 | 644 | 123.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | B:PACKT3 | 556 | 644 | 123.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | B:PACKT3 | 556 | 644 | 123.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FITZ 345 | 556 | 644 | 123.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FITZ - EDIC FEI 345 | 556 | 644 | 123.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - FITZ 345 | SB:PA230_R3230 | 556 | 644 | 123.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-2 345 | B:PACKT3 | 556 | 644 | 123.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | SB:PA230_R3230 | 556 | 644 | 123.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R3230 | 556 | 644 | 123.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DEWI345_R915 | 556 | 644 | 123.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DEWI345_R130 | 556 | 644 | 123.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DEWI345_R220 | 556 | 644 | 123.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-1 345 | B:PACKT3 | 556 | 644 | 123.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:STOLLE345 | 556 | 644 | 123.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | S:PA_HNTL78 | 556 | 644 | 123.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | S:PA_HNTL78 | 556 | 644 | 123.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | S:PA_HNTL78 | 556 | 644 | 123.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | VOL - MARCY 19 345 | 556 | 644 | 123.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | VOLNEY - MARCY I9 345 | 556 | 644 | 123.15
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | S:PA_HNTL78 | 556 | 644 | 123.15
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | S:PA_HNTL78 | 556 | 644 | 123.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R3230 | 556 | 644 | 123.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:VOLN_R925 | 556 | 644 | 123.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 123.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | S:PA_HNTL78 | 556 | 644 | 123.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:5M-SR_37&W-F_171 | 556 | 644 | 123.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3914 | 556 | 644 | 123.08
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PANN345_3814 | 556 | 644 | 123.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ROCH 345/115 5TR | 556 | 644 | 123.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | S:PA_HNTL78 | 556 | 644 | 123.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | S:PA_HNTL78 | 556 | 644 | 123.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | SB:PA230_R304 | 556 | 644 | 123.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 123.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | S:PA_HNTL78 | 556 | 644 | 123.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OS - EL - LFYTE 17 345 | SB:PA230_R3230 | 556 | 644 | 123.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 123.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - FITZ 345 | S:PA_HNTL78 | 556 | 644 | 123.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | S:PA_HNTL78 | 556 | 644 | 123.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:GINNA | 556 | 644 | 123.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 4 | SB:PA230_R3230 | 556 | 644 | 122.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 5 | SB:PA230_R3230 | 556 | 644 | 122.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 6 | SB:PA230_R3230 | 556 | 644 | 122.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 7 | SB:PA230_R3230 | 556 | 644 | 122.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-2 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.96
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1502 | 556 | 644 | 122.95
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-1 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.95
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - FITZ 345 | B:PACKT3 | 556 | 644 | 122.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL78 | 556 | 644 | 122.92
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 1TR | SB:PA230_R3230 | 556 | 644 | 122.91
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 2TR | SB:PA230_R3230 | 556 | 644 | 122.91
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 3TR | SB:PA230_R3230 | 556 | 644 | 122.9
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.9
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.9
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.9
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | VOL - MARCY 19 345 | SB:PA230_R3230 | 556 | 644 | 122.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | B:PACKT3 | 556 | 644 | 122.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 1TR | SB:PA230_R3230 | 556 | 644 | 122.85
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 2TR | SB:PA230_R3230 | 556 | 644 | 122.85
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OS - EL - LFYTE 17 345 | S:PA_HNTL78 | 556 | 644 | 122.85
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | B:PACKT3 | 556 | 644 | 122.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | B:PACKT3 | 556 | 644 | 122.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | B:PACKT3 | 556 | 644 | 122.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OS - EL - LFYTE 17 345 | B:PACKT3 | 556 | 644 | 122.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 4 | B:PACKT3 | 556 | 644 | 122.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 5 | B:PACKT3 | 556 | 644 | 122.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 6 | B:PACKT3 | 556 | 644 | 122.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 7 | B:PACKT3 | 556 | 644 | 122.77
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 1TR | S:PA_HNTL78 | 556 | 644 | 122.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 2TR | S:PA_HNTL78 | 556 | 644 | 122.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 3TR | S:PA_HNTL78 | 556 | 644 | 122.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 3 115 | SB:PA230_R3230 | 556 | 644 | 122.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - TEAL 10 115 | SB:PA230_R3230 | 556 | 644 | 122.76
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | S:PA_HNTL78 | 556 | 644 | 122.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - LM 14 115 | SB:PA230_R3230 | 556 | 644 | 122.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | S:PA_HNTL78 | 556 | 644 | 122.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - TEAL 11 115 | SB:PA230_R3230 | 556 | 644 | 122.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1502 | 556 | 644 | 122.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | SB:PA230_R304 | 556 | 644 | 122.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | SB:PA230_R304 | 556 | 644 | 122.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | SB:PA230_R304 | 556 | 644 | 122.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | S:PA_HNTL78 | 556 | 644 | 122.72
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | S:PA_HNTL78 | 556 | 644 | 122.72
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | VOL - MARCY 19 345 | S:PA_HNTL78 | 556 | 644 | 122.72
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - FITZ 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.72
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 1TR | S:PA_HNTL78 | 556 | 644 | 122.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 2TR | S:PA_HNTL78 | 556 | 644 | 122.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 5 115 | SB:PA230_R3230 | 556 | 644 | 122.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LHH - CLAY 7 115 | SB:PA230_R3230 | 556 | 644 | 122.7
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - WOOD 17 115 | SB:PA230_R3230 | 556 | 644 | 122.7
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - VOL 21 345 | SB:PA230_R3230 | 556 | 644 | 122.7
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 1TR | B:PACKT3 | 556 | 644 | 122.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 2TR | B:PACKT3 | 556 | 644 | 122.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FUL - CLAY 4 115 | SB:PA230_R3230 | 556 | 644 | 122.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - VOL 20 345 | SB:PA230_R3230 | 556 | 644 | 122.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA 345/115 1TR | SB:PA230_R3230 | 556 | 644 | 122.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA 345/115 2TR | SB:PA230_R3230 | 556 | 644 | 122.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | SB:PA230_R3230 | 556 | 644 | 122.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 3TR | B:PACKT3 | 556 | 644 | 122.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - 9MI1 9 345 | SB:PA230_R3230 | 556 | 644 | 122.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R3230 | 556 | 644 | 122.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R3230 | 556 | 644 | 122.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - IND 25 345 | SB:PA230_R3230 | 556 | 644 | 122.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW - VOL 11 345 | SB:PA230_R3230 | 556 | 644 | 122.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW - VOL 12 345 | SB:PA230_R3230 | 556 | 644 | 122.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW 345/115 1TR | SB:PA230_R3230 | 556 | 644 | 122.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | T:78&79 | 556 | 644 | 122.64
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - FITZ 10 345 | SB:PA230_R3230 | 556 | 644 | 122.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | VOL - MARCY 19 345 | B:PACKT3 | 556 | 644 | 122.63
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 1TR | B:PACKT3 | 556 | 644 | 122.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 2TR | B:PACKT3 | 556 | 644 | 122.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - MRCY ue 1-7 345 | SB:PA230_R3230 | 556 | 644 | 122.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 3 115 | S:PA_HNTL78 | 556 | 644 | 122.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - TEAL 10 115 | S:PA_HNTL78 | 556 | 644 | 122.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - TEAL 11 115 | S:PA_HNTL78 | 556 | 644 | 122.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 5 115 | S:PA_HNTL78 | 556 | 644 | 122.58
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - LM 14 115 | S:PA_HNTL78 | 556 | 644 | 122.58
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LHH - CLAY 7 115 | S:PA_HNTL78 | 556 | 644 | 122.57
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - VOL 21 345 | S:PA_HNTL78 | 556 | 644 | 122.57
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FUL - CLAY 4 115 | S:PA_HNTL78 | 556 | 644 | 122.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - WOOD 17 115 | S:PA_HNTL78 | 556 | 644 | 122.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:SITHE 1 | SB:PA230_R3230 | 556 | 644 | 122.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:SITHE 2 | SB:PA230_R3230 | 556 | 644 | 122.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OS - EL - LFYTE 17 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - VOL 20 345 | S:PA_HNTL78 | 556 | 644 | 122.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA 345/115 1TR | S:PA_HNTL78 | 556 | 644 | 122.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA 345/115 2TR | S:PA_HNTL78 | 556 | 644 | 122.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - 9MI1 9 345 | S:PA_HNTL78 | 556 | 644 | 122.55
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | S:PA_HNTL78 | 556 | 644 | 122.55
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - IND 25 345 | S:PA_HNTL78 | 556 | 644 | 122.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW - VOL 11 345 | S:PA_HNTL78 | 556 | 644 | 122.53
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW - VOL 12 345 | S:PA_HNTL78 | 556 | 644 | 122.53
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH 345/115 5TR | SB:PA230_R3230 | 556 | 644 | 122.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW 345/115 1TR | S:PA_HNTL78 | 556 | 644 | 122.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - BECK_TSA 345 | SB:PA230_R3230 | 556 | 644 | 122.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - BECK_TSB 345 | SB:PA230_R3230 | 556 | 644 | 122.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 3 115 | B:PACKT3 | 556 | 644 | 122.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - TEAL 10 115 | B:PACKT3 | 556 | 644 | 122.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - TEAL 11 115 | B:PACKT3 | 556 | 644 | 122.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | S:PA_HNTL78 | 556 | 644 | 122.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | S:PA_HNTL78 | 556 | 644 | 122.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - FITZ 10 345 | S:PA_HNTL78 | 556 | 644 | 122.5
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MASS_765_7108 | 556 | 644 | 122.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - LM 14 115 | B:PACKT3 | 556 | 644 | 122.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - MRCY ue 1-7 345 | S:PA_HNTL78 | 556 | 644 | 122.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LOCKPORT | SB:PA230_R3230 | 556 | 644 | 122.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 5 115 | B:PACKT3 | 556 | 644 | 122.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LHH - CLAY 7 115 | B:PACKT3 | 556 | 644 | 122.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:SITHE 1 | S:PA_HNTL78 | 556 | 644 | 122.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:SITHE 2 | S:PA_HNTL78 | 556 | 644 | 122.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FUL - CLAY 4 115 | B:PACKT3 | 556 | 644 | 122.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - WOOD 17 115 | B:PACKT3 | 556 | 644 | 122.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:OSWEGO 5 | S:PA_HNTL78 | 556 | 644 | 122.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - VOL 21 345 | B:PACKT3 | 556 | 644 | 122.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA 345/115 1TR | B:PACKT3 | 556 | 644 | 122.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA 345/115 2TR | B:PACKT3 | 556 | 644 | 122.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | B:PACKT3 | 556 | 644 | 122.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | SB:PA230_R304 | 556 | 644 | 122.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - 9MI1 9 345 | B:PACKT3 | 556 | 644 | 122.46
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - VOL 20 345 | B:PACKT3 | 556 | 644 | 122.46
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 1TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.45
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 2TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.45
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 3TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.44
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW - VOL 11 345 | B:PACKT3 | 556 | 644 | 122.44
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW - VOL 12 345 | B:PACKT3 | 556 | 644 | 122.44
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - IND 25 345 | B:PACKT3 | 556 | 644 | 122.44
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW 345/115 1TR | B:PACKT3 | 556 | 644 | 122.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:AVOCA | 556 | 644 | 122.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CANDQUA - STNYRDG 68A 230 | 556 | 644 | 122.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | SB:PA230_R304 | 556 | 644 | 122.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | SB:PA230_R3230 | 556 | 644 | 122.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:OSWEGO 6 | S:PA_HNTL78 | 556 | 644 | 122.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | VOL - MARCY 19 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | T:78&79 | 556 | 644 | 122.41
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | B:PACKT3 | 556 | 644 | 122.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | B:PACKT3 | 556 | 644 | 122.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - FITZ 10 345 | B:PACKT3 | 556 | 644 | 122.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:STONYRIDGE | 556 | 644 | 122.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 1TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 2TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - MRCY ue 1-7 345 | B:PACKT3 | 556 | 644 | 122.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - BECK_TSA 345 | B:PACKT3 | 556 | 644 | 122.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - BECK_TSB 345 | B:PACKT3 | 556 | 644 | 122.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH 345/115 5TR | B:PACKT3 | 556 | 644 | 122.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - TEAL 11 115 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MASS_765_7102 | 556 | 644 | 122.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH 345/115 5TR | S:PA_HNTL78 | 556 | 644 | 122.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | S:PA_HNTL78 | 556 | 644 | 122.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 3 115 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - TEAL 10 115 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - LM 14 115 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 5 115 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LHH - CLAY 7 115 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FUL - CLAY 4 115 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - WOOD 17 115 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - VOL 21 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA 345/115 1TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA 345/115 2TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - 9MI1 9 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - VOL 20 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW - VOL 11 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW - VOL 12 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - IND 25 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LOCKPORT | B:PACKT3 | 556 | 644 | 122.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | B:PACKT3 | 556 | 644 | 122.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW 345/115 1TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - FITZ 10 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:SITHE 1 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:SITHE 2 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:OSWEGO 5 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - MRCY ue 1-7 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 122.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ERIE E - 4 MILE 230 | 556 | 644 | 122.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R304 | 556 | 644 | 121.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH 345/115 5TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 121.98
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:62&BP76 | 556 | 644 | 121.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | SB:PA230_R304 | 556 | 644 | 121.83
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | SB:PA230_R304 | 556 | 644 | 121.81
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | SB:PA230_R304 | 556 | 644 | 121.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | SB:PA230_R304 | 556 | 644 | 121.78
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | SB:PA230_R3230 | 556 | 644 | 121.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | SB:PA230_R3230 | 556 | 644 | 121.68
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R3230 | 556 | 644 | 121.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | SB:PA230_R3230 | 556 | 644 | 121.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | SB:PA230_R3230 | 556 | 644 | 121.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | B:PACKT3 | 556 | 644 | 121.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | B:PACKT3 | 556 | 644 | 121.5
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | SB:PA230_R304 | 556 | 644 | 121.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RAIN345_1W | 556 | 644 | 121.45
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT2 | 556 | 644 | 121.45
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FRASER - OAKDLE 32 345 | 556 | 644 | 121.44
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDL - FRASER 32 345 | 556 | 644 | 121.44
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RAIN345_9W | 556 | 644 | 121.44
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:FRAS345_B1-3262 | 556 | 644 | 121.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: RAVENSWOOD | 556 | 644 | 121.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:30 | 556 | 644 | 121.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | BWLN - WHAV -LDN 67 345 | 556 | 644 | 121.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT1 | 556 | 644 | 121.41
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 2TR | 556 | 644 | 121.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | B:PACKT3 | 556 | 644 | 121.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | B:PACKT3 | 556 | 644 | 121.38
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | B:PACKT3 | 556 | 644 | 121.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B2 | 556 | 644 | 121.36
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROSE345_30553 | 556 | 644 | 121.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_4-56-2 | 556 | 644 | 121.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | SB:PA230_R304 | 556 | 644 | 121.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M7TR | 556 | 644 | 121.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_1-56-2 | 556 | 644 | 121.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_6-56-2 | 556 | 644 | 121.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:SCRIBA_R925 | 556 | 644 | 121.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:SCRIBA_R230 | 556 | 644 | 121.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:9 MI PT2 | 556 | 644 | 121.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:LADE_3-56-2 | 556 | 644 | 121.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:NOEND | 556 | 644 | 121.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B3 | 556 | 644 | 121.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - WTRCR 31 345 | 556 | 644 | 121.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROSE345_30551 | 556 | 644 | 121.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROSE345_31152 | 556 | 644 | 121.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RMP345_T1500 | 556 | 644 | 121.12
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON2 | 556 | 644 | 121.12
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | RAMAPO - BRNCHBRG 5018 345 | 556 | 644 | 121.11
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WATRC345_31-2 | 556 | 644 | 121.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2208 | 556 | 644 | 121.08
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:RMP345_1500-2X | 556 | 644 | 121.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M6TR | 556 | 644 | 121.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M8TR | 556 | 644 | 121.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2214 | 556 | 644 | 121.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS17-20 | 556 | 644 | 121.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2224 | 556 | 644 | 121.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1724 | 556 | 644 | 121.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1714 | 556 | 644 | 121.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1524 | 556 | 644 | 121.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1514 | 556 | 644 | 121.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE115_1508 | 556 | 644 | 121.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | SB:PA230_R304 | 556 | 644 | 121.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2514 | 556 | 644 | 121.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2524 | 556 | 644 | 121.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS21-24 | 556 | 644 | 121.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MOSE230_2508 | 556 | 644 | 121.03
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | SB:PA230_R304 | 556 | 644 | 121.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON1 | 556 | 644 | 120.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | SB:PA230_R304 | 556 | 644 | 120.92
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3208 | 556 | 644 | 120.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/NWES | 556 | 644 | 120.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SRIPL - ERIE E 69 230 | 556 | 644 | 120.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | DUNKIRK - SRIPL 68 230 | 556 | 644 | 120.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:SRIPLEY | 556 | 644 | 120.85
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:AT_R6361 | 556 | 644 | 120.84
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BESICORP | 556 | 644 | 120.83
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:EMPIRE | 556 | 644 | 120.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:EMPIRE | 556 | 644 | 120.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | SB:PA230_R304 | 556 | 644 | 120.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | SB:PA230_R3230 | 556 | 644 | 120.74
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:72&69 | 556 | 644 | 120.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: IND PT 2 | 556 | 644 | 120.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | S:PA_HNTL78 | 556 | 644 | 120.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | S:PA_HNTL78 | 556 | 644 | 120.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R304 | 556 | 644 | 120.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN GILBOA #3&4 | 556 | 644 | 120.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3302 | 556 | 644 | 120.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 2TR | S:PA_HNTL78 | 556 | 644 | 120.64
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | B:PACKT3 | 556 | 644 | 120.61
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN GILBOA #1&2 | 556 | 644 | 120.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3202 | 556 | 644 | 120.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | BECK - PACKARD BP76 230 | 556 | 644 | 120.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GILB345_3308 | 556 | 644 | 120.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHN_11 | 556 | 644 | 120.59
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHN_9 | 556 | 644 | 120.59
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | SB:PA230_R3230 | 556 | 644 | 120.57
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:NTHF3&4 | 556 | 644 | 120.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | S:PA_HNTL78 | 556 | 644 | 120.57
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHN_7 | 556 | 644 | 120.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | SB:PA230_R3230 | 556 | 644 | 120.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | S:PA_HNTL78 | 556 | 644 | 120.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | SB:PA230_R3230 | 556 | 644 | 120.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | S:PA_HNTL78 | 556 | 644 | 120.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | S:PA_HNTL78 | 556 | 644 | 120.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STONYCR - WTHRS 230 | 556 | 644 | 120.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | S:PA_HNTL78 | 556 | 644 | 120.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | S:PA_HNTL78 | 556 | 644 | 120.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | B:PACKT3 | 556 | 644 | 120.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - FARMVLY | 556 | 644 | 120.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: IND PT 3 | 556 | 644 | 120.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | SB:PA230_R304 | 556 | 644 | 120.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | SB:PA230_R3230 | 556 | 644 | 120.45
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHS_1 | 556 | 644 | 120.44
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:BUCHS_3 | 556 | 644 | 120.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | SB:PA230_R304 | 556 | 644 | 120.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | SB:PA230_R304 | 556 | 644 | 120.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | SB:PA230_R304 | 556 | 644 | 120.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | SB:PA230_R304 | 556 | 644 | 120.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | SB:PA230_R304 | 556 | 644 | 120.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | SB:PA230_R304 | 556 | 644 | 120.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | SB:PA230_R3230 | 556 | 644 | 120.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | SB:PA230_R3230 | 556 | 644 | 120.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | S:PA_HNTL78 | 556 | 644 | 120.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | S:PA_HNTL78 | 556 | 644 | 120.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | SB:PA230_R3230 | 556 | 644 | 120.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | SB:PA230_R3230 | 556 | 644 | 120.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:67&68&BW | 556 | 644 | 120.37
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | B:PACKT3 | 556 | 644 | 120.35
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | S:PA_HNTL78 | 556 | 644 | 120.34
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HILLSIDE 230/115 4TR | 556 | 644 | 120.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:HILLSIDE | 556 | 644 | 120.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:HILL_B412 | 556 | 644 | 120.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | B:PACKT3 | 556 | 644 | 120.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | B:PACKT3 | 556 | 644 | 120.33
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | SB:PA230_R3230 | 556 | 644 | 120.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 2TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R3230 | 556 | 644 | 120.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | S:PA_HNTL78 | 556 | 644 | 120.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | S:PA_HNTL78 | 556 | 644 | 120.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | S:PA_HNTL78 | 556 | 644 | 120.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | S:PA_HNTL78 | 556 | 644 | 120.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R3230 | 556 | 644 | 120.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | B:PACKT3 | 556 | 644 | 120.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - ELM 70 230 | 556 | 644 | 120.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R3230 | 556 | 644 | 120.27
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R304 | 556 | 644 | 120.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R304 | 556 | 644 | 120.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R304 | 556 | 644 | 120.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:BETHSTM | 556 | 644 | 120.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:SITHE 1 | 556 | 644 | 120.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:SITHE 2 | 556 | 644 | 120.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | B:PACKT3 | 556 | 644 | 120.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | B:PACKT3 | 556 | 644 | 120.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | B:PACKT3 | 556 | 644 | 120.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | B:PACKT3 | 556 | 644 | 120.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | S:PA_HNTL78 | 556 | 644 | 120.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:HILL_68-B412 | 556 | 644 | 120.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:MBWC/NWES | 556 | 644 | 120.13
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HCWC/NWES | 556 | 644 | 120.13
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STNYRDG - HILLSIDE 68B 230 | 556 | 644 | 120.1
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WTHERS230 | 556 | 644 | 120.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:130 | 556 | 644 | 120.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:120_130 | 556 | 644 | 120.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:W97&W98 | 556 | 644 | 120.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WATRC345_30-3142 | 556 | 644 | 120.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | WTRCR - MAINSBRG 30A 345 | 556 | 644 | 120.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | SB:PA230_R304 | 556 | 644 | 120.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | B:PACKT3 | 556 | 644 | 120.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WATRC345_B1-3042 | 556 | 644 | 120.08
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL78 | 556 | 644 | 120.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL78 | 556 | 644 | 120.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | B:PACKT3 | 556 | 644 | 120.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.03
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | SB:PA230_R3230 | 556 | 644 | 120.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL78 | 556 | 644 | 120.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | SB:PA230_R304 | 556 | 644 | 120.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | SB:PA230_R304 | 556 | 644 | 120.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 120.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | B:PACKT3 | 556 | 644 | 120.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | SB:PA230_R3230 | 556 | 644 | 120
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | B:PACKT3 | 556 | 644 | 119.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-WC_30&W-F_171 | 556 | 644 | 119.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:61&191 | 556 | 644 | 119.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-1 345 | SB:PA230_R304 | 556 | 644 | 119.92
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-2 345 | SB:PA230_R304 | 556 | 644 | 119.92
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | SB:PA230_R3230 | 556 | 644 | 119.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | B:PACKT3 | 556 | 644 | 119.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 119.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R3230 | 556 | 644 | 119.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL - DUNKIRK 73 230 | 556 | 644 | 119.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:DUNKG3 | 556 | 644 | 119.84
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL - DUNKIRK 74 230 | 556 | 644 | 119.83
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | B:PACKT3 | 556 | 644 | 119.83
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HCMB/NWES | 556 | 644 | 119.81
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R304 | 556 | 644 | 119.77
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:DUNKG4 | 556 | 644 | 119.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MAINSBRG - HOMERCITY 30B 345 | 556 | 644 | 119.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - PACKARD 62 230 | 556 | 644 | 119.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 119.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | S:PA_HNTL78 | 556 | 644 | 119.74
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | SB:PA230_R304 | 556 | 644 | 119.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 119.72
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 119.71
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | B:PACKT3 | 556 | 644 | 119.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - FITZ 345 | SB:PA230_R304 | 556 | 644 | 119.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - PACKARD 61 230 | 556 | 644 | 119.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-MB_30&W-F_171 | 556 | 644 | 119.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | SB:PA230_R304 | 556 | 644 | 119.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R304 | 556 | 644 | 119.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | B:PACKT3 | 556 | 644 | 119.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | S:PA_HNTL78 | 556 | 644 | 119.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | SB:PA230_R3230 | 556 | 644 | 119.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:PA27&BP76 | 556 | 644 | 119.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:62&PA27 | 556 | 644 | 119.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OS - EL - LFYTE 17 345 | SB:PA230_R304 | 556 | 644 | 119.53
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | HUNTLEY - PACKARD 78 230 | 556 | 644 | 119.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | S:PA_HNTL78 | 556 | 644 | 119.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 1TR | SB:PA230_R304 | 556 | 644 | 119.46
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 2TR | SB:PA230_R304 | 556 | 644 | 119.46
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 3TR | SB:PA230_R304 | 556 | 644 | 119.45
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:KINT_39-B112 | 556 | 644 | 119.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 4 | SB:PA230_R304 | 556 | 644 | 119.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 5 | SB:PA230_R304 | 556 | 644 | 119.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 6 | SB:PA230_R304 | 556 | 644 | 119.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 7 | SB:PA230_R304 | 556 | 644 | 119.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 1TR | SB:PA230_R304 | 556 | 644 | 119.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 2TR | SB:PA230_R304 | 556 | 644 | 119.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | VOL - MARCY 19 345 | SB:PA230_R304 | 556 | 644 | 119.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | B:PACKT3 | 556 | 644 | 119.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1502 | 556 | 644 | 119.38
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/WF/NWES | 556 | 644 | 119.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:DKSR/WRFL | 556 | 644 | 119.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/WRFL | 556 | 644 | 119.35
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:KINT_B1-3812 | 556 | 644 | 119.34
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 119.34
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 3 115 | SB:PA230_R304 | 556 | 644 | 119.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - TEAL 10 115 | SB:PA230_R304 | 556 | 644 | 119.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - TEAL 11 115 | SB:PA230_R304 | 556 | 644 | 119.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - LM 14 115 | SB:PA230_R304 | 556 | 644 | 119.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 5 115 | SB:PA230_R304 | 556 | 644 | 119.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LHH - CLAY 7 115 | SB:PA230_R304 | 556 | 644 | 119.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FUL - CLAY 4 115 | SB:PA230_R304 | 556 | 644 | 119.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - WOOD 17 115 | SB:PA230_R304 | 556 | 644 | 119.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - VOL 21 345 | SB:PA230_R304 | 556 | 644 | 119.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA 345/115 1TR | SB:PA230_R304 | 556 | 644 | 119.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA 345/115 2TR | SB:PA230_R304 | 556 | 644 | 119.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - 9MI1 9 345 | SB:PA230_R304 | 556 | 644 | 119.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - VOL 20 345 | SB:PA230_R304 | 556 | 644 | 119.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | SB:PA230_R304 | 556 | 644 | 119.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW - VOL 11 345 | SB:PA230_R304 | 556 | 644 | 119.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW - VOL 12 345 | SB:PA230_R304 | 556 | 644 | 119.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - IND 25 345 | SB:PA230_R304 | 556 | 644 | 119.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OSW 345/115 1TR | SB:PA230_R304 | 556 | 644 | 119.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 119.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R304 | 556 | 644 | 119.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R304 | 556 | 644 | 119.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - FITZ 10 345 | SB:PA230_R304 | 556 | 644 | 119.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - MRCY ue 1-7 345 | SB:PA230_R304 | 556 | 644 | 119.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R304 | 556 | 644 | 119.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | S:PA_HNTL78 | 556 | 644 | 119.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | S:PA_HNTL78 | 556 | 644 | 119.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | S:PA_HNTL78 | 556 | 644 | 119.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | S:PA_HNTL78 | 556 | 644 | 119.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | SB:PA230_R3230 | 556 | 644 | 119.13
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | T:78&79 | 556 | 644 | 119.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | S:PA_HNTL78 | 556 | 644 | 119.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH 345/115 5TR | SB:PA230_R304 | 556 | 644 | 119.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | S:PA_HNTL78 | 556 | 644 | 119.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | SB:PA230_R304 | 556 | 644 | 118.99
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | S:PA_HNTL78 | 556 | 644 | 118.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | SB:PA230_R3230 | 556 | 644 | 118.96
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R955 | 556 | 644 | 118.95
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:OSWEGO 5 | 556 | 644 | 118.94
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | S:PA_HNTL78 | 556 | 644 | 118.94
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R965 | 556 | 644 | 118.91
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | B:PACKT3 | 556 | 644 | 118.9
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | SB:PA230_R3230 | 556 | 644 | 118.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | SB:PA230_R3230 | 556 | 644 | 118.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | SB:PA230_R3230 | 556 | 644 | 118.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | S:PA_HNTL78 | 556 | 644 | 118.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | B:Hunt68 | 556 | 644 | 118.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.83
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:CNDGUA | 556 | 644 | 118.8
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:250 | 556 | 644 | 118.8
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:MILLST3 | 556 | 644 | 118.8
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:MLS3&OMS | 556 | 644 | 118.8
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MEYER - CANDQUA 60 230 | 556 | 644 | 118.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.77
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | B:PACKT3 | 556 | 644 | 118.72
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | B:PACKT3 | 556 | 644 | 118.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | B:PACKT3 | 556 | 644 | 118.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | B:PACKT3 | 556 | 644 | 118.69
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.68
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:KINTIGH | 556 | 644 | 118.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:FRGT/WRFL | 556 | 644 | 118.67
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:68&160 | 556 | 644 | 118.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R925 | 556 | 644 | 118.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:OSWEGO 6 | 556 | 644 | 118.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:9MIPT1 | 556 | 644 | 118.59
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.58
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:OSWE_R935 | 556 | 644 | 118.57
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | SB:PA230_R3230 | 556 | 644 | 118.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | SB:PA230_R3230 | 556 | 644 | 118.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | SB:PA230_R3230 | 556 | 644 | 118.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | SB:PA230_R3230 | 556 | 644 | 118.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | SB:PA230_R3230 | 556 | 644 | 118.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | SB:PA230_R3230 | 556 | 644 | 118.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | S:PA_HNTL78 | 556 | 644 | 118.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | S:PA_HNTL78 | 556 | 644 | 118.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | S:PA_HNTL78 | 556 | 644 | 118.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | SB:PA230_R304 | 556 | 644 | 118.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | S:PA_HNTL78 | 556 | 644 | 118.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | S:PA_HNTL78 | 556 | 644 | 118.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | S:PA_HNTL78 | 556 | 644 | 118.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | SB:PA230_R3230 | 556 | 644 | 118.45
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1402 | 556 | 644 | 118.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:FITZPATR | 556 | 644 | 118.37
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | SB:PA230_R304 | 556 | 644 | 118.35
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | SB:PA230_R3230 | 556 | 644 | 118.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | B:PACKT3 | 556 | 644 | 118.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | B:PACKT3 | 556 | 644 | 118.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | B:PACKT3 | 556 | 644 | 118.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | B:PACKT3 | 556 | 644 | 118.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | B:PACKT3 | 556 | 644 | 118.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:73&74 | 556 | 644 | 118.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SEAB&OMS | 556 | 644 | 118.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SEABROOK | 556 | 644 | 118.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | B:PACKT3 | 556 | 644 | 118.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | S:PA_HNTL78 | 556 | 644 | 118.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | B:PACKT3 | 556 | 644 | 118.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R304 | 556 | 644 | 118.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | SB:PA230_R304 | 556 | 644 | 118.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | SB:PA230_R304 | 556 | 644 | 118.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MARC_765_7402 | 556 | 644 | 118.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MSU1_7202>7214>7208>7214 | 556 | 644 | 118.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HQ-NY 765 | 556 | 644 | 118.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | HUNTLEY - PACKARD 78 230 | 556 | 644 | 118.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | B:PACKT3 | 556 | 644 | 118.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | S:PA_HNTL78 | 556 | 644 | 117.91
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | SB:PA230_R3230 | 556 | 644 | 117.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SHLDON - STONYCR 230 | 556 | 644 | 117.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SANDY_DC&OMS | 556 | 644 | 117.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SANDY_DC | 556 | 644 | 117.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | B:PACKT3 | 556 | 644 | 117.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | SB:PA230_R3230 | 556 | 644 | 117.64
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | S:PA_HNTL78 | 556 | 644 | 117.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 117.61
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | B:Hunt68 | 556 | 644 | 117.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:STONY230 | 556 | 644 | 117.58
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | SB:PA230_R3230 | 556 | 644 | 117.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DUNK230_R1312 | 556 | 644 | 117.5
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1502 | 556 | 644 | 117.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | SB:PA230_R3230 | 556 | 644 | 117.45
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | B:PACKT3 | 556 | 644 | 117.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1502 | 556 | 644 | 117.36
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | SB:PA230_R304 | 556 | 644 | 117.36
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R3230 | 556 | 644 | 117.35
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 117.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | B:PACKT3 | 556 | 644 | 117.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1402 | 556 | 644 | 117.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | B:PACKT3 | 556 | 644 | 117.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | SB:PA230_R304 | 556 | 644 | 117.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | SB:PA230_R304 | 556 | 644 | 117.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 4TR | SB:PA230_R304 | 556 | 644 | 117.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | SB:PA230_R304 | 556 | 644 | 117.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | SB:PA230_R304 | 556 | 644 | 117.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | T:78&79 | 556 | 644 | 117.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | S:PA_HNTL78 | 556 | 644 | 117.13
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | T:78&79 | 556 | 644 | 117.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | S:PA_HNTL78 | 556 | 644 | 117.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | B:PACKT3 | 556 | 644 | 117.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL78 | 556 | 644 | 117.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:GINNA | 556 | 644 | 117.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | SB:PA230_R304 | 556 | 644 | 116.95
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | SB:PA230_R304 | 556 | 644 | 116.95
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | SB:PA230_R304 | 556 | 644 | 116.94
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | SB:PA230_R304 | 556 | 644 | 116.94
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | SB:PA230_R304 | 556 | 644 | 116.93
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R304 | 556 | 644 | 116.92
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R304 | 556 | 644 | 116.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R304 | 556 | 644 | 116.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 116.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 116.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 116.74
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | SB:PA230_R304 | 556 | 644 | 116.74
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:62&BP76 | 556 | 644 | 116.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | SB:PA230_R304 | 556 | 644 | 116.71
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1502 | 556 | 644 | 116.68
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R304 | 556 | 644 | 116.58
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:BRUCE5 | 556 | 644 | 116.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | SB:PA230_R304 | 556 | 644 | 116.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CANDQUA - STNYRDG 68A 230 | 556 | 644 | 116.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:AVOCA | 556 | 644 | 116.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:STONYRIDGE | 556 | 644 | 116.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MASS_765_7108 | 556 | 644 | 116.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | S:PA_HNTL78 | 556 | 644 | 116.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | SB:HUNT230_R1502 | 556 | 644 | 116.39
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:78&79 | 556 | 644 | 116.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:MASS_765_7102 | 556 | 644 | 116.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | SB:PA230_R304 | 556 | 644 | 116.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | B:Hunt68 | 556 | 644 | 116.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | WTHRS - MEYER 230 | 556 | 644 | 116.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | T:78&79 | 556 | 644 | 116.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 116.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ERIE E - 4 MILE 230 | 556 | 644 | 116.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:MEYER | 556 | 644 | 116.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | SB:PA230_R304 | 556 | 644 | 115.83
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1402 | 556 | 644 | 115.81
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R3230 | 556 | 644 | 115.68
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:DARLIN1 | 556 | 644 | 115.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | SB:HUNT230_R1502 | 556 | 644 | 115.41
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | SB:PA230_R304 | 556 | 644 | 115.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | SB:PA230_R304 | 556 | 644 | 115.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | SB:PA230_R304 | 556 | 644 | 115.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:SCRIBA_R925 | 556 | 644 | 115.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:9 MI PT2 | 556 | 644 | 115.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:SCRIBA_R230 | 556 | 644 | 115.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | SB:PA230_R304 | 556 | 644 | 115.12
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | SB:PA230_R304 | 556 | 644 | 115.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | T:78&79 | 556 | 644 | 115.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | SB:PA230_R304 | 556 | 644 | 115.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | SB:PA230_R304 | 556 | 644 | 115.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | SB:PA230_R304 | 556 | 644 | 115.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | SB:PA230_R304 | 556 | 644 | 115.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | SB:PA230_R304 | 556 | 644 | 115.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | SB:PA230_R304 | 556 | 644 | 115.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | SB:PA230_R3230 | 556 | 644 | 114.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/NWES | 556 | 644 | 114.83
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | DUNKIRK - SRIPL 68 230 | 556 | 644 | 114.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:SRIPLEY | 556 | 644 | 114.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SRIPL - ERIE E 69 230 | 556 | 644 | 114.8
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | SB:PA230_R3230 | 556 | 644 | 114.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | SB:PA230_R304 | 556 | 644 | 114.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R3230 | 556 | 644 | 114.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | B:PACKT3 | 556 | 644 | 114.64
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | S:PA_HNTL78 | 556 | 644 | 114.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | SB:PA230_R3230 | 556 | 644 | 114.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | SB:PA230_R3230 | 556 | 644 | 114.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | S:PA_HNTL78 | 556 | 644 | 114.58
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | S:PA_HNTL78 | 556 | 644 | 114.55
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | B:PACKT3 | 556 | 644 | 114.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | SB:PA230_R304 | 556 | 644 | 114.53
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | S:PA_HNTL78 | 556 | 644 | 114.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | S:PA_HNTL78 | 556 | 644 | 114.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STONYCR - WTHRS 230 | 556 | 644 | 114.5
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1502 | 556 | 644 | 114.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | S:PA_HNTL78 | 556 | 644 | 114.46
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | B:PACKT3 | 556 | 644 | 114.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | B:PACKT3 | 556 | 644 | 114.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | B:PACKT3 | 556 | 644 | 114.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | SB:PA230_R304 | 556 | 644 | 114.37
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 114.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | SB:HUNT230_R1502 | 556 | 644 | 114.34
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | SB:PA230_R304 | 556 | 644 | 114.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 114.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 114.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | HUNTLEY - PACKARD 78 230 | 556 | 644 | 114.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | HUNTLEY - PACKARD 78 230 | 556 | 644 | 114.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | T:78&79 | 556 | 644 | 114.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R304 | 556 | 644 | 114.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | SB:HUNT230_R1502 | 556 | 644 | 114.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:WTHERS230 | 556 | 644 | 114.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | T:78&79 | 556 | 644 | 114.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:DUNKG4 | 556 | 644 | 113.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | T:78&79 | 556 | 644 | 113.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | S:PA_HNTL78 | 556 | 644 | 113.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1502 | 556 | 644 | 113.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | SB:HUNT230_R1502 | 556 | 644 | 113.64
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | HUNTLEY - PACKARD 78 230 | 556 | 644 | 113.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | T:78&79 | 556 | 644 | 113.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R3230 | 556 | 644 | 113.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | SB:PA230_R3230 | 556 | 644 | 113.46
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | B:PACKT3 | 556 | 644 | 113.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | T:78&79 | 556 | 644 | 113.34
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:DKSR/WRFL | 556 | 644 | 113.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/WF/NWES | 556 | 644 | 113.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/WRFL | 556 | 644 | 113.27
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | SB:HUNT230_R1502 | 556 | 644 | 113.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | B:PACKT3 | 556 | 644 | 113.25
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | B:PACKT3 | 556 | 644 | 113.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | SB:PA230_R3230 | 556 | 644 | 113.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | SB:PA230_R3230 | 556 | 644 | 113.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | S:PA_HNTL78 | 556 | 644 | 113.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | SB:HUNT230_R1502 | 556 | 644 | 113
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | SB:HUNT230_R1502 | 556 | 644 | 113
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | T:78&79 | 556 | 644 | 112.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | S:PA_HNTL78 | 556 | 644 | 112.96
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R3230 | 556 | 644 | 112.94
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | B:PACKT3 | 556 | 644 | 112.9
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1502 | 556 | 644 | 112.9
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | B:PACKT3 | 556 | 644 | 112.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | S:PA_HNTL78 | 556 | 644 | 112.86
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | B:Hunt68 | 556 | 644 | 112.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_R833 | 556 | 644 | 112.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | SB:HUNT230_R1502 | 556 | 644 | 112.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:GARD72&79 | 556 | 644 | 112.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | B:PACKT3 | 556 | 644 | 112.74
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | T:78&79 | 556 | 644 | 112.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | T:78&79 | 556 | 644 | 112.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | HUNTLEY - PACKARD 78 230 | 556 | 644 | 112.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 112.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:78&79 | 556 | 644 | 112.64
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | SB:HUNT230_R1502 | 556 | 644 | 112.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:KINTIGH | 556 | 644 | 112.61
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:68&160 | 556 | 644 | 112.6
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | SB:HUNT230_R1502 | 556 | 644 | 112.59
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_R823 | 556 | 644 | 112.58
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | B:Hunt68 | 556 | 644 | 112.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | T:78&79 | 556 | 644 | 112.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 112.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1402 | 556 | 644 | 112.46
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | SB:HUNT230_R1502 | 556 | 644 | 112.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:73&74 | 556 | 644 | 112.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | SB:HUNT230_R1502 | 556 | 644 | 112.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | T:78&79 | 556 | 644 | 112.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | SB:HUNT230_R1502 | 556 | 644 | 112.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | T:78&79 | 556 | 644 | 112.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | SB:HUNT230_R1502 | 556 | 644 | 112.25
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | T:78&79 | 556 | 644 | 112.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1402 | 556 | 644 | 112.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | B:Hunt68 | 556 | 644 | 112.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | SB:HUNT230_R1502 | 556 | 644 | 112.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | SB:HUNT230_R1502 | 556 | 644 | 112.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | SB:HUNT230_R1502 | 556 | 644 | 112.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | T:78&79 | 556 | 644 | 112.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | T:78&79 | 556 | 644 | 112.11
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - GARDENVILL 80 230 | 556 | 644 | 112.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:HNT_GRD80 | 556 | 644 | 112.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 112.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1402 | 556 | 644 | 111.99
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - GARDENVILL 79 230 | 556 | 644 | 111.99
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:78&79 | 556 | 644 | 111.98
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 111.97
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | T:78&79 | 556 | 644 | 111.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | S:PA_HNTL78 | 556 | 644 | 111.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | T:78&79 | 556 | 644 | 111.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | T:78&79 | 556 | 644 | 111.91
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | T:78&79 | 556 | 644 | 111.91
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | T:78&79 | 556 | 644 | 111.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1402 | 556 | 644 | 111.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | SB:PA230_R304 | 556 | 644 | 111.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:DUNK230_R1312 | 556 | 644 | 111.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | SB:PA230_R304 | 556 | 644 | 111.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R304 | 556 | 644 | 111.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | SB:PA230_R304 | 556 | 644 | 111.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | SB:PA230_R304 | 556 | 644 | 111.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | B:Hunt68 | 556 | 644 | 110.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | SB:PA230_R3230 | 556 | 644 | 110.92
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:Hunt68 | 556 | 644 | 110.92
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | B:Hunt68 | 556 | 644 | 110.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R304 | 556 | 644 | 110.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | B:PACKT3 | 556 | 644 | 110.64
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:GARD73&80 | 556 | 644 | 110.64
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1402 | 556 | 644 | 110.63
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R304 | 556 | 644 | 110.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R3230 | 556 | 644 | 110.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | SB:HUNT230_R1502 | 556 | 644 | 110.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:BRUCE5 | 556 | 644 | 110.53
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | S:PA_HNTL78 | 556 | 644 | 110.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1402 | 556 | 644 | 110.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | SB:HUNT230_R1502 | 556 | 644 | 110.46
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | SB:HUNT230_R1502 | 556 | 644 | 110.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | SB:HUNT230_R1502 | 556 | 644 | 110.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | SB:HUNT230_R1502 | 556 | 644 | 110.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | SB:HUNT230_R1502 | 556 | 644 | 110.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | SB:HUNT230_R1502 | 556 | 644 | 110.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | SB:HUNT230_R1502 | 556 | 644 | 110.35
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | SB:PA230_R304 | 556 | 644 | 110.33
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | T:78&79 | 556 | 644 | 110.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:HUNT230_R1502 | 556 | 644 | 110.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:HUNT230_R1502 | 556 | 644 | 110.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | T:78&79 | 556 | 644 | 110.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:HUNT230_R1502 | 556 | 644 | 110.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_R873 | 556 | 644 | 110.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | T:78&79 | 556 | 644 | 110.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | T:78&79 | 556 | 644 | 110.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 110.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | WTHRS - MEYER 230 | 556 | 644 | 110.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | T:78&79 | 556 | 644 | 110.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | T:78&79 | 556 | 644 | 110.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | T:78&79 | 556 | 644 | 110.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | T:78&79 | 556 | 644 | 110.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:MEYER | 556 | 644 | 110.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | SB:PA230_R304 | 556 | 644 | 109.95
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | T:78&79 | 556 | 644 | 109.95
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | T:78&79 | 556 | 644 | 109.94
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | SB:PA230_R304 | 556 | 644 | 109.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | T:78&79 | 556 | 644 | 109.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | SB:HUNT230_R1502 | 556 | 644 | 109.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | SB:HUNT230_R1502 | 556 | 644 | 109.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | SB:HUNT230_R1502 | 556 | 644 | 109.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | S:PA_HNTL78 | 556 | 644 | 109.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R304 | 556 | 644 | 109.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1502 | 556 | 644 | 109.72
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | T:78&79 | 556 | 644 | 109.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | T:78&79 | 556 | 644 | 109.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | T:78&79 | 556 | 644 | 109.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | SB:HUNT230_R1502 | 556 | 644 | 109.59
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:DARLIN1 | 556 | 644 | 109.53
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | T:78&79 | 556 | 644 | 109.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | SB:HUNT230_R1502 | 556 | 644 | 109.37
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | T:78&79 | 556 | 644 | 109.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | SB:HUNT230_R1502 | 556 | 644 | 109.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | SB:HUNT230_R1502 | 556 | 644 | 109.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | SB:HUNT230_R1502 | 556 | 644 | 109.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | T:78&79 | 556 | 644 | 109.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | SB:HUNT230_R1502 | 556 | 644 | 109.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | SB:HUNT230_R1502 | 556 | 644 | 109.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | T:78&79 | 556 | 644 | 109.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | SB:HUNT230_R1502 | 556 | 644 | 109.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | T:78&79 | 556 | 644 | 109
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | T:78&79 | 556 | 644 | 108.92
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | T:78&79 | 556 | 644 | 108.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | T:78&79 | 556 | 644 | 108.83
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | SB:HUNT230_R1502 | 556 | 644 | 108.8
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | SB:HUNT230_R1502 | 556 | 644 | 108.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | T:78&79 | 556 | 644 | 108.76
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | SB:HUNT230_R1502 | 556 | 644 | 108.72
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | SB:HUNT230_R1502 | 556 | 644 | 108.71
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | SB:HUNT230_R1502 | 556 | 644 | 108.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_R833 | 556 | 644 | 108.7
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | T:78&79 | 556 | 644 | 108.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | T:78&79 | 556 | 644 | 108.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_R823 | 556 | 644 | 108.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | T:78&79 | 556 | 644 | 108.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | T:78&79 | 556 | 644 | 108.46
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | T:78&79 | 556 | 644 | 108.45
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | SB:HUNT230_R1502 | 556 | 644 | 108.45
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | SB:HUNT230_R1502 | 556 | 644 | 108.41
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | SB:HUNT230_R1502 | 556 | 644 | 108.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | SB:HUNT230_R1502 | 556 | 644 | 108.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | SB:HUNT230_R1502 | 556 | 644 | 108.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | T:78&79 | 556 | 644 | 108.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | T:78&79 | 556 | 644 | 108.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | SB:HUNT230_R1502 | 556 | 644 | 108.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | SB:HUNT230_R1502 | 556 | 644 | 108.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | SB:HUNT230_R1502 | 556 | 644 | 108.11
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | T:78&79 | 556 | 644 | 108.08
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | T:78&79 | 556 | 644 | 108.08
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | SB:HUNT230_R1502 | 556 | 644 | 108.08
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | SB:HUNT230_R1502 | 556 | 644 | 108.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | T:78&79 | 556 | 644 | 108.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:GARD72&79 | 556 | 644 | 107.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-2 345 | SB:HUNT230_R1502 | 556 | 644 | 107.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-1 345 | SB:HUNT230_R1502 | 556 | 644 | 107.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | SB:HUNT230_R1502 | 556 | 644 | 107.96
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R3230 | 556 | 644 | 107.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | T:78&79 | 556 | 644 | 107.93
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | SB:PA230_R304 | 556 | 644 | 107.91
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | T:78&79 | 556 | 644 | 107.91
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | SB:HUNT230_R1502 | 556 | 644 | 107.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | T:78&79 | 556 | 644 | 107.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | SB:HUNT230_R1502 | 556 | 644 | 107.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | SB:HUNT230_R1502 | 556 | 644 | 107.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | T:78&79 | 556 | 644 | 107.84
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | T:78&79 | 556 | 644 | 107.83
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | B:PACKT3 | 556 | 644 | 107.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | SB:HUNT230_R1502 | 556 | 644 | 107.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | SB:HUNT230_R1502 | 556 | 644 | 107.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | SB:HUNT230_R1502 | 556 | 644 | 107.8
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - FITZ 345 | SB:HUNT230_R1502 | 556 | 644 | 107.79
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | SB:HUNT230_R1502 | 556 | 644 | 107.79
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | SB:HUNT230_R1502 | 556 | 644 | 107.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-2 345 | T:78&79 | 556 | 644 | 107.78
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | SB:HUNT230_R1502 | 556 | 644 | 107.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | T:78&79 | 556 | 644 | 107.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL - CLAY PC-1 345 | T:78&79 | 556 | 644 | 107.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | B:Hunt68 | 556 | 644 | 107.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:HUNT230_R1502 | 556 | 644 | 107.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | T:78&79 | 556 | 644 | 107.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | T:78&79 | 556 | 644 | 107.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | T:78&79 | 556 | 644 | 107.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | B:PACKT3 | 556 | 644 | 107.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OS - EL - LFYTE 17 345 | SB:HUNT230_R1502 | 556 | 644 | 107.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | EDIC - FITZ 345 | T:78&79 | 556 | 644 | 107.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | T:78&79 | 556 | 644 | 107.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | T:78&79 | 556 | 644 | 107.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | T:78&79 | 556 | 644 | 107.55
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 1TR | SB:HUNT230_R1502 | 556 | 644 | 107.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 2TR | SB:HUNT230_R1502 | 556 | 644 | 107.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | VOL - MARCY 19 345 | SB:HUNT230_R1502 | 556 | 644 | 107.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | T:78&79 | 556 | 644 | 107.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | T:78&79 | 556 | 644 | 107.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 3TR | SB:HUNT230_R1502 | 556 | 644 | 107.53
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | T:78&79 | 556 | 644 | 107.53
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 1TR | SB:HUNT230_R1502 | 556 | 644 | 107.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 2TR | SB:HUNT230_R1502 | 556 | 644 | 107.49
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | T:78&79 | 556 | 644 | 107.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1402 | 556 | 644 | 107.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OS - EL - LFYTE 17 345 | T:78&79 | 556 | 644 | 107.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | SB:HUNT230_R1502 | 556 | 644 | 107.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | SB:HUNT230_R1502 | 556 | 644 | 107.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | SB:HUNT230_R1502 | 556 | 644 | 107.35
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | SB:HUNT230_R1502 | 556 | 644 | 107.35
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 1TR | T:78&79 | 556 | 644 | 107.34
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 2TR | T:78&79 | 556 | 644 | 107.34
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PANL 345/115 3TR | T:78&79 | 556 | 644 | 107.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | VOL - MARCY 19 345 | T:78&79 | 556 | 644 | 107.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 1TR | T:78&79 | 556 | 644 | 107.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY 345/115 2TR | T:78&79 | 556 | 644 | 107.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - GARDENVILL 80 230 | 556 | 644 | 107.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:HNT_GRD80 | 556 | 644 | 107.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - TEAL 11 115 | T:78&79 | 556 | 644 | 107.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 3 115 | T:78&79 | 556 | 644 | 107.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - TEAL 10 115 | T:78&79 | 556 | 644 | 107.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - LM 14 115 | T:78&79 | 556 | 644 | 107.19
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1402 | 556 | 644 | 107.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - GARDENVILL 79 230 | 556 | 644 | 107.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 5 115 | T:78&79 | 556 | 644 | 107.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LHH - CLAY 7 115 | T:78&79 | 556 | 644 | 107.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | T:78&79 | 556 | 644 | 107.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 107.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FUL - CLAY 4 115 | T:78&79 | 556 | 644 | 107.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - WOOD 17 115 | T:78&79 | 556 | 644 | 107.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA - VOL 21 345 | T:78&79 | 556 | 644 | 107.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA 345/115 1TR | T:78&79 | 556 | 644 | 107.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SCRIBA 345/115 2TR | T:78&79 | 556 | 644 | 107.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | T:78&79 | 556 | 644 | 107.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | T:78&79 | 556 | 644 | 107.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | T:78&79 | 556 | 644 | 107.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - PACKARD 78 230 | 556 | 644 | 107.12
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | S:PA_HNTL78 | 556 | 644 | 107.12
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | T:78&79 | 556 | 644 | 107.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | T:78&79 | 556 | 644 | 107.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | B:Hunt68 | 556 | 644 | 106.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:Hunt68 | 556 | 644 | 105.95
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | SB:HUNT230_R1502 | 556 | 644 | 105.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | SB:HUNT230_R1502 | 556 | 644 | 105.79
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1402 | 556 | 644 | 105.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:GARD73&80 | 556 | 644 | 105.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | B:Hunt68 | 556 | 644 | 105.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | SB:HUNT230_R1502 | 556 | 644 | 105.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | SB:HUNT230_R1502 | 556 | 644 | 105.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | SB:HUNT230_R1502 | 556 | 644 | 105.67
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | SB:HUNT230_R1502 | 556 | 644 | 105.67
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | T:78&79 | 556 | 644 | 105.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | SB:HUNT230_R1502 | 556 | 644 | 105.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | SB:HUNT230_R1502 | 556 | 644 | 105.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | SB:HUNT230_R1502 | 556 | 644 | 105.63
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | T:78&79 | 556 | 644 | 105.55
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | SB:HUNT230_R1502 | 556 | 644 | 105.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | SB:HUNT230_R1502 | 556 | 644 | 105.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | SB:HUNT230_R1502 | 556 | 644 | 105.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | SB:HUNT230_R1502 | 556 | 644 | 105.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:HUNT230_R1502 | 556 | 644 | 105.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | T:78&79 | 556 | 644 | 105.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:HUNT230_R1502 | 556 | 644 | 105.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | SB:HUNT230_R1502 | 556 | 644 | 105.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | T:78&79 | 556 | 644 | 105.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | T:78&79 | 556 | 644 | 105.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | T:78&79 | 556 | 644 | 105.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:Hunt68 | 556 | 644 | 105.41
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1402 | 556 | 644 | 105.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:HUNT230_R1502 | 556 | 644 | 105.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_R873 | 556 | 644 | 105.37
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R304 | 556 | 644 | 105.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | T:78&79 | 556 | 644 | 105.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | T:78&79 | 556 | 644 | 105.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | T:78&79 | 556 | 644 | 105.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | T:78&79 | 556 | 644 | 105.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | T:78&79 | 556 | 644 | 105.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | T:78&79 | 556 | 644 | 105.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | T:78&79 | 556 | 644 | 105.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | T:78&79 | 556 | 644 | 105.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R304 | 556 | 644 | 105.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | B:Hunt68 | 556 | 644 | 105.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1402 | 556 | 644 | 105.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | SB:HUNT230_R1502 | 556 | 644 | 104.95
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | SB:HUNT230_R1502 | 556 | 644 | 104.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | SB:HUNT230_R1502 | 556 | 644 | 104.77
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | SB:HUNT230_R1402 | 556 | 644 | 104.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | SB:HUNT230_R1502 | 556 | 644 | 104.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | T:78&79 | 556 | 644 | 104.72
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | T:78&79 | 556 | 644 | 104.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | T:78&79 | 556 | 644 | 104.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | T:78&79 | 556 | 644 | 104.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | SB:HUNT230_R1502 | 556 | 644 | 104.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | SB:HUNT230_R1502 | 556 | 644 | 104.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | SB:HUNT230_R1502 | 556 | 644 | 104.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | SB:HUNT230_R1502 | 556 | 644 | 104.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | SB:HUNT230_R1502 | 556 | 644 | 104.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | SB:HUNT230_R1502 | 556 | 644 | 104.39
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | SB:HUNT230_R1502 | 556 | 644 | 104.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | T:78&79 | 556 | 644 | 104.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | T:78&79 | 556 | 644 | 104.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | T:78&79 | 556 | 644 | 104.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | T:78&79 | 556 | 644 | 104.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | T:78&79 | 556 | 644 | 104.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | B:Hunt68 | 556 | 644 | 104.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | T:78&79 | 556 | 644 | 104.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | T:78&79 | 556 | 644 | 104.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | SB:HUNT230_R1502 | 556 | 644 | 103.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | SB:HUNT230_R1502 | 556 | 644 | 103.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | SB:HUNT230_R1502 | 556 | 644 | 103.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | SB:HUNT230_R1502 | 556 | 644 | 103.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | SB:HUNT230_R1502 | 556 | 644 | 103.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | SB:HUNT230_R1502 | 556 | 644 | 103.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | SB:HUNT230_R1502 | 556 | 644 | 103.95
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | SB:HUNT230_R1502 | 556 | 644 | 103.84
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | SB:HUNT230_R1402 | 556 | 644 | 103.84
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | T:78&79 | 556 | 644 | 103.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | T:78&79 | 556 | 644 | 103.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | T:78&79 | 556 | 644 | 103.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | T:78&79 | 556 | 644 | 103.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | T:78&79 | 556 | 644 | 103.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | T:78&79 | 556 | 644 | 103.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | T:78&79 | 556 | 644 | 103.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | T:78&79 | 556 | 644 | 103.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | SB:HUNT230_R1502 | 556 | 644 | 103.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | T:78&79 | 556 | 644 | 103.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | SB:HUNT230_R1502 | 556 | 644 | 103.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | SB:HUNT230_R1502 | 556 | 644 | 103.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | B:Hunt68 | 556 | 644 | 103.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R3230 | 556 | 644 | 103.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | B:Hunt68 | 556 | 644 | 103.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | T:78&79 | 556 | 644 | 103.11
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | T:78&79 | 556 | 644 | 103.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | B:PACKT3 | 556 | 644 | 102.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:HUNT230_R1502 | 556 | 644 | 102.95
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | B:Hunt68 | 556 | 644 | 102.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1402 | 556 | 644 | 102.9
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | SB:HUNT230_R1402 | 556 | 644 | 102.81
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | T:78&79 | 556 | 644 | 102.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | SB:HUNT230_R1502 | 556 | 644 | 102.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | SB:HUNT230_R1402 | 556 | 644 | 102.6
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | B:Hunt68 | 556 | 644 | 102.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1502 | 556 | 644 | 102.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | T:78&79 | 556 | 644 | 102.46
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | B:Hunt68 | 556 | 644 | 102.45
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | T:78&79 | 556 | 644 | 102.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | SB:HUNT230_R1402 | 556 | 644 | 102.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | B:Hunt68 | 556 | 644 | 102.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1402 | 556 | 644 | 102.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | SB:HUNT230_R1402 | 556 | 644 | 101.87
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | B:Hunt68 | 556 | 644 | 101.78
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | B:Hunt68 | 556 | 644 | 101.67
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | B:Hunt68 | 556 | 644 | 101.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:Hunt68 | 556 | 644 | 101.64
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | B:Hunt68 | 556 | 644 | 101.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | SB:HUNT230_R1402 | 556 | 644 | 101.45
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | B:Hunt68 | 556 | 644 | 101.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | SB:HUNT230_R1402 | 556 | 644 | 101.37
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | SB:HUNT230_R1402 | 556 | 644 | 101.37
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1402 | 556 | 644 | 101.33
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | SB:HUNT230_R1402 | 556 | 644 | 101.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | B:Hunt68 | 556 | 644 | 101.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | B:Hunt68 | 556 | 644 | 101.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | B:Hunt68 | 556 | 644 | 101.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | B:Hunt68 | 556 | 644 | 101.15
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | SB:HUNT230_R1402 | 556 | 644 | 101.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | SB:HUNT230_R1502 | 556 | 644 | 100.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_R1402 | 556 | 644 | 100.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | SB:HUNT230_R1402 | 556 | 644 | 100.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | SB:HUNT230_R1402 | 556 | 644 | 100.83
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | SB:HUNT230_R1402 | 556 | 644 | 100.83
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | SB:HUNT230_R1402 | 556 | 644 | 100.83
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | SB:HUNT230_R1502 | 556 | 644 | 100.81
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | T:78&79 | 556 | 644 | 100.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | SB:HUNT230_R1502 | 556 | 644 | 100.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | SB:HUNT230_R1502 | 556 | 644 | 100.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | SB:HUNT230_R1502 | 556 | 644 | 100.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | T:78&79 | 556 | 644 | 100.67
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | T:78&79 | 556 | 644 | 100.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | T:78&79 | 556 | 644 | 100.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | T:78&79 | 556 | 644 | 100.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R3230 | 556 | 644 | 100.14
| 135303 SAWYER77 230 135415 PACKARD2 230 1 Max |  |  |  |  | 152.48
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 566 | 654 | 137.87
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 136.73
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 230 | 566 | 654 | 136.54
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 566 | 654 | 135.89
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 134.85
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | B:PACKT4 | 566 | 654 | 134.78
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 133.99
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:61&64 | 566 | 654 | 133.43
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 133.34
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 133.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL77 | 566 | 654 | 132.69
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | B:PACKT4 | 566 | 654 | 132.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_T7-12 | 566 | 654 | 131.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | SB:PA230_R506 | 566 | 654 | 131.44
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | B:PACKT4 | 566 | 654 | 130.96
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 566 | 654 | 130.89
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3430 | 566 | 654 | 130.64
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 130.62
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 566 | 654 | 129.96
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 566 | 654 | 129.34
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R506 | 566 | 654 | 129.1
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 129.05
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 566 | 654 | 129.04
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 230 | 566 | 654 | 128.96
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:255_345B302 | 566 | 654 | 128.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAG345_3108 | 566 | 654 | 128.53
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - NEWROCH 1 345 | 566 | 654 | 128.48
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 128.32
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | B:PACKT4 | 566 | 654 | 128.29
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 128.21
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3430 | 566 | 654 | 127.89
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R506 | 566 | 654 | 127.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 127.44
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:255_345B202 | 566 | 654 | 127.11
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SOMERSET - NEWROCH 1 345 | 566 | 654 | 127.03
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 126.97
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3430 | 566 | 654 | 126.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 126.71
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 566 | 654 | 126.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:61&64 | 566 | 654 | 126.4
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | B:PACKT4 | 566 | 654 | 126.25
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | B:PACKT4 | 566 | 654 | 125.97
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_T7-12 | 566 | 654 | 125.5
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL77 | 566 | 654 | 125
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | B:PACKT4 | 566 | 654 | 124.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R506 | 566 | 654 | 124.59
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 124.38
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 566 | 654 | 124.19
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:40&41 | 566 | 654 | 124.16
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R3430 | 566 | 654 | 124.08
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | B:PACKT4 | 566 | 654 | 123.87
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 566 | 654 | 123.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | SB:PA230_R506 | 566 | 654 | 123.09
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - HOMERCTY | 566 | 654 | 122.96
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-FV_37&W-F_171 | 566 | 654 | 122.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:41&33 | 566 | 654 | 122.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:255_345B302 | 566 | 654 | 122.7
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 122.67
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 566 | 654 | 122.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAG345_3108 | 566 | 654 | 122.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - NEWROCH 1 345 | 566 | 654 | 122.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAW230_2014 | 566 | 654 | 122.55
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | SB:PA230_R506 | 566 | 654 | 122.47
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3430 | 566 | 654 | 122.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R506 | 566 | 654 | 121.96
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:34&42 | 566 | 654 | 121.93
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 121.88
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3430 | 566 | 654 | 121.79
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 121.77
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA 230/115 1TR | 566 | 654 | 121.76
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_1 | 566 | 654 | 121.49
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_2 | 566 | 654 | 121.49
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | B:PACKT4 | 566 | 654 | 121.48
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | LFYTE - CLARKCRNS 36A 345 | 566 | 654 | 121.46
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAFA_ELB | 566 | 654 | 121.45
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAFAYETT | 566 | 654 | 121.4
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 121.11
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:255_345B202 | 566 | 654 | 121.09
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SOMERSET - NEWROCH 1 345 | 566 | 654 | 121.01
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_4 | 566 | 654 | 120.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_3 | 566 | 654 | 120.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | PACKARD 230/115 3TR | 566 | 654 | 120.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R506 | 566 | 654 | 120.77
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B5 | 566 | 654 | 120.67
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3430 | 566 | 654 | 120.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B6 | 566 | 654 | 120.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - CLARKCRNS 36B 345 | 566 | 654 | 120.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE_B | 566 | 654 | 120.5
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 566 | 654 | 120.31
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | B:PACKT4 | 566 | 654 | 120.21
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:31&41 | 566 | 654 | 120.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_42-4182 | 566 | 654 | 120.05
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 119.97
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3208 | 566 | 654 | 119.82
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R915 | 566 | 654 | 119.78
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:MP11&41 | 566 | 654 | 119.77
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3430 | 566 | 654 | 119.67
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_4182 | 566 | 654 | 119.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3202 | 566 | 654 | 119.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - COOPERS 345 SC | 566 | 654 | 119.61
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:30&40 | 566 | 654 | 119.49
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAG345_3308 | 566 | 654 | 119.35
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT4 | 566 | 654 | 119.33
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:77&76 | 566 | 654 | 119.25
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - KINTIGH 345 | 566 | 654 | 119.24
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R400 | 566 | 654 | 119.22
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R935 | 566 | 654 | 119.02
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FRASER 345 SC | 566 | 654 | 119
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:FRAS345_B1-4062 | 566 | 654 | 119
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | B:PACKT4 | 566 | 654 | 118.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:FRAS345_40-B262 | 566 | 654 | 118.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 118.96
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | B:PACKT4 | 566 | 654 | 118.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 77 230 | 566 | 654 | 118.91
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 118.69
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:69J&70K | 566 | 654 | 118.64
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:170 | 566 | 654 | 118.62
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:180 | 566 | 654 | 118.62
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL77 | 566 | 654 | 118.58
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._99 | 566 | 654 | 118.56
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._77 | 566 | 654 | 118.5
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3308 | 566 | 654 | 118.48
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:MP12&18 | 566 | 654 | 118.48
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:160 | 566 | 654 | 118.47
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:150 | 566 | 654 | 118.47
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:40&41 | 566 | 654 | 118.44
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_3414 | 566 | 654 | 118.44
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_3514 | 566 | 654 | 118.43
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:PECHBTM2 | 566 | 654 | 118.42
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:W89&W90 | 566 | 654 | 118.41
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R140 | 566 | 654 | 118.37
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:90 | 566 | 654 | 118.36
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - N.SCOT99 I8 345 | 566 | 654 | 118.33
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3314 | 566 | 654 | 118.33
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:F38&F39 | 566 | 654 | 118.33
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 118.33
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE | 566 | 654 | 118.28
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_2T8082 | 566 | 654 | 118.23
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:SUSQ1 | 566 | 654 | 118.22
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3108 | 566 | 654 | 118.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - N.SCOT77 I4 345 | 566 | 654 | 118.19
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:F30&F31 | 566 | 654 | 118.17
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_376512 | 566 | 654 | 118.14
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_31153 | 566 | 654 | 118.12
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_34XC | 566 | 654 | 118.08
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 118.06
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R935 | 566 | 654 | 118.05
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PV345_RNS5 | 566 | 654 | 118.05
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - 5MILE 345 | 566 | 654 | 118.05
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R945 | 566 | 654 | 118.05
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:FV-5M_37&W-F_171 | 566 | 654 | 118.04
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-SR_37&W-F_171 | 566 | 654 | 118.04
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PV345_RNS4 | 566 | 654 | 118.03
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LEEDS345_R9293 | 566 | 654 | 117.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:SALEMG1 | 566 | 654 | 117.96
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:HOPECG1 | 566 | 654 | 117.95
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:LIMERCK2 | 566 | 654 | 117.94
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_3456 | 566 | 654 | 117.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | HUNTLEY - PACKARD 77 230 | 566 | 654 | 117.89
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_34-B382 | 566 | 654 | 117.87
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_B2-3482 | 566 | 654 | 117.87
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | HURLEY - ROCKT CMT/MTR-34 345 | 566 | 654 | 117.87
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CMT/MTR-34 345 | 566 | 654 | 117.87
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | B:PACKT4 | 566 | 654 | 117.85
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 566 | 654 | 117.84
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R506 | 566 | 654 | 117.82
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R150 | 566 | 654 | 117.8
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3908 | 566 | 654 | 117.79
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R160 | 566 | 654 | 117.79
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3808 | 566 | 654 | 117.79
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - DEW 13 345 | 566 | 654 | 117.73
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LEEDS345_R94301 | 566 | 654 | 117.72
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R110 | 566 | 654 | 117.69
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_4255 | 566 | 654 | 117.69
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL77 | 566 | 654 | 117.69
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R150 | 566 | 654 | 117.67
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R160 | 566 | 654 | 117.67
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_B2-4282 | 566 | 654 | 117.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 566 | 654 | 117.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 566 | 654 | 117.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 1-16 345 | 566 | 654 | 117.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 566 | 654 | 117.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 566 | 654 | 117.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DUNW345_3 | 566 | 654 | 117.64
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R10 | 566 | 654 | 117.63
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 566 | 654 | 117.61
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LEEDS345_R92 | 566 | 654 | 117.61
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 566 | 654 | 117.61
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3102 | 566 | 654 | 117.6
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 566 | 654 | 117.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 566 | 654 | 117.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DUNW345_8 | 566 | 654 | 117.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FITZ 345 | 566 | 654 | 117.56
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FITZ - EDIC FEI 345 | 566 | 654 | 117.56
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DEWI345_R915 | 566 | 654 | 117.55
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DEWI345_R130 | 566 | 654 | 117.55
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DEWI345_R220 | 566 | 654 | 117.55
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | VOLNEY - MARCY I9 345 | 566 | 654 | 117.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | VOL - MARCY 19 345 | 566 | 654 | 117.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:VOLN_R925 | 566 | 654 | 117.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3914 | 566 | 654 | 117.49
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3814 | 566 | 654 | 117.48
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:JAMESGN7 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 117.36
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R3430 | 566 | 654 | 117.24
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - HOMERCTY | 566 | 654 | 117.19
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 117.09
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-FV_37&W-F_171 | 566 | 654 | 117.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 117.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | S:PA_HNTL77 | 566 | 654 | 117.06
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:41&33 | 566 | 654 | 117.03
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 116.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 116.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R506 | 566 | 654 | 116.75
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS2 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 116.69
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 116.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | B:PACKT4 | 566 | 654 | 116.62
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 116.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | B:PACKT4 | 566 | 654 | 116.57
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 116.57
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 116.57
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 116.45
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-1 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 116.4
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 116.4
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | B:PACKT4 | 566 | 654 | 116.38
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:34&42 | 566 | 654 | 116.14
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3430 | 566 | 654 | 115.97
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | B:PACKT4 | 566 | 654 | 115.94
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | S:PA_HNTL77 | 566 | 654 | 115.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDL - FRASER 32 345 | 566 | 654 | 115.91
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FRASER - OAKDLE 32 345 | 566 | 654 | 115.91
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT2 | 566 | 654 | 115.89
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RAIN345_1W | 566 | 654 | 115.89
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R506 | 566 | 654 | 115.89
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RAIN345_9W | 566 | 654 | 115.88
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:FRAS345_B1-3262 | 566 | 654 | 115.87
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: RAVENSWOOD | 566 | 654 | 115.86
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:30 | 566 | 654 | 115.86
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | BWLN - WHAV -LDN 67 345 | 566 | 654 | 115.86
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT1 | 566 | 654 | 115.86
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B2 | 566 | 654 | 115.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROSE345_30553 | 566 | 654 | 115.76
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_4-56-2 | 566 | 654 | 115.75
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 2TR | 566 | 654 | 115.73
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_1-56-2 | 566 | 654 | 115.72
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_6-56-2 | 566 | 654 | 115.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_1 | 566 | 654 | 115.68
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_2 | 566 | 654 | 115.68
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAFA_ELB | 566 | 654 | 115.68
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | LFYTE - CLARKCRNS 36A 345 | 566 | 654 | 115.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_3-56-2 | 566 | 654 | 115.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B3 | 566 | 654 | 115.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - WTRCR 31 345 | 566 | 654 | 115.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:NOEND | 566 | 654 | 115.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | SB:PA230_R506 | 566 | 654 | 115.63
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROSE345_30551 | 566 | 654 | 115.62
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROSE345_31152 | 566 | 654 | 115.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAFAYETT | 566 | 654 | 115.6
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RMP345_T1500 | 566 | 654 | 115.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M7TR | 566 | 654 | 115.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 2TR | B:PACKT4 | 566 | 654 | 115.58
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | RAMAPO - BRNCHBRG 5018 345 | 566 | 654 | 115.58
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON2 | 566 | 654 | 115.58
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WATRC345_31-2 | 566 | 654 | 115.57
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2208 | 566 | 654 | 115.55
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RMP345_1500-2X | 566 | 654 | 115.54
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2214 | 566 | 654 | 115.54
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS17-20 | 566 | 654 | 115.54
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2224 | 566 | 654 | 115.54
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | SB:PA230_R506 | 566 | 654 | 115.53
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1724 | 566 | 654 | 115.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1714 | 566 | 654 | 115.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1524 | 566 | 654 | 115.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1514 | 566 | 654 | 115.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1508 | 566 | 654 | 115.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2524 | 566 | 654 | 115.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2514 | 566 | 654 | 115.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS21-24 | 566 | 654 | 115.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2508 | 566 | 654 | 115.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | B:PACKT4 | 566 | 654 | 115.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON1 | 566 | 654 | 115.44
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3208 | 566 | 654 | 115.35
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M6TR | 566 | 654 | 115.35
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M8TR | 566 | 654 | 115.35
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:AT_R6361 | 566 | 654 | 115.31
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BESICORP | 566 | 654 | 115.31
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:EMPIRE | 566 | 654 | 115.3
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | S:EMPIRE | 566 | 654 | 115.24
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: IND PT 2 | 566 | 654 | 115.15
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN GILBOA #3&4 | 566 | 654 | 115.13
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3302 | 566 | 654 | 115.13
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R3430 | 566 | 654 | 115.09
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN GILBOA #1&2 | 566 | 654 | 115.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3202 | 566 | 654 | 115.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3308 | 566 | 654 | 115.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHN_11 | 566 | 654 | 115.06
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHN_9 | 566 | 654 | 115.06
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:NTHF3&4 | 566 | 654 | 115.05
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:72&69 | 566 | 654 | 115.05
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHN_7 | 566 | 654 | 115.04
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - FARMVLY | 566 | 654 | 115.02
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_4 | 566 | 654 | 115.01
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_3 | 566 | 654 | 115.01
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | BECK - PACKARD BP76 230 | 566 | 654 | 114.99
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:JAMESGN7 | B:PACKT4 | 566 | 654 | 114.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: IND PT 3 | 566 | 654 | 114.97
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | B:PACKT4 | 566 | 654 | 114.94
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHS_3 | 566 | 654 | 114.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHS_1 | 566 | 654 | 114.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | S:PA_HNTL77 | 566 | 654 | 114.88
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | S:PA_HNTL77 | 566 | 654 | 114.86
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B5 | 566 | 654 | 114.85
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:67&68&BW | 566 | 654 | 114.84
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B6 | 566 | 654 | 114.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - CLARKCRNS 36B 345 | 566 | 654 | 114.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3430 | 566 | 654 | 114.78
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - FARMVLY | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.73
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | HILLSIDE 230/115 4TR | 566 | 654 | 114.73
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:HILLSIDE | 566 | 654 | 114.73
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HILL_B412 | 566 | 654 | 114.73
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | SB:PA230_R3430 | 566 | 654 | 114.72
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:SITHE 2 | 566 | 654 | 114.72
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:SITHE 1 | 566 | 654 | 114.72
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 2TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.72
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE_B | 566 | 654 | 114.71
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:BETHSTM | 566 | 654 | 114.71
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 13 345 | B:PACKT4 | 566 | 654 | 114.71
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HCWC/NWES | 566 | 654 | 114.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:MBWC/NWES | 566 | 654 | 114.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | S:PA_HNTL77 | 566 | 654 | 114.64
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | HUNTLEY - ELM 70 230 | 566 | 654 | 114.63
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WATRC345_30-3142 | 566 | 654 | 114.61
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | WTRCR - MAINSBRG 30A 345 | 566 | 654 | 114.61
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WATRC345_B1-3042 | 566 | 654 | 114.6
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-SR_37&W-F_171 | B:PACKT4 | 566 | 654 | 114.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:FV-5M_37&W-F_171 | B:PACKT4 | 566 | 654 | 114.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M7TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:120_130 | 566 | 654 | 114.58
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:130 | 566 | 654 | 114.58
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:W97&W98 | 566 | 654 | 114.58
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HILL_68-B412 | 566 | 654 | 114.54
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | STNYRDG - HILLSIDE 68B 230 | 566 | 654 | 114.5
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 7-9 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.5
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 10-12 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.5
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | BECK - PACKARD BP76 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.49
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 1-3 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.49
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 4-6 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.49
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-WC_30&W-F_171 | 566 | 654 | 114.48
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | SB:PA230_R506 | 566 | 654 | 114.42
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - 5MILE 345 | B:PACKT4 | 566 | 654 | 114.37
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M6TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.37
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M8TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.37
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS2 | B:PACKT4 | 566 | 654 | 114.34
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HCMB/NWES | 566 | 654 | 114.32
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:31&41 | 566 | 654 | 114.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | MAINSBRG - HOMERCITY 30B 345 | 566 | 654 | 114.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | S:PA_HNTL77 | 566 | 654 | 114.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL - DUNKIRK 73 230 | 566 | 654 | 114.25
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DEWITT3 - LAFAYTTE 345 | B:PACKT4 | 566 | 654 | 114.24
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_42-4182 | 566 | 654 | 114.23
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL - DUNKIRK 74 230 | 566 | 654 | 114.23
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:DUNKG3 | 566 | 654 | 114.22
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - WATERCURE 69 230 | B:PACKT4 | 566 | 654 | 114.21
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - ETWANDA 70 230 | B:PACKT4 | 566 | 654 | 114.21
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:PACKT4 | 566 | 654 | 114.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3430 | 566 | 654 | 114.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-MB_30&W-F_171 | 566 | 654 | 114.15
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:KINT_39-B112 | 566 | 654 | 114.15
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - BECK_TSA 345 | B:PACKT4 | 566 | 654 | 114.13
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - BECK_TSB 345 | B:PACKT4 | 566 | 654 | 114.13
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STNYRDG - HILLSIDE 68B 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.11
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 73 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.1
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - EDIC 2-15 345 | B:PACKT4 | 566 | 654 | 114.1
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:KINT_B1-3812 | 566 | 654 | 114.09
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 74 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 114.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-2 345 | B:PACKT4 | 566 | 654 | 114.05
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:PA27&BP76 | 566 | 654 | 114.02
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3208 | 566 | 654 | 114.01
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT4 | 566 | 654 | 114
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 1 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 113.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 2 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 113.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 3 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 113.98
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R915 | 566 | 654 | 113.97
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL77 | 566 | 654 | 113.97
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:MP11&41 | 566 | 654 | 113.95
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_4182 | 566 | 654 | 113.85
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:61&191 | 566 | 654 | 113.85
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3202 | 566 | 654 | 113.84
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | S:PA_HNTL77 | 566 | 654 | 113.83
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - COOPERS 345 SC | 566 | 654 | 113.8
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - ELM 70 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 113.7
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:30&40 | 566 | 654 | 113.67
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - PACKARD 62 230 | 566 | 654 | 113.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | SB:PA230_R3430 | 566 | 654 | 113.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - PACKARD 61 230 | 566 | 654 | 113.57
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | PACKARD 230/115 3TR | 566 | 654 | 113.56
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R955 | 566 | 654 | 113.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:OSWEGO 5 | 566 | 654 | 113.49
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:62&PA27 | 566 | 654 | 113.49
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R965 | 566 | 654 | 113.47
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:77&76 | 566 | 654 | 113.43
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R400 | 566 | 654 | 113.41
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | SB:PA230_R506 | 566 | 654 | 113.35
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:MILLST3 | 566 | 654 | 113.34
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:MLS3&OMS | 566 | 654 | 113.34
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:250 | 566 | 654 | 113.34
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAG345_3308 | 566 | 654 | 113.32
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CNDGUA | 566 | 654 | 113.31
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA 230/115 1TR | 566 | 654 | 113.29
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | MEYER - CANDQUA 60 230 | 566 | 654 | 113.29
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:JAMESGN7 | S:PA_HNTL77 | 566 | 654 | 113.29
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | SB:PA230_R506 | 566 | 654 | 113.27
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - KINTIGH 345 | 566 | 654 | 113.22
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R935 | 566 | 654 | 113.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:FRGT/WRFL | 566 | 654 | 113.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R925 | 566 | 654 | 113.19
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - WTRCR 31 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 113.19
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FRASER 345 SC | 566 | 654 | 113.18
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:FRAS345_B1-4062 | 566 | 654 | 113.18
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 113.17
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:OSWEGO 6 | 566 | 654 | 113.17
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:FRAS345_40-B262 | 566 | 654 | 113.16
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:9MIPT1 | 566 | 654 | 113.15
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R935 | 566 | 654 | 113.14
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MEYER - CANDQUA 60 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 113.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 77 230 | 566 | 654 | 113.11
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL77 | 566 | 654 | 113.02
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 13 345 | S:PA_HNTL77 | 566 | 654 | 113.02
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | SB:PA230_R506 | 566 | 654 | 113
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:FITZPATR | 566 | 654 | 112.94
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:SEABROOK | 566 | 654 | 112.87
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:SEAB&OMS | 566 | 654 | 112.87
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:69J&70K | 566 | 654 | 112.81
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 112.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:170 | 566 | 654 | 112.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:180 | 566 | 654 | 112.79
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-SR_37&W-F_171 | S:PA_HNTL77 | 566 | 654 | 112.75
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:FV-5M_37&W-F_171 | S:PA_HNTL77 | 566 | 654 | 112.75
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC_765_7402 | 566 | 654 | 112.75
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MSU1_7202>7214>7208>7214 | 566 | 654 | 112.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:90 | 566 | 654 | 112.74
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | HQ-NY 765 | 566 | 654 | 112.73
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._99 | 566 | 654 | 112.72
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - PACKARD 61 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 112.72
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE | 566 | 654 | 112.68
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 112.67
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._77 | 566 | 654 | 112.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 112.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3308 | 566 | 654 | 112.65
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:MP12&18 | 566 | 654 | 112.65
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:160 | 566 | 654 | 112.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:150 | 566 | 654 | 112.64
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS2 | S:PA_HNTL77 | 566 | 654 | 112.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_3414 | 566 | 654 | 112.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_3514 | 566 | 654 | 112.62
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL77 | 566 | 654 | 112.62
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:GINNA | HUNTLEY - PACKARD 77 230 | 566 | 654 | 112.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:PECHBTM2 | 566 | 654 | 112.58
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDL - FRASER 32 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 112.58
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | SB:PA230_R506 | 566 | 654 | 112.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:W89&W90 | 566 | 654 | 112.57
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - 5MILE 345 | S:PA_HNTL77 | 566 | 654 | 112.56
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R140 | 566 | 654 | 112.54
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL77 | 566 | 654 | 112.53
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAW230_2014 | 566 | 654 | 112.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SHLDON - STONYCR 230 | 566 | 654 | 112.51
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 112.5
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - WATERCURE 69 230 | S:PA_HNTL77 | 566 | 654 | 112.5
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - ETWANDA 70 230 | S:PA_HNTL77 | 566 | 654 | 112.5
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3314 | 566 | 654 | 112.49
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - N.SCOT99 I8 345 | 566 | 654 | 112.49
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:F38&F39 | 566 | 654 | 112.49
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_2T8082 | 566 | 654 | 112.44
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 112.42
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 2TR | B:PACKT4 | 566 | 654 | 112.42
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:SUSQ1 | 566 | 654 | 112.4
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - FARMVLY | B:PACKT4 | 566 | 654 | 112.4
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | SB:PA230_R3430 | 566 | 654 | 112.39
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - EDIC 2-15 345 | S:PA_HNTL77 | 566 | 654 | 112.39
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3108 | 566 | 654 | 112.37
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - N.SCOT77 I4 345 | 566 | 654 | 112.35
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | SB:PA230_R3430 | 566 | 654 | 112.35
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-1 345 | S:PA_HNTL77 | 566 | 654 | 112.34
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-2 345 | S:PA_HNTL77 | 566 | 654 | 112.34
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 112.33
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:F30&F31 | 566 | 654 | 112.32
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 2TR | SB:PA230_R506 | 566 | 654 | 112.32
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_376512 | 566 | 654 | 112.3
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_34XC | 566 | 654 | 112.29
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M7TR | B:PACKT4 | 566 | 654 | 112.29
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_31153 | 566 | 654 | 112.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:STONY230 | 566 | 654 | 112.23
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SANDY_DC&OMS | 566 | 654 | 112.22
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SANDY_DC | 566 | 654 | 112.22
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PV345_RNS5 | 566 | 654 | 112.21
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 7-9 | B:PACKT4 | 566 | 654 | 112.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 10-12 | B:PACKT4 | 566 | 654 | 112.2
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - 5MILE 345 | 566 | 654 | 112.19
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R935 | 566 | 654 | 112.19
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 1-3 | B:PACKT4 | 566 | 654 | 112.19
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 4-6 | B:PACKT4 | 566 | 654 | 112.19
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PV345_RNS4 | 566 | 654 | 112.18
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R945 | 566 | 654 | 112.18
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-SR_37&W-F_171 | 566 | 654 | 112.16
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:FV-5M_37&W-F_171 | 566 | 654 | 112.16
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | SB:PA230_R3430 | 566 | 654 | 112.16
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | SB:PA230_R506 | 566 | 654 | 112.16
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LEEDS345_R9293 | 566 | 654 | 112.13
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:SALEMG1 | 566 | 654 | 112.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:HOPECG1 | 566 | 654 | 112.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:LIMERCK2 | 566 | 654 | 112.11
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ERIE E - 4 MILE 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 112.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M6TR | B:PACKT4 | 566 | 654 | 112.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M8TR | B:PACKT4 | 566 | 654 | 112.08
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_3456 | 566 | 654 | 112.07
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | HUNTLEY - PACKARD 77 230 | 566 | 654 | 112.06
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_34-B382 | 566 | 654 | 112.02
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_B2-3482 | 566 | 654 | 112.02
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | HURLEY - ROCKT CMT/MTR-34 345 | 566 | 654 | 112.02
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CMT/MTR-34 345 | 566 | 654 | 112.02
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SHLDON - STONYCR 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.96
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R150 | 566 | 654 | 111.95
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R160 | 566 | 654 | 111.94
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3908 | 566 | 654 | 111.92
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3808 | 566 | 654 | 111.91
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - DEW 13 345 | 566 | 654 | 111.88
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LEEDS345_R94301 | 566 | 654 | 111.87
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R110 | 566 | 654 | 111.84
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_4255 | 566 | 654 | 111.84
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R150 | 566 | 654 | 111.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R160 | 566 | 654 | 111.82
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STNYRDG - HILLSIDE 68B 230 | B:PACKT4 | 566 | 654 | 111.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_B2-4282 | 566 | 654 | 111.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 566 | 654 | 111.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 566 | 654 | 111.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 1-16 345 | 566 | 654 | 111.81
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 73 230 | B:PACKT4 | 566 | 654 | 111.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 566 | 654 | 111.8
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 566 | 654 | 111.8
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.8
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 74 230 | B:PACKT4 | 566 | 654 | 111.8
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R10 | 566 | 654 | 111.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DUNW345_3 | 566 | 654 | 111.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LEEDS345_R92 | 566 | 654 | 111.76
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 566 | 654 | 111.76
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 566 | 654 | 111.76
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3102 | 566 | 654 | 111.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 566 | 654 | 111.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 566 | 654 | 111.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DUNW345_8 | 566 | 654 | 111.74
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | SB:PA230_R3430 | 566 | 654 | 111.73
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FITZ - EDIC FEI 345 | 566 | 654 | 111.72
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FITZ 345 | 566 | 654 | 111.72
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DEWI345_R915 | 566 | 654 | 111.7
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DEWI345_R130 | 566 | 654 | 111.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DEWI345_R220 | 566 | 654 | 111.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.68
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | VOLNEY - MARCY I9 345 | 566 | 654 | 111.67
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | VOL - MARCY 19 345 | 566 | 654 | 111.67
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:VOLN_R925 | 566 | 654 | 111.67
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:JAMESGN7 | SB:PA230_R506 | 566 | 654 | 111.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:GINNA | 566 | 654 | 111.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3914 | 566 | 654 | 111.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3814 | 566 | 654 | 111.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ROCH 345/115 5TR | 566 | 654 | 111.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R506 | 566 | 654 | 111.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:JAMESGN7 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.56
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-SR_37&W-F_171 | SB:PA230_R506 | 566 | 654 | 111.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:FV-5M_37&W-F_171 | SB:PA230_R506 | 566 | 654 | 111.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 11 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 12 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 13 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 8 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 9 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 10 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.5
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL - CLAY PC-1 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.48
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL - CLAY PC-2 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.48
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - ELM 70 230 | B:PACKT4 | 566 | 654 | 111.45
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 13 345 | SB:PA230_R506 | 566 | 654 | 111.39
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 2TR | SB:PA230_R3430 | 566 | 654 | 111.37
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SRIPL - ERIE E 69 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.34
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DUNKIRK - SRIPL 68 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.33
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | SB:PA230_R3430 | 566 | 654 | 111.3
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | EDIC - FITZ 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - 5MILE 345 | SB:PA230_R506 | 566 | 654 | 111.22
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.16
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MASS_765_7108 | 566 | 654 | 111.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OS - EL - LFYTE 17 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.11
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.09
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.09
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 1TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.02
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 2TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.02
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 3TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.01
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS2 | SB:PA230_R506 | 566 | 654 | 111.01
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | VOL - MARCY 19 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.98
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY 345/115 1TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.96
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY 345/115 2TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.96
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CANDQUA - STNYRDG 68A 230 | 566 | 654 | 110.95
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | S:AVOCA | 566 | 654 | 110.95
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R506 | 566 | 654 | 110.93
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MASS_765_7102 | 566 | 654 | 110.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:STONYRIDGE | 566 | 654 | 110.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R506 | 566 | 654 | 110.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R506 | 566 | 654 | 110.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - WTRCR 31 345 | B:PACKT4 | 566 | 654 | 110.89
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.88
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 3 115 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.86
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - TEAL 10 115 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.86
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - TEAL 11 115 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.86
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS2 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.86
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PA230_R506 | 566 | 654 | 110.85
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 5 115 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.84
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - LM 14 115 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.84
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LHH - CLAY 7 115 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.83
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - VOL 21 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MEYER - CANDQUA 60 230 | B:PACKT4 | 566 | 654 | 110.83
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FUL - CLAY 4 115 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - WOOD 17 115 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - 9MI1 9 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - VOL 20 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA 345/115 1TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA 345/115 2TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - IND 25 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.8
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW - VOL 11 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW - VOL 12 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW 345/115 1TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.78
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - EDIC 2-15 345 | SB:PA230_R506 | 566 | 654 | 110.78
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:JAMESGN7 | SB:PA230_R3430 | 566 | 654 | 110.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - FITZ 10 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.76
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GEN:OSWEGO 5 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GEN:SITHE 1 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GEN:SITHE 2 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | EDIC - MRCY ue 1-7 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3430 | 566 | 654 | 110.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R506 | 566 | 654 | 110.67
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - FARMVLY | S:PA_HNTL77 | 566 | 654 | 110.67
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 2TR | S:PA_HNTL77 | 566 | 654 | 110.65
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | 5 MILE - STOLLE 37A 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HOMERCTY - STOLLRD 37 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.61
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ERIE E - 4 MILE 230 | 566 | 654 | 110.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:5M-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.59
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH 345/115 5TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 110.56
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | BECK - PACKARD BP76 230 | B:PACKT4 | 566 | 654 | 110.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M7TR | S:PA_HNTL77 | 566 | 654 | 110.52
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 13 345 | SB:PA230_R3430 | 566 | 654 | 110.5
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:62&BP76 | 566 | 654 | 110.49
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 7-9 | S:PA_HNTL77 | 566 | 654 | 110.45
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 10-12 | S:PA_HNTL77 | 566 | 654 | 110.45
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 1-3 | S:PA_HNTL77 | 566 | 654 | 110.44
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 4-6 | S:PA_HNTL77 | 566 | 654 | 110.44
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | BECK - PACKARD BP76 230 | S:PA_HNTL77 | 566 | 654 | 110.43
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-SR_37&W-F_171 | SB:PA230_R3430 | 566 | 654 | 110.34
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:FV-5M_37&W-F_171 | SB:PA230_R3430 | 566 | 654 | 110.34
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDL - FRASER 32 345 | B:PACKT4 | 566 | 654 | 110.3
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M6TR | S:PA_HNTL77 | 566 | 654 | 110.29
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M8TR | S:PA_HNTL77 | 566 | 654 | 110.29
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:GINNA | B:PACKT4 | 566 | 654 | 110.28
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | B:PACKT4 | 566 | 654 | 110.2
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | B:PACKT4 | 566 | 654 | 110.13
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS2 | SB:PA230_R3430 | 566 | 654 | 110.13
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - 5MILE 345 | SB:PA230_R3430 | 566 | 654 | 110.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RAIN345_1W | 566 | 654 | 110.03
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT2 | 566 | 654 | 110.03
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDL - FRASER 32 345 | 566 | 654 | 110.02
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FRASER - OAKDLE 32 345 | 566 | 654 | 110.02
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RAIN345_9W | 566 | 654 | 110.02
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL77 | 566 | 654 | 110.02
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL77 | 566 | 654 | 110.02
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R3430 | 566 | 654 | 110.02
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R3430 | 566 | 654 | 110.01
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R3430 | 566 | 654 | 110.01
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: RAVENSWOOD | 566 | 654 | 110
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:FRAS345_B1-3262 | 566 | 654 | 110
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:30 | 566 | 654 | 110
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | BWLN - WHAV -LDN 67 345 | 566 | 654 | 110
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL77 | 566 | 654 | 110
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT1 | 566 | 654 | 109.99
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 2TR | 566 | 654 | 109.94
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B2 | 566 | 654 | 109.94
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 1 | S:PA_HNTL77 | 566 | 654 | 109.93
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 2 | S:PA_HNTL77 | 566 | 654 | 109.93
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 3 | S:PA_HNTL77 | 566 | 654 | 109.93
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - BECK_TSA 345 | SB:PA230_R3430 | 566 | 654 | 109.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - BECK_TSB 345 | SB:PA230_R3430 | 566 | 654 | 109.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ERIE E - 4 MILE 230 | B:PACKT4 | 566 | 654 | 109.91
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROSE345_30553 | 566 | 654 | 109.89
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - EDIC 2-15 345 | SB:PA230_R3430 | 566 | 654 | 109.89
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_4-56-2 | 566 | 654 | 109.88
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:9 MI PT2 | 566 | 654 | 109.88
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:SCRIBA_R230 | 566 | 654 | 109.88
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:SCRIBA_R925 | 566 | 654 | 109.88
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_1-56-2 | 566 | 654 | 109.85
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH 345/115 5TR | SB:PA230_R3430 | 566 | 654 | 109.85
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-2 345 | SB:PA230_R3430 | 566 | 654 | 109.84
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M7TR | 566 | 654 | 109.83
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_6-56-2 | 566 | 654 | 109.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_3-56-2 | 566 | 654 | 109.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:NOEND | 566 | 654 | 109.77
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - WTRCR 31 345 | 566 | 654 | 109.76
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B3 | 566 | 654 | 109.76
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROSE345_30551 | 566 | 654 | 109.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R3430 | 566 | 654 | 109.75
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SHLDON - STONYCR 230 | B:PACKT4 | 566 | 654 | 109.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROSE345_31152 | 566 | 654 | 109.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RMP345_T1500 | 566 | 654 | 109.72
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON2 | 566 | 654 | 109.71
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | RAMAPO - BRNCHBRG 5018 345 | 566 | 654 | 109.7
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | B:PACKT4 | 566 | 654 | 109.68
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WATRC345_31-2 | 566 | 654 | 109.67
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2208 | 566 | 654 | 109.67
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RMP345_1500-2X | 566 | 654 | 109.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2214 | 566 | 654 | 109.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS17-20 | 566 | 654 | 109.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2224 | 566 | 654 | 109.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1724 | 566 | 654 | 109.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1714 | 566 | 654 | 109.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1524 | 566 | 654 | 109.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1514 | 566 | 654 | 109.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1508 | 566 | 654 | 109.64
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - ELM 70 230 | S:PA_HNTL77 | 566 | 654 | 109.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2524 | 566 | 654 | 109.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2514 | 566 | 654 | 109.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS21-24 | 566 | 654 | 109.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2508 | 566 | 654 | 109.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M8TR | 566 | 654 | 109.62
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M6TR | 566 | 654 | 109.62
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | B:PACKT4 | 566 | 654 | 109.59
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON1 | 566 | 654 | 109.57
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/NWES | 566 | 654 | 109.51
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | B:PACKT4 | 566 | 654 | 109.5
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3208 | 566 | 654 | 109.48
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SRIPL - ERIE E 69 230 | 566 | 654 | 109.48
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | B:PACKT4 | 566 | 654 | 109.46
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | DUNKIRK - SRIPL 68 230 | 566 | 654 | 109.46
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:SRIPLEY | 566 | 654 | 109.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:AT_R6361 | 566 | 654 | 109.44
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BESICORP | 566 | 654 | 109.43
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:EMPIRE | 566 | 654 | 109.42
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | S:EMPIRE | 566 | 654 | 109.36
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: IND PT 2 | 566 | 654 | 109.29
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 13 345 | B:PACKT4 | 566 | 654 | 109.29
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 11 | B:PACKT4 | 566 | 654 | 109.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 12 | B:PACKT4 | 566 | 654 | 109.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 13 | B:PACKT4 | 566 | 654 | 109.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 8 | B:PACKT4 | 566 | 654 | 109.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 9 | B:PACKT4 | 566 | 654 | 109.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 10 | B:PACKT4 | 566 | 654 | 109.26
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN GILBOA #3&4 | 566 | 654 | 109.25
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3302 | 566 | 654 | 109.25
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:72&69 | 566 | 654 | 109.23
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN GILBOA #1&2 | 566 | 654 | 109.21
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3202 | 566 | 654 | 109.21
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3308 | 566 | 654 | 109.2
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHN_11 | 566 | 654 | 109.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 1 | SB:PA230_R506 | 566 | 654 | 109.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 2 | SB:PA230_R506 | 566 | 654 | 109.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 3 | SB:PA230_R506 | 566 | 654 | 109.2
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | BECK - PACKARD BP76 230 | 566 | 654 | 109.19
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHN_9 | 566 | 654 | 109.19
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SRIPL - ERIE E 69 230 | B:PACKT4 | 566 | 654 | 109.19
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DUNKIRK - SRIPL 68 230 | B:PACKT4 | 566 | 654 | 109.18
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:NTHF3&4 | 566 | 654 | 109.17
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHN_7 | 566 | 654 | 109.17
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 2TR | SB:PA230_R506 | 566 | 654 | 109.17
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - FARMVLY | SB:PA230_R506 | 566 | 654 | 109.16
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | STONYCR - WTHRS 230 | 566 | 654 | 109.14
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - WTRCR 31 345 | S:PA_HNTL77 | 566 | 654 | 109.13
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | S:PA_HNTL77 | 566 | 654 | 109.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - FARMVLY | 566 | 654 | 109.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: IND PT 3 | 566 | 654 | 109.1
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-WC_30&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 109.07
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHS_1 | 566 | 654 | 109.05
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHS_3 | 566 | 654 | 109.05
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MEYER - CANDQUA 60 230 | S:PA_HNTL77 | 566 | 654 | 109.05
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | S:PA_HNTL77 | 566 | 654 | 109.04
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M7TR | SB:PA230_R506 | 566 | 654 | 109.03
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | B:PACKT4 | 566 | 654 | 109.02
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCWC/NWES | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.99
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:MBWC/NWES | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.99
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:67&68&BW | 566 | 654 | 108.98
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 2TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.97
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | WTRCR - MAINSBRG 30A 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.97
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | B:PACKT4 | 566 | 654 | 108.92
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 2TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.9
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | HILLSIDE 230/115 4TR | 566 | 654 | 108.89
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:HILLSIDE | 566 | 654 | 108.89
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STONYCR - WTHRS 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.89
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HILL_B412 | 566 | 654 | 108.88
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 7-9 | SB:PA230_R506 | 566 | 654 | 108.88
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 10-12 | SB:PA230_R506 | 566 | 654 | 108.88
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - FARMVLY | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.87
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 1-3 | SB:PA230_R506 | 566 | 654 | 108.87
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 4-6 | SB:PA230_R506 | 566 | 654 | 108.87
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | HUNTLEY - ELM 70 230 | 566 | 654 | 108.85
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M7TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.85
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:SITHE 1 | 566 | 654 | 108.84
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:SITHE 2 | 566 | 654 | 108.84
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:BETHSTM | 566 | 654 | 108.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M6TR | SB:PA230_R506 | 566 | 654 | 108.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M8TR | SB:PA230_R506 | 566 | 654 | 108.83
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DEWITT3 - LAFAYTTE 345 | B:PACKT4 | 566 | 654 | 108.76
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - PACKARD 62 230 | S:PA_HNTL77 | 566 | 654 | 108.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:MBWC/NWES | 566 | 654 | 108.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HCWC/NWES | 566 | 654 | 108.74
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WTHERS230 | 566 | 654 | 108.72
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:120_130 | 566 | 654 | 108.71
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:130 | 566 | 654 | 108.71
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:W97&W98 | 566 | 654 | 108.71
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | WTRCR - MAINSBRG 30A 345 | 566 | 654 | 108.71
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WATRC345_30-3142 | 566 | 654 | 108.71
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | BECK - PACKARD BP76 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.7
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HILL_68-B412 | 566 | 654 | 108.7
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WATRC345_B1-3042 | 566 | 654 | 108.69
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - PACKARD 61 230 | S:PA_HNTL77 | 566 | 654 | 108.67
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | STNYRDG - HILLSIDE 68B 230 | 566 | 654 | 108.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M6TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M8TR | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 1-3 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 4-6 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 7-9 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 10-12 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - EDIC 2-15 345 | B:PACKT4 | 566 | 654 | 108.64
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R506 | 566 | 654 | 108.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | S:PA_HNTL77 | 566 | 654 | 108.6
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R506 | 566 | 654 | 108.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | S:PA_HNTL77 | 566 | 654 | 108.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R506 | 566 | 654 | 108.59
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-WC_30&W-F_171 | 566 | 654 | 108.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-2 345 | B:PACKT4 | 566 | 654 | 108.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:61&191 | 566 | 654 | 108.57
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:GINNA | S:PA_HNTL77 | 566 | 654 | 108.55
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDL - FRASER 32 345 | S:PA_HNTL77 | 566 | 654 | 108.54
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:JAMESGN7 | B:PACKT4 | 566 | 654 | 108.53
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - WTRCR 31 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.51
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL - CLAY PC-2 345 | B:PACKT4 | 566 | 654 | 108.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL - CLAY PC-1 345 | B:PACKT4 | 566 | 654 | 108.45
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | S:PA_HNTL77 | 566 | 654 | 108.44
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HCMB/NWES | 566 | 654 | 108.43
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL - DUNKIRK 73 230 | 566 | 654 | 108.42
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:DUNKG3 | 566 | 654 | 108.4
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL - DUNKIRK 74 230 | 566 | 654 | 108.4
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | MAINSBRG - HOMERCITY 30B 345 | 566 | 654 | 108.38
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | S:PA_HNTL77 | 566 | 654 | 108.36
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - PACKARD 62 230 | 566 | 654 | 108.35
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:DUNKG4 | 566 | 654 | 108.35
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STNYRDG - HILLSIDE 68B 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.32
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 73 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.31
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 74 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.29
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - PACKARD 61 230 | 566 | 654 | 108.28
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-MB_30&W-F_171 | 566 | 654 | 108.27
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 13 345 | S:PA_HNTL77 | 566 | 654 | 108.26
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | EDIC - FITZ 345 | B:PACKT4 | 566 | 654 | 108.24
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - ELM 70 230 | SB:PA230_R506 | 566 | 654 | 108.22
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-SR_37&W-F_171 | B:PACKT4 | 566 | 654 | 108.2
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:FV-5M_37&W-F_171 | B:PACKT4 | 566 | 654 | 108.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GEN:KINTIGH | HUNTLEY - PACKARD 77 230 | 566 | 654 | 108.2
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:PA27&BP76 | 566 | 654 | 108.19
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - FARMVLY | SB:PA230_R3430 | 566 | 654 | 108.19
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 2TR | SB:PA230_R3430 | 566 | 654 | 108.19
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:62&PA27 | 566 | 654 | 108.16
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OS - EL - LFYTE 17 345 | B:PACKT4 | 566 | 654 | 108.09
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:KINT_39-B112 | 566 | 654 | 108.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M7TR | SB:PA230_R3430 | 566 | 654 | 108.07
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/WF/NWES | 566 | 654 | 108.01
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:KINT_B1-3812 | 566 | 654 | 108
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ERIE E - 4 MILE 230 | S:PA_HNTL77 | 566 | 654 | 108
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/WRFL | 566 | 654 | 108
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 1TR | B:PACKT4 | 566 | 654 | 107.99
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 2TR | B:PACKT4 | 566 | 654 | 107.99
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | S:PA_HNTL77 | 566 | 654 | 107.99
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 3TR | B:PACKT4 | 566 | 654 | 107.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:DKSR/WRFL | 566 | 654 | 107.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 7-9 | SB:PA230_R3430 | 566 | 654 | 107.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 10-12 | SB:PA230_R3430 | 566 | 654 | 107.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 1-3 | SB:PA230_R3430 | 566 | 654 | 107.97
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 4-6 | SB:PA230_R3430 | 566 | 654 | 107.97
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - ELM 70 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 107.96
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | VOL - MARCY 19 345 | B:PACKT4 | 566 | 654 | 107.96
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY 345/115 1TR | B:PACKT4 | 566 | 654 | 107.93
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY 345/115 2TR | B:PACKT4 | 566 | 654 | 107.93
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - 5MILE 345 | B:PACKT4 | 566 | 654 | 107.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SHLDON - STONYCR 230 | S:PA_HNTL77 | 566 | 654 | 107.91
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDL - FRASER 32 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 107.87
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M6TR | SB:PA230_R3430 | 566 | 654 | 107.86
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M8TR | SB:PA230_R3430 | 566 | 654 | 107.86
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 3 115 | B:PACKT4 | 566 | 654 | 107.83
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - TEAL 10 115 | B:PACKT4 | 566 | 654 | 107.83
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - TEAL 11 115 | B:PACKT4 | 566 | 654 | 107.83
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS2 | B:PACKT4 | 566 | 654 | 107.83
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 5 115 | B:PACKT4 | 566 | 654 | 107.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - LM 14 115 | B:PACKT4 | 566 | 654 | 107.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LHH - CLAY 7 115 | B:PACKT4 | 566 | 654 | 107.8
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - VOL 21 345 | B:PACKT4 | 566 | 654 | 107.8
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FUL - CLAY 4 115 | B:PACKT4 | 566 | 654 | 107.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - WOOD 17 115 | B:PACKT4 | 566 | 654 | 107.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - VOL 20 345 | B:PACKT4 | 566 | 654 | 107.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA 345/115 1TR | B:PACKT4 | 566 | 654 | 107.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA 345/115 2TR | B:PACKT4 | 566 | 654 | 107.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - 9MI1 9 345 | B:PACKT4 | 566 | 654 | 107.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - IND 25 345 | B:PACKT4 | 566 | 654 | 107.77
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL77 | 566 | 654 | 107.76
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW - VOL 11 345 | B:PACKT4 | 566 | 654 | 107.76
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW - VOL 12 345 | B:PACKT4 | 566 | 654 | 107.76
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW 345/115 1TR | B:PACKT4 | 566 | 654 | 107.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:5M-SR_37&W-F_171 | B:PACKT4 | 566 | 654 | 107.73
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - FITZ 10 345 | B:PACKT4 | 566 | 654 | 107.73
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | 5 MILE - STOLLE 37A 345 | B:PACKT4 | 566 | 654 | 107.72
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | EDIC - MRCY ue 1-7 345 | B:PACKT4 | 566 | 654 | 107.72
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HOMERCTY - STOLLRD 37 345 | B:PACKT4 | 566 | 654 | 107.71
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - WATERCURE 69 230 | B:PACKT4 | 566 | 654 | 107.71
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - ETWANDA 70 230 | B:PACKT4 | 566 | 654 | 107.71
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - WTRCR 31 345 | SB:PA230_R506 | 566 | 654 | 107.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3430 | 566 | 654 | 107.67
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:PACKT4 | 566 | 654 | 107.67
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MEYER - CANDQUA 60 230 | SB:PA230_R506 | 566 | 654 | 107.67
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - BECK_TSA 345 | B:PACKT4 | 566 | 654 | 107.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - BECK_TSB 345 | B:PACKT4 | 566 | 654 | 107.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R955 | 566 | 654 | 107.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - EDIC 2-15 345 | S:PA_HNTL77 | 566 | 654 | 107.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:OSWEGO 5 | 566 | 654 | 107.6
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R3430 | 566 | 654 | 107.6
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R3430 | 566 | 654 | 107.59
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R965 | 566 | 654 | 107.57
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH 345/115 5TR | B:PACKT4 | 566 | 654 | 107.57
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 1 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 107.56
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 2 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 107.56
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 3 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 107.56
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R3430 | 566 | 654 | 107.56
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-2 345 | S:PA_HNTL77 | 566 | 654 | 107.54
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 107.49
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:JAMESGN7 | S:PA_HNTL77 | 566 | 654 | 107.49
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCMB/NWES | HUNTLEY - PACKARD 77 230 | 566 | 654 | 107.47
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:MLS3&OMS | 566 | 654 | 107.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:MILLST3 | 566 | 654 | 107.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:250 | 566 | 654 | 107.46
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 11 | S:PA_HNTL77 | 566 | 654 | 107.46
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 12 | S:PA_HNTL77 | 566 | 654 | 107.46
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 13 | S:PA_HNTL77 | 566 | 654 | 107.46
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 8 | S:PA_HNTL77 | 566 | 654 | 107.46
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 9 | S:PA_HNTL77 | 566 | 654 | 107.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL - CLAY PC-1 345 | S:PA_HNTL77 | 566 | 654 | 107.44
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL - CLAY PC-2 345 | S:PA_HNTL77 | 566 | 654 | 107.44
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 10 | S:PA_HNTL77 | 566 | 654 | 107.44
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CNDGUA | 566 | 654 | 107.43
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - PACKARD 61 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 107.42
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | MEYER - CANDQUA 60 230 | 566 | 654 | 107.41
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:KINTIGH | 566 | 654 | 107.41
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-MB_30&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 107.38
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:68&160 | 566 | 654 | 107.38
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:FRGT/WRFL | 566 | 654 | 107.3
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MAINSBRG - HOMERCITY 30B 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 107.3
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R925 | 566 | 654 | 107.29
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SRIPL - ERIE E 69 230 | S:PA_HNTL77 | 566 | 654 | 107.28
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:OSWEGO 6 | 566 | 654 | 107.27
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MEYER - CANDQUA 60 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 107.27
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:9MIPT1 | 566 | 654 | 107.26
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DUNKIRK - SRIPL 68 230 | S:PA_HNTL77 | 566 | 654 | 107.26
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R935 | 566 | 654 | 107.25
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - ELM 70 230 | SB:PA230_R3430 | 566 | 654 | 107.24
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | EDIC - FITZ 345 | S:PA_HNTL77 | 566 | 654 | 107.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDL - FRASER 32 345 | SB:PA230_R506 | 566 | 654 | 107.11
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:GINNA | SB:PA230_R506 | 566 | 654 | 107.09
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | SB:PA230_R506 | 566 | 654 | 107.07
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL77 | 566 | 654 | 107.06
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OS - EL - LFYTE 17 345 | S:PA_HNTL77 | 566 | 654 | 107.05
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:FITZPATR | 566 | 654 | 107.04
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-SR_37&W-F_171 | S:PA_HNTL77 | 566 | 654 | 107
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:FV-5M_37&W-F_171 | S:PA_HNTL77 | 566 | 654 | 107
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:SEAB&OMS | 566 | 654 | 106.98
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:SEABROOK | 566 | 654 | 106.98
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | SB:PA230_R506 | 566 | 654 | 106.97
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 1TR | S:PA_HNTL77 | 566 | 654 | 106.97
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 2TR | S:PA_HNTL77 | 566 | 654 | 106.97
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 3TR | S:PA_HNTL77 | 566 | 654 | 106.96
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 11 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 106.93
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 12 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 106.93
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 13 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 106.93
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:73&74 | 566 | 654 | 106.93
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY 345/115 1TR | S:PA_HNTL77 | 566 | 654 | 106.92
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY 345/115 2TR | S:PA_HNTL77 | 566 | 654 | 106.92
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 8 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 106.92
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 9 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 106.92
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | VOL - MARCY 19 345 | S:PA_HNTL77 | 566 | 654 | 106.91
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 10 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 106.91
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ERIE E - 4 MILE 230 | SB:PA230_R506 | 566 | 654 | 106.91
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC_765_7402 | 566 | 654 | 106.87
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MSU1_7202>7214>7208>7214 | 566 | 654 | 106.87
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | HQ-NY 765 | 566 | 654 | 106.85
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-WC_30&W-F_171 | B:PACKT4 | 566 | 654 | 106.85
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - TEAL 11 115 | S:PA_HNTL77 | 566 | 654 | 106.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 3 115 | S:PA_HNTL77 | 566 | 654 | 106.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - TEAL 10 115 | S:PA_HNTL77 | 566 | 654 | 106.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - LM 14 115 | S:PA_HNTL77 | 566 | 654 | 106.8
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 5 115 | S:PA_HNTL77 | 566 | 654 | 106.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LHH - CLAY 7 115 | S:PA_HNTL77 | 566 | 654 | 106.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS2 | S:PA_HNTL77 | 566 | 654 | 106.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - 5MILE 345 | S:PA_HNTL77 | 566 | 654 | 106.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FUL - CLAY 4 115 | S:PA_HNTL77 | 566 | 654 | 106.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - WOOD 17 115 | S:PA_HNTL77 | 566 | 654 | 106.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - VOL 21 345 | S:PA_HNTL77 | 566 | 654 | 106.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA 345/115 1TR | S:PA_HNTL77 | 566 | 654 | 106.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA 345/115 2TR | S:PA_HNTL77 | 566 | 654 | 106.78
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | WTRCR - MAINSBRG 30A 345 | B:PACKT4 | 566 | 654 | 106.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - 9MI1 9 345 | S:PA_HNTL77 | 566 | 654 | 106.77
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - VOL 20 345 | S:PA_HNTL77 | 566 | 654 | 106.77
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCWC/NWES | B:PACKT4 | 566 | 654 | 106.76
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:MBWC/NWES | B:PACKT4 | 566 | 654 | 106.76
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL77 | 566 | 654 | 106.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW - VOL 11 345 | S:PA_HNTL77 | 566 | 654 | 106.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW - VOL 12 345 | S:PA_HNTL77 | 566 | 654 | 106.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - IND 25 345 | S:PA_HNTL77 | 566 | 654 | 106.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:GINNA | HUNTLEY - PACKARD 77 230 | 566 | 654 | 106.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW 345/115 1TR | S:PA_HNTL77 | 566 | 654 | 106.74
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STONYCR - WTHRS 230 | B:PACKT4 | 566 | 654 | 106.73
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - FITZ 10 345 | S:PA_HNTL77 | 566 | 654 | 106.72
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SHLDON - STONYCR 230 | SB:PA230_R506 | 566 | 654 | 106.71
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - WTRCR 31 345 | SB:PA230_R3430 | 566 | 654 | 106.71
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | EDIC - MRCY ue 1-7 345 | S:PA_HNTL77 | 566 | 654 | 106.7
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GEN:SITHE 1 | S:PA_HNTL77 | 566 | 654 | 106.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GEN:SITHE 2 | S:PA_HNTL77 | 566 | 654 | 106.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - WATERCURE 69 230 | S:PA_HNTL77 | 566 | 654 | 106.68
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - ETWANDA 70 230 | S:PA_HNTL77 | 566 | 654 | 106.68
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GEN:OSWEGO 5 | S:PA_HNTL77 | 566 | 654 | 106.68
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MEYER - CANDQUA 60 230 | SB:PA230_R3430 | 566 | 654 | 106.62
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SHLDON - STONYCR 230 | 566 | 654 | 106.56
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH 345/115 5TR | S:PA_HNTL77 | 566 | 654 | 106.5
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-1 345 | S:PA_HNTL77 | 566 | 654 | 106.5
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1302 | 566 | 654 | 106.48
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | SB:PA230_R506 | 566 | 654 | 106.45
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | SB:PA230_R506 | 566 | 654 | 106.39
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SANDY_DC | 566 | 654 | 106.33
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SANDY_DC&OMS | 566 | 654 | 106.33
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | BECK - PACKARD BP76 230 | SB:PA230_R3430 | 566 | 654 | 106.31
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:STONY230 | 566 | 654 | 106.27
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ERIE E - 4 MILE 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 106.24
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | SB:PA230_R506 | 566 | 654 | 106.23
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | SB:PA230_R506 | 566 | 654 | 106.22
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SRIPL - ERIE E 69 230 | SB:PA230_R506 | 566 | 654 | 106.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DUNKIRK - SRIPL 68 230 | SB:PA230_R506 | 566 | 654 | 106.19
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:GINNA | SB:PA230_R3430 | 566 | 654 | 106.09
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDL - FRASER 32 345 | SB:PA230_R3430 | 566 | 654 | 106.09
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 13 345 | SB:PA230_R506 | 566 | 654 | 106.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DUNK230_R1312 | 566 | 654 | 106.08
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SHLDON - STONYCR 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 106.05
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 2TR | B:PACKT4 | 566 | 654 | 105.99
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | SB:PA230_R3430 | 566 | 654 | 105.96
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | SB:PA230_R3430 | 566 | 654 | 105.91
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 11 | SB:PA230_R506 | 566 | 654 | 105.91
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 12 | SB:PA230_R506 | 566 | 654 | 105.91
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 13 | SB:PA230_R506 | 566 | 654 | 105.91
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 8 | SB:PA230_R506 | 566 | 654 | 105.9
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 9 | SB:PA230_R506 | 566 | 654 | 105.9
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M7TR | B:PACKT4 | 566 | 654 | 105.89
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GEN:KINTIGH | B:PACKT4 | 566 | 654 | 105.89
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 10 | SB:PA230_R506 | 566 | 654 | 105.89
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - FARMVLY | B:PACKT4 | 566 | 654 | 105.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R506 | 566 | 654 | 105.83
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | SB:PA230_R506 | 566 | 654 | 105.8
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 3 | B:PACKT4 | 566 | 654 | 105.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 1 | B:PACKT4 | 566 | 654 | 105.77
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 2 | B:PACKT4 | 566 | 654 | 105.77
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:GINNA | 566 | 654 | 105.76
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M6TR | B:PACKT4 | 566 | 654 | 105.71
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M8TR | B:PACKT4 | 566 | 654 | 105.71
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ERIE E - 4 MILE 230 | SB:PA230_R3430 | 566 | 654 | 105.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 1-3 | B:PACKT4 | 566 | 654 | 105.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 7-9 | B:PACKT4 | 566 | 654 | 105.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 10-12 | B:PACKT4 | 566 | 654 | 105.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 4-6 | B:PACKT4 | 566 | 654 | 105.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1302 | 566 | 654 | 105.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R506 | 566 | 654 | 105.56
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SHLDON - STONYCR 230 | SB:PA230_R3430 | 566 | 654 | 105.55
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - WTRCR 31 345 | B:PACKT4 | 566 | 654 | 105.53
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DUNKIRK - SRIPL 68 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 105.48
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SRIPL - ERIE E 69 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 105.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | SB:PA230_R3430 | 566 | 654 | 105.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - EDIC 2-15 345 | SB:PA230_R506 | 566 | 654 | 105.42
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:62&BP76 | 566 | 654 | 105.41
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | SB:PA230_R3430 | 566 | 654 | 105.4
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 73 230 | B:PACKT4 | 566 | 654 | 105.36
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 105.36
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STNYRDG - HILLSIDE 68B 230 | B:PACKT4 | 566 | 654 | 105.35
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-2 345 | SB:PA230_R506 | 566 | 654 | 105.35
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:JAMESGN7 | SB:PA230_R506 | 566 | 654 | 105.35
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 74 230 | B:PACKT4 | 566 | 654 | 105.34
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCMB/NWES | B:PACKT4 | 566 | 654 | 105.32
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:BRUCE5 | 566 | 654 | 105.32
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | SB:PA230_R3430 | 566 | 654 | 105.28
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | SB:PA230_R3430 | 566 | 654 | 105.27
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL - CLAY PC-1 345 | SB:PA230_R506 | 566 | 654 | 105.26
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL - CLAY PC-2 345 | SB:PA230_R506 | 566 | 654 | 105.26
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-SR_37&W-F_171 | SB:PA230_R506 | 566 | 654 | 105.25
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:FV-5M_37&W-F_171 | SB:PA230_R506 | 566 | 654 | 105.25
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-MB_30&W-F_171 | B:PACKT4 | 566 | 654 | 105.24
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MASS_765_7108 | 566 | 654 | 105.21
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MAINSBRG - HOMERCITY 30B 345 | B:PACKT4 | 566 | 654 | 105.16
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CANDQUA - STNYRDG 68A 230 | 566 | 654 | 105.11
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | S:AVOCA | 566 | 654 | 105.11
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:STONYRIDGE | 566 | 654 | 105.09
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 13 345 | SB:PA230_R3430 | 566 | 654 | 105.07
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 11 | SB:PA230_R3430 | 566 | 654 | 105.07
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 12 | SB:PA230_R3430 | 566 | 654 | 105.07
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 13 | SB:PA230_R3430 | 566 | 654 | 105.07
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 8 | SB:PA230_R3430 | 566 | 654 | 105.07
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 9 | SB:PA230_R3430 | 566 | 654 | 105.07
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 10 | SB:PA230_R3430 | 566 | 654 | 105.06
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - ELM 70 230 | B:PACKT4 | 566 | 654 | 105.04
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | EDIC - FITZ 345 | SB:PA230_R506 | 566 | 654 | 105.03
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-WC_30&W-F_171 | S:PA_HNTL77 | 566 | 654 | 105.01
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MASS_765_7102 | 566 | 654 | 105
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SRIPL - ERIE E 69 230 | SB:PA230_R3430 | 566 | 654 | 104.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | WTRCR - MAINSBRG 30A 345 | S:PA_HNTL77 | 566 | 654 | 104.96
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DUNKIRK - SRIPL 68 230 | SB:PA230_R3430 | 566 | 654 | 104.96
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCWC/NWES | S:PA_HNTL77 | 566 | 654 | 104.94
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:MBWC/NWES | S:PA_HNTL77 | 566 | 654 | 104.94
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - 5MILE 345 | SB:PA230_R506 | 566 | 654 | 104.92
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OS - EL - LFYTE 17 345 | SB:PA230_R506 | 566 | 654 | 104.88
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 2TR | S:PA_HNTL77 | 566 | 654 | 104.87
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDL - FRASER 32 345 | B:PACKT4 | 566 | 654 | 104.87
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 2TR | S:PA_HNTL77 | 566 | 654 | 104.86
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | SB:PA230_R3430 | 566 | 654 | 104.82
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STONYCR - WTHRS 230 | S:PA_HNTL77 | 566 | 654 | 104.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - FARMVLY | S:PA_HNTL77 | 566 | 654 | 104.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 1TR | SB:PA230_R506 | 566 | 654 | 104.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 2TR | SB:PA230_R506 | 566 | 654 | 104.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 3TR | SB:PA230_R506 | 566 | 654 | 104.8
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M7TR | S:PA_HNTL77 | 566 | 654 | 104.79
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY 345/115 1TR | SB:PA230_R506 | 566 | 654 | 104.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY 345/115 2TR | SB:PA230_R506 | 566 | 654 | 104.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | VOL - MARCY 19 345 | SB:PA230_R506 | 566 | 654 | 104.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:5M-SR_37&W-F_171 | SB:PA230_R506 | 566 | 654 | 104.7
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1202 | 566 | 654 | 104.7
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ERIE E - 4 MILE 230 | 566 | 654 | 104.69
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | WTHRS - MEYER 230 | 566 | 654 | 104.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS2 | SB:PA230_R506 | 566 | 654 | 104.67
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R3430 | 566 | 654 | 104.67
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | 5 MILE - STOLLE 37A 345 | SB:PA230_R506 | 566 | 654 | 104.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - TEAL 11 115 | SB:PA230_R506 | 566 | 654 | 104.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 104.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R506 | 566 | 654 | 104.65
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 3 115 | SB:PA230_R506 | 566 | 654 | 104.65
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - TEAL 10 115 | SB:PA230_R506 | 566 | 654 | 104.65
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - LM 14 115 | SB:PA230_R506 | 566 | 654 | 104.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | BECK - PACKARD BP76 230 | S:PA_HNTL77 | 566 | 654 | 104.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 5 115 | SB:PA230_R506 | 566 | 654 | 104.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LHH - CLAY 7 115 | SB:PA230_R506 | 566 | 654 | 104.63
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:MEYER | 566 | 654 | 104.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FUL - CLAY 4 115 | SB:PA230_R506 | 566 | 654 | 104.62
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - WOOD 17 115 | SB:PA230_R506 | 566 | 654 | 104.62
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - VOL 21 345 | SB:PA230_R506 | 566 | 654 | 104.62
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA 345/115 1TR | SB:PA230_R506 | 566 | 654 | 104.62
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA 345/115 2TR | SB:PA230_R506 | 566 | 654 | 104.62
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - 9MI1 9 345 | SB:PA230_R506 | 566 | 654 | 104.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - VOL 20 345 | SB:PA230_R506 | 566 | 654 | 104.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M6TR | S:PA_HNTL77 | 566 | 654 | 104.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M8TR | S:PA_HNTL77 | 566 | 654 | 104.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - IND 25 345 | SB:PA230_R506 | 566 | 654 | 104.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 7-9 | S:PA_HNTL77 | 566 | 654 | 104.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 10-12 | S:PA_HNTL77 | 566 | 654 | 104.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW - VOL 11 345 | SB:PA230_R506 | 566 | 654 | 104.59
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW - VOL 12 345 | SB:PA230_R506 | 566 | 654 | 104.59
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 1-3 | S:PA_HNTL77 | 566 | 654 | 104.59
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 4-6 | S:PA_HNTL77 | 566 | 654 | 104.59
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 2TR | B:PACKT4 | 566 | 654 | 104.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW 345/115 1TR | SB:PA230_R506 | 566 | 654 | 104.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R3430 | 566 | 654 | 104.57
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R506 | 566 | 654 | 104.56
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R506 | 566 | 654 | 104.56
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PA230_R506 | 566 | 654 | 104.48
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - WTRCR 31 345 | S:PA_HNTL77 | 566 | 654 | 104.44
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - EDIC 2-15 345 | SB:PA230_R3430 | 566 | 654 | 104.43
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | B:Hunt67 | 566 | 654 | 104.41
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH 345/115 5TR | SB:PA230_R506 | 566 | 654 | 104.4
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-2 345 | SB:PA230_R3430 | 566 | 654 | 104.36
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:DARLIN1 | 566 | 654 | 104.34
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:JAMESGN7 | SB:PA230_R3430 | 566 | 654 | 104.32
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MEYER - CANDQUA 60 230 | B:PACKT4 | 566 | 654 | 104.31
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL - CLAY PC-2 345 | SB:PA230_R3430 | 566 | 654 | 104.27
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL - CLAY PC-1 345 | SB:PA230_R3430 | 566 | 654 | 104.26
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL77 | 566 | 654 | 104.22
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL77 | 566 | 654 | 104.22
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL77 | 566 | 654 | 104.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GEN:KINTIGH | S:PA_HNTL77 | 566 | 654 | 104.15
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | BECK - PACKARD BP76 230 | B:PACKT4 | 566 | 654 | 104.13
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | EDIC - FITZ 345 | SB:PA230_R3430 | 566 | 654 | 104.03
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:SCRIBA_R230 | 566 | 654 | 103.97
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:9 MI PT2 | 566 | 654 | 103.97
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:SCRIBA_R925 | 566 | 654 | 103.97
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-SR_37&W-F_171 | SB:PA230_R3430 | 566 | 654 | 103.94
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:FV-5M_37&W-F_171 | SB:PA230_R3430 | 566 | 654 | 103.94
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 11 | B:PACKT4 | 566 | 654 | 103.94
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 12 | B:PACKT4 | 566 | 654 | 103.94
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 13 | B:PACKT4 | 566 | 654 | 103.94
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 8 | B:PACKT4 | 566 | 654 | 103.94
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 9 | B:PACKT4 | 566 | 654 | 103.94
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 10 | B:PACKT4 | 566 | 654 | 103.93
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - ELM 70 230 | S:PA_HNTL77 | 566 | 654 | 103.89
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OS - EL - LFYTE 17 345 | SB:PA230_R3430 | 566 | 654 | 103.88
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1302 | 566 | 654 | 103.87
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 1TR | SB:PA230_R3430 | 566 | 654 | 103.8
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 2TR | SB:PA230_R3430 | 566 | 654 | 103.8
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDL - FRASER 32 345 | S:PA_HNTL77 | 566 | 654 | 103.8
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PANL 345/115 3TR | SB:PA230_R3430 | 566 | 654 | 103.79
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-WC_30&W-F_171 | SB:PA230_R506 | 566 | 654 | 103.77
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STONYCR - WTHRS 230 | SB:PA230_R506 | 566 | 654 | 103.77
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:GINNA | B:PACKT4 | 566 | 654 | 103.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY 345/115 1TR | SB:PA230_R3430 | 566 | 654 | 103.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY 345/115 2TR | SB:PA230_R3430 | 566 | 654 | 103.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | VOL - MARCY 19 345 | SB:PA230_R3430 | 566 | 654 | 103.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - 5MILE 345 | SB:PA230_R3430 | 566 | 654 | 103.7
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R506 | 566 | 654 | 103.68
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCWC/NWES | SB:PA230_R506 | 566 | 654 | 103.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:MBWC/NWES | SB:PA230_R506 | 566 | 654 | 103.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 3 115 | SB:PA230_R3430 | 566 | 654 | 103.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - TEAL 10 115 | SB:PA230_R3430 | 566 | 654 | 103.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - TEAL 11 115 | SB:PA230_R3430 | 566 | 654 | 103.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - LM 14 115 | SB:PA230_R3430 | 566 | 654 | 103.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS2 | SB:PA230_R3430 | 566 | 654 | 103.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 5 115 | SB:PA230_R3430 | 566 | 654 | 103.62
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LHH - CLAY 7 115 | SB:PA230_R3430 | 566 | 654 | 103.62
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - WOOD 17 115 | SB:PA230_R3430 | 566 | 654 | 103.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - VOL 21 345 | SB:PA230_R3430 | 566 | 654 | 103.61
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FUL - CLAY 4 115 | SB:PA230_R3430 | 566 | 654 | 103.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - 9MI1 9 345 | SB:PA230_R3430 | 566 | 654 | 103.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - VOL 20 345 | SB:PA230_R3430 | 566 | 654 | 103.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA 345/115 1TR | SB:PA230_R3430 | 566 | 654 | 103.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA 345/115 2TR | SB:PA230_R3430 | 566 | 654 | 103.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW - VOL 11 345 | SB:PA230_R3430 | 566 | 654 | 103.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW - VOL 12 345 | SB:PA230_R3430 | 566 | 654 | 103.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - IND 25 345 | SB:PA230_R3430 | 566 | 654 | 103.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/NWES | 566 | 654 | 103.57
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OSW 345/115 1TR | SB:PA230_R3430 | 566 | 654 | 103.57
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SRIPL - ERIE E 69 230 | 566 | 654 | 103.55
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SCRIBA - FITZ 10 345 | SB:PA230_R3430 | 566 | 654 | 103.54
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | DUNKIRK - SRIPL 68 230 | 566 | 654 | 103.53
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:SRIPLEY | 566 | 654 | 103.53
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | EDIC - MRCY ue 1-7 345 | SB:PA230_R3430 | 566 | 654 | 103.53
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R3430 | 566 | 654 | 103.51
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R3430 | 566 | 654 | 103.51
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 1 | S:PA_HNTL77 | 566 | 654 | 103.5
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 2 | S:PA_HNTL77 | 566 | 654 | 103.5
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 3 | S:PA_HNTL77 | 566 | 654 | 103.5
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCMB/NWES | S:PA_HNTL77 | 566 | 654 | 103.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - PACKARD 62 230 | S:PA_HNTL77 | 566 | 654 | 103.44
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - BECK_TSA 345 | SB:PA230_R3430 | 566 | 654 | 103.43
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | 5 MILE - STOLLE 37A 345 | SB:PA230_R3430 | 566 | 654 | 103.42
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - BECK_TSB 345 | SB:PA230_R3430 | 566 | 654 | 103.42
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R3430 | 566 | 654 | 103.41
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:5M-SR_37&W-F_171 | SB:PA230_R3430 | 566 | 654 | 103.4
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1202 | 566 | 654 | 103.4
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ERIE E - 4 MILE 230 | B:PACKT4 | 566 | 654 | 103.39
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - PACKARD 61 230 | S:PA_HNTL77 | 566 | 654 | 103.37
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-MB_30&W-F_171 | S:PA_HNTL77 | 566 | 654 | 103.37
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH 345/115 5TR | SB:PA230_R3430 | 566 | 654 | 103.36
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MAINSBRG - HOMERCITY 30B 345 | S:PA_HNTL77 | 566 | 654 | 103.3
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MEYER - CANDQUA 60 230 | S:PA_HNTL77 | 566 | 654 | 103.22
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | STONYCR - WTHRS 230 | 566 | 654 | 103.2
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-WC_30&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 103.14
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SHLDON - STONYCR 230 | B:PACKT4 | 566 | 654 | 103.14
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | B:Hunt67 | 566 | 654 | 103.09
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | WTRCR - MAINSBRG 30A 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 103.04
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCWC/NWES | HUNTLEY - PACKARD 77 230 | 566 | 654 | 103.01
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:MBWC/NWES | HUNTLEY - PACKARD 77 230 | 566 | 654 | 103.01
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STONYCR - WTHRS 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 102.99
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GEN:KINTIGH | SB:PA230_R506 | 566 | 654 | 102.89
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 11 | S:PA_HNTL77 | 566 | 654 | 102.86
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 12 | S:PA_HNTL77 | 566 | 654 | 102.86
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 13 | S:PA_HNTL77 | 566 | 654 | 102.86
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 8 | S:PA_HNTL77 | 566 | 654 | 102.85
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 9 | S:PA_HNTL77 | 566 | 654 | 102.85
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 10 | S:PA_HNTL77 | 566 | 654 | 102.84
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WTHERS230 | 566 | 654 | 102.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M7TR | SB:PA230_R506 | 566 | 654 | 102.77
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - FARMVLY | SB:PA230_R506 | 566 | 654 | 102.76
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:GINNA | S:PA_HNTL77 | 566 | 654 | 102.67
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-WC_30&W-F_171 | SB:PA230_R3430 | 566 | 654 | 102.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DUNKIRK - SRIPL 68 230 | B:PACKT4 | 566 | 654 | 102.64
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SRIPL - ERIE E 69 230 | B:PACKT4 | 566 | 654 | 102.63
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | WTHRS - MEYER 230 | B:PACKT4 | 566 | 654 | 102.63
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M6TR | SB:PA230_R506 | 566 | 654 | 102.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M8TR | SB:PA230_R506 | 566 | 654 | 102.6
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | T:77&80 | 566 | 654 | 102.6
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R3430 | 566 | 654 | 102.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCWC/NWES | SB:PA230_R3430 | 566 | 654 | 102.57
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:MBWC/NWES | SB:PA230_R3430 | 566 | 654 | 102.57
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 1 | SB:PA230_R506 | 566 | 654 | 102.51
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 2 | SB:PA230_R506 | 566 | 654 | 102.51
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 3 | SB:PA230_R506 | 566 | 654 | 102.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STONYCR - WTHRS 230 | SB:PA230_R3430 | 566 | 654 | 102.51
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 1-3 | SB:PA230_R506 | 566 | 654 | 102.5
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 7-9 | SB:PA230_R506 | 566 | 654 | 102.5
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 10-12 | SB:PA230_R506 | 566 | 654 | 102.5
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 4-6 | SB:PA230_R506 | 566 | 654 | 102.49
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:DUNKG4 | 566 | 654 | 102.48
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | B:PACKT4 | 566 | 654 | 102.45
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - WTRCR 31 345 | SB:PA230_R506 | 566 | 654 | 102.43
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GEN:KINTIGH | HUNTLEY - PACKARD 77 230 | 566 | 654 | 102.3
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R506 | 566 | 654 | 102.29
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R506 | 566 | 654 | 102.26
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCMB/NWES | SB:PA230_R506 | 566 | 654 | 102.26
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R506 | 566 | 654 | 102.25
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-MB_30&W-F_171 | SB:PA230_R506 | 566 | 654 | 102.2
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ERIE E - 4 MILE 230 | S:PA_HNTL77 | 566 | 654 | 102.15
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R506 | 566 | 654 | 102.1
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/WF/NWES | 566 | 654 | 102.05
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:DKSR/WRFL | 566 | 654 | 102.04
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/WRFL | 566 | 654 | 102.03
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SHLDON - STONYCR 230 | S:PA_HNTL77 | 566 | 654 | 102
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - ELM 70 230 | SB:PA230_R506 | 566 | 654 | 101.96
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1202 | 566 | 654 | 101.96
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDL - FRASER 32 345 | SB:PA230_R506 | 566 | 654 | 101.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 2TR | SB:PA230_R3430 | 566 | 654 | 101.77
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | B:Hunt67 | 566 | 654 | 101.76
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GEN:KINTIGH | SB:PA230_R3430 | 566 | 654 | 101.7
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M7TR | SB:PA230_R3430 | 566 | 654 | 101.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - FARMVLY | SB:PA230_R3430 | 566 | 654 | 101.65
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 1 | SB:PA230_R3430 | 566 | 654 | 101.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 2 | SB:PA230_R3430 | 566 | 654 | 101.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 3 | SB:PA230_R3430 | 566 | 654 | 101.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCMB/NWES | HUNTLEY - PACKARD 77 230 | 566 | 654 | 101.54
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 2TR | SB:PA230_R506 | 566 | 654 | 101.52
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M6TR | SB:PA230_R3430 | 566 | 654 | 101.51
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL 230/115 M8TR | SB:PA230_R3430 | 566 | 654 | 101.51
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-MB_30&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 101.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 7-9 | SB:PA230_R3430 | 566 | 654 | 101.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 10-12 | SB:PA230_R3430 | 566 | 654 | 101.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:KINTIGH | 566 | 654 | 101.45
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 1-3 | SB:PA230_R3430 | 566 | 654 | 101.45
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:LEW 4-6 | SB:PA230_R3430 | 566 | 654 | 101.45
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:68&160 | 566 | 654 | 101.43
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SRIPL - ERIE E 69 230 | S:PA_HNTL77 | 566 | 654 | 101.41
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DUNKIRK - SRIPL 68 230 | S:PA_HNTL77 | 566 | 654 | 101.4
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MAINSBRG - HOMERCITY 30B 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 101.38
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | T:77&80 | 566 | 654 | 101.38
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - WTRCR 31 345 | SB:PA230_R3430 | 566 | 654 | 101.32
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MEYER - CANDQUA 60 230 | SB:PA230_R506 | 566 | 654 | 101.29
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL77 | 566 | 654 | 101.26
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_R833 | 566 | 654 | 101.16
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:GARD72&79 | 566 | 654 | 101.16
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:73&74 | 566 | 654 | 101.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R3430 | 566 | 654 | 101.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R3430 | 566 | 654 | 101.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R3430 | 566 | 654 | 101.11
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCMB/NWES | SB:PA230_R3430 | 566 | 654 | 101.11
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-MB_30&W-F_171 | SB:PA230_R3430 | 566 | 654 | 101.04
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R3430 | 566 | 654 | 100.95
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - ELM 70 230 | SB:PA230_R3430 | 566 | 654 | 100.83
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 11 | SB:PA230_R506 | 566 | 654 | 100.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 12 | SB:PA230_R506 | 566 | 654 | 100.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 13 | SB:PA230_R506 | 566 | 654 | 100.75
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 10 | SB:PA230_R506 | 566 | 654 | 100.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 8 | SB:PA230_R506 | 566 | 654 | 100.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:NIAG. 9 | SB:PA230_R506 | 566 | 654 | 100.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:GINNA | SB:PA230_R506 | 566 | 654 | 100.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDL - FRASER 32 345 | SB:PA230_R3430 | 566 | 654 | 100.67
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | WTHRS - MEYER 230 | S:PA_HNTL77 | 566 | 654 | 100.59
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ERIE E - 4 MILE 230 | SB:PA230_R506 | 566 | 654 | 100.52
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1302 | 566 | 654 | 100.41
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1302 | 566 | 654 | 100.31
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 2TR | SB:PA230_R3430 | 566 | 654 | 100.3
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DUNK230_R1312 | 566 | 654 | 100.29
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SHLDON - STONYCR 230 | SB:PA230_R506 | 566 | 654 | 100.24
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-WC_30&W-F_171 | B:PACKT4 | 566 | 654 | 100.21
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | WTRCR - MAINSBRG 30A 345 | B:PACKT4 | 566 | 654 | 100.14
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STONYCR - WTHRS 230 | B:PACKT4 | 566 | 654 | 100.13
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | MEYER - CANDQUA 60 230 | SB:PA230_R3430 | 566 | 654 | 100.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HCWC/NWES | B:PACKT4 | 566 | 654 | 100.11
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:MBWC/NWES | B:PACKT4 | 566 | 654 | 100.11
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1302 | 566 | 654 | 100.11
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 Max |  |  |  |  | 137.87
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 556 | 644 | 150.14
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL77 | 556 | 644 | 149.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 148.93
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 230 | 556 | 644 | 148.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 556 | 644 | 148.1
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3430 | 556 | 644 | 147.1
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 556 | 644 | 147.03
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | B:PACKT4 | 556 | 644 | 146.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 556 | 644 | 146.42
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 146.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:61&64 | 556 | 644 | 145.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 556 | 644 | 145.54
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 556 | 644 | 145.51
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 145.23
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3430 | 556 | 644 | 144.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | B:PACKT4 | 556 | 644 | 144.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_T7-12 | 556 | 644 | 143.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | SB:PA230_R506 | 556 | 644 | 143.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 556 | 644 | 143.22
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3430 | 556 | 644 | 143.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 556 | 644 | 143.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | B:PACKT4 | 556 | 644 | 142.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 142.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL77 | 556 | 644 | 141.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 556 | 644 | 141.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 141.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 230 | 556 | 644 | 141.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R506 | 556 | 644 | 141.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 556 | 644 | 140.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:255_345B302 | 556 | 644 | 140.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R3430 | 556 | 644 | 140.66
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAG345_3108 | 556 | 644 | 140.66
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - NEWROCH 1 345 | 556 | 644 | 140.61
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 140.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 556 | 644 | 140.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | B:PACKT4 | 556 | 644 | 140.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 556 | 644 | 139.87
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R506 | 556 | 644 | 139.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 139.46
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:255_345B202 | 556 | 644 | 139.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SOMERSET - NEWROCH 1 345 | 556 | 644 | 139.15
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 556 | 644 | 139.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 556 | 644 | 139.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 138.76
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3430 | 556 | 644 | 138.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:61&64 | 556 | 644 | 138.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3430 | 556 | 644 | 138.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | B:PACKT4 | 556 | 644 | 138.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | B:PACKT4 | 556 | 644 | 138.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_T7-12 | 556 | 644 | 137.56
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3430 | 556 | 644 | 137.04
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 556 | 644 | 136.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | B:PACKT4 | 556 | 644 | 136.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R506 | 556 | 644 | 136.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 136.47
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:40&41 | 556 | 644 | 136.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3430 | 556 | 644 | 136.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | B:PACKT4 | 556 | 644 | 135.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | SB:PA230_R506 | 556 | 644 | 134.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - HOMERCTY | 556 | 644 | 134.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL77 | 556 | 644 | 134.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-FV_37&W-F_171 | 556 | 644 | 134.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:41&33 | 556 | 644 | 134.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:255_345B302 | 556 | 644 | 134.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAG345_3108 | 556 | 644 | 134.66
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 134.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - NEWROCH 1 345 | 556 | 644 | 134.63
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | SB:PA230_R506 | 556 | 644 | 134.46
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAW230_2014 | 556 | 644 | 134.44
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 556 | 644 | 134.34
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL77 | 556 | 644 | 134.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 133.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:34&42 | 556 | 644 | 133.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R506 | 556 | 644 | 133.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R3430 | 556 | 644 | 133.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 133.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA 230/115 1TR | 556 | 644 | 133.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | B:PACKT4 | 556 | 644 | 133.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_1 | 556 | 644 | 133.42
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_2 | 556 | 644 | 133.42
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | LFYTE - CLARKCRNS 36A 345 | 556 | 644 | 133.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAFA_ELB | 556 | 644 | 133.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAFAYETT | 556 | 644 | 133.34
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | T:77&80 | 556 | 644 | 133.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | S:PA_HNTL77 | 556 | 644 | 133.23
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:255_345B202 | 556 | 644 | 133.11
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SOMERSET - NEWROCH 1 345 | 556 | 644 | 133.02
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 132.96
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_3 | 556 | 644 | 132.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_4 | 556 | 644 | 132.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | PACKARD 230/115 3TR | 556 | 644 | 132.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R506 | 556 | 644 | 132.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B5 | 556 | 644 | 132.58
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B6 | 556 | 644 | 132.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - CLARKCRNS 36B 345 | 556 | 644 | 132.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | T:77&80 | 556 | 644 | 132.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE_B | 556 | 644 | 132.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3430 | 556 | 644 | 132.27
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | S:PA_HNTL77 | 556 | 644 | 132.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | B:PACKT4 | 556 | 644 | 132.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:31&41 | 556 | 644 | 131.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_42-4182 | 556 | 644 | 131.93
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 131.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3208 | 556 | 644 | 131.7
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R915 | 556 | 644 | 131.66
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:MP11&41 | 556 | 644 | 131.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_4182 | 556 | 644 | 131.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3202 | 556 | 644 | 131.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - COOPERS 345 SC | 556 | 644 | 131.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:30&40 | 556 | 644 | 131.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R3430 | 556 | 644 | 131.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3430 | 556 | 644 | 131.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAG345_3308 | 556 | 644 | 131.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | S:PA_HNTL77 | 556 | 644 | 131.14
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT4 | 556 | 644 | 131.14
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:77&76 | 556 | 644 | 131.11
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | S:PA_HNTL77 | 556 | 644 | 131.08
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - KINTIGH 345 | 556 | 644 | 131.08
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R400 | 556 | 644 | 131.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | B:PACKT4 | 556 | 644 | 130.89
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R935 | 556 | 644 | 130.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FRASER 345 SC | 556 | 644 | 130.85
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:FRAS345_B1-4062 | 556 | 644 | 130.85
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:FRAS345_40-B262 | 556 | 644 | 130.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 130.83
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | SB:PA230_R3430 | 556 | 644 | 130.82
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | S:PA_HNTL77 | 556 | 644 | 130.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 77 230 | 556 | 644 | 130.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | B:PACKT4 | 556 | 644 | 130.63
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | T:77&80 | 556 | 644 | 130.59
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 130.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:69J&70K | 556 | 644 | 130.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:170 | 556 | 644 | 130.46
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:180 | 556 | 644 | 130.45
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:90 | 556 | 644 | 130.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | S:PA_HNTL77 | 556 | 644 | 130.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:40&41 | 556 | 644 | 130.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._99 | 556 | 644 | 130.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE | 556 | 644 | 130.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL77 | 556 | 644 | 130.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._77 | 556 | 644 | 130.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3308 | 556 | 644 | 130.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:MP12&18 | 556 | 644 | 130.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:160 | 556 | 644 | 130.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:150 | 556 | 644 | 130.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_3414 | 556 | 644 | 130.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_3514 | 556 | 644 | 130.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:PECHBTM2 | 556 | 644 | 130.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:W89&W90 | 556 | 644 | 130.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R140 | 556 | 644 | 130.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - N.SCOT99 I8 345 | 556 | 644 | 130.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3314 | 556 | 644 | 130.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:F38&F39 | 556 | 644 | 130.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 130.12
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SUSQ1 | 556 | 644 | 130.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_2T8082 | 556 | 644 | 130.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3108 | 556 | 644 | 130.03
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - N.SCOT77 I4 345 | 556 | 644 | 130.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 129.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:F30&F31 | 556 | 644 | 129.98
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-SR_37&W-F_171 | 556 | 644 | 129.96
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:FV-5M_37&W-F_171 | 556 | 644 | 129.96
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_376512 | 556 | 644 | 129.96
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | S:PA_HNTL77 | 556 | 644 | 129.96
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_31153 | 556 | 644 | 129.93
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - 5MILE 345 | 556 | 644 | 129.93
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_34XC | 556 | 644 | 129.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R935 | 556 | 644 | 129.87
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R945 | 556 | 644 | 129.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PV345_RNS5 | 556 | 644 | 129.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PV345_RNS4 | 556 | 644 | 129.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LEEDS345_R9293 | 556 | 644 | 129.79
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SALEMG1 | 556 | 644 | 129.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:HOPECG1 | 556 | 644 | 129.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | SB:PA230_R3430 | 556 | 644 | 129.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:LIMERCK2 | 556 | 644 | 129.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_3456 | 556 | 644 | 129.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R506 | 556 | 644 | 129.7
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_34-B382 | 556 | 644 | 129.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_B2-3482 | 556 | 644 | 129.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HURLEY - ROCKT CMT/MTR-34 345 | 556 | 644 | 129.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CMT/MTR-34 345 | 556 | 644 | 129.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | HUNTLEY - PACKARD 77 230 | 556 | 644 | 129.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R150 | 556 | 644 | 129.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3908 | 556 | 644 | 129.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R160 | 556 | 644 | 129.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3808 | 556 | 644 | 129.59
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | B:PACKT4 | 556 | 644 | 129.56
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - DEW 13 345 | 556 | 644 | 129.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LEEDS345_R94301 | 556 | 644 | 129.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R110 | 556 | 644 | 129.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_4255 | 556 | 644 | 129.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R150 | 556 | 644 | 129.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R160 | 556 | 644 | 129.47
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_B2-4282 | 556 | 644 | 129.46
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 644 | 129.46
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 644 | 129.46
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 1-16 345 | 556 | 644 | 129.46
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 556 | 644 | 129.45
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 556 | 644 | 129.45
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | S:PA_HNTL77 | 556 | 644 | 129.45
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R10 | 556 | 644 | 129.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DUNW345_3 | 556 | 644 | 129.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LEEDS345_R92 | 556 | 644 | 129.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 556 | 644 | 129.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 556 | 644 | 129.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3102 | 556 | 644 | 129.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 556 | 644 | 129.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 556 | 644 | 129.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DUNW345_8 | 556 | 644 | 129.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FITZ - EDIC FEI 345 | 556 | 644 | 129.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FITZ 345 | 556 | 644 | 129.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DEWI345_R915 | 556 | 644 | 129.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DEWI345_R130 | 556 | 644 | 129.34
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DEWI345_R220 | 556 | 644 | 129.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL77 | 556 | 644 | 129.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | VOLNEY - MARCY I9 345 | 556 | 644 | 129.32
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | VOL - MARCY 19 345 | 556 | 644 | 129.32
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:VOLN_R925 | 556 | 644 | 129.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3914 | 556 | 644 | 129.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3814 | 556 | 644 | 129.27
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 129.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | S:PA_HNTL77 | 556 | 644 | 129.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - HOMERCTY | 556 | 644 | 129.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | S:PA_HNTL77 | 556 | 644 | 129.06
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | S:PA_HNTL77 | 556 | 644 | 129.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-FV_37&W-F_171 | 556 | 644 | 128.99
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 128.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:41&33 | 556 | 644 | 128.91
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 128.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1302 | 556 | 644 | 128.83
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | S:PA_HNTL77 | 556 | 644 | 128.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | S:PA_HNTL77 | 556 | 644 | 128.73
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 128.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 128.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | S:PA_HNTL77 | 556 | 644 | 128.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | S:PA_HNTL77 | 556 | 644 | 128.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL77 | 556 | 644 | 128.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | SB:PA230_R3430 | 556 | 644 | 128.58
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | S:PA_HNTL77 | 556 | 644 | 128.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R506 | 556 | 644 | 128.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 128.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | SB:PA230_R3430 | 556 | 644 | 128.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | S:PA_HNTL77 | 556 | 644 | 128.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | S:PA_HNTL77 | 556 | 644 | 128.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | S:PA_HNTL77 | 556 | 644 | 128.47
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | S:PA_HNTL77 | 556 | 644 | 128.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 128.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-1 345 | S:PA_HNTL77 | 556 | 644 | 128.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | B:PACKT4 | 556 | 644 | 128.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 128.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 128.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 128.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | B:PACKT4 | 556 | 644 | 128.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | SB:PA230_R3430 | 556 | 644 | 128.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 128.21
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 128.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-1 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 128.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | B:PACKT4 | 556 | 644 | 128.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:34&42 | 556 | 644 | 127.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1302 | 556 | 644 | 127.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | SB:PA230_R3430 | 556 | 644 | 127.79
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDL - FRASER 32 345 | 556 | 644 | 127.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FRASER - OAKDLE 32 345 | 556 | 644 | 127.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT2 | 556 | 644 | 127.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RAIN345_1W | 556 | 644 | 127.63
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:FRAS345_B1-3262 | 556 | 644 | 127.63
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RAIN345_9W | 556 | 644 | 127.62
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R506 | 556 | 644 | 127.61
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: RAVENSWOOD | 556 | 644 | 127.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:30 | 556 | 644 | 127.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | BWLN - WHAV -LDN 67 345 | 556 | 644 | 127.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT1 | 556 | 644 | 127.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | B:PACKT4 | 556 | 644 | 127.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B2 | 556 | 644 | 127.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAFA_ELB | 556 | 644 | 127.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_1 | 556 | 644 | 127.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_2 | 556 | 644 | 127.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 2TR | 556 | 644 | 127.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | LFYTE - CLARKCRNS 36A 345 | 556 | 644 | 127.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROSE345_30553 | 556 | 644 | 127.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_4-56-2 | 556 | 644 | 127.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_1-56-2 | 556 | 644 | 127.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAFAYETT | 556 | 644 | 127.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_6-56-2 | 556 | 644 | 127.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 2TR | SB:PA230_R3430 | 556 | 644 | 127.42
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B3 | 556 | 644 | 127.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - WTRCR 31 345 | 556 | 644 | 127.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_3-56-2 | 556 | 644 | 127.39
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | SB:PA230_R506 | 556 | 644 | 127.38
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:NOEND | 556 | 644 | 127.38
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROSE345_30551 | 556 | 644 | 127.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M7TR | 556 | 644 | 127.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | SB:PA230_R3430 | 556 | 644 | 127.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROSE345_31152 | 556 | 644 | 127.34
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | T:77&80 | 556 | 644 | 127.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RMP345_T1500 | 556 | 644 | 127.32
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WATRC345_31-2 | 556 | 644 | 127.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | RAMAPO - BRNCHBRG 5018 345 | 556 | 644 | 127.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON2 | 556 | 644 | 127.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2208 | 556 | 644 | 127.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RMP345_1500-2X | 556 | 644 | 127.27
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2214 | 556 | 644 | 127.27
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS17-20 | 556 | 644 | 127.27
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2224 | 556 | 644 | 127.27
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | SB:PA230_R506 | 556 | 644 | 127.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1724 | 556 | 644 | 127.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1714 | 556 | 644 | 127.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1524 | 556 | 644 | 127.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1514 | 556 | 644 | 127.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1508 | 556 | 644 | 127.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | T:77&80 | 556 | 644 | 127.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2524 | 556 | 644 | 127.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2514 | 556 | 644 | 127.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS21-24 | 556 | 644 | 127.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2508 | 556 | 644 | 127.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 2TR | B:PACKT4 | 556 | 644 | 127.22
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON1 | 556 | 644 | 127.17
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | B:PACKT4 | 556 | 644 | 127.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | T:77&80 | 556 | 644 | 127.11
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M6TR | 556 | 644 | 127.11
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M8TR | 556 | 644 | 127.11
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3208 | 556 | 644 | 127.08
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:AT_R6361 | 556 | 644 | 127.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BESICORP | 556 | 644 | 127.03
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:EMPIRE | 556 | 644 | 127.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3430 | 556 | 644 | 127
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | S:EMPIRE | 556 | 644 | 126.96
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | SB:PA230_R3430 | 556 | 644 | 126.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: IND PT 2 | 556 | 644 | 126.87
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN GILBOA #3&4 | 556 | 644 | 126.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3302 | 556 | 644 | 126.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:72&69 | 556 | 644 | 126.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_3 | 556 | 644 | 126.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_4 | 556 | 644 | 126.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN GILBOA #1&2 | 556 | 644 | 126.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3202 | 556 | 644 | 126.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3308 | 556 | 644 | 126.79
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHN_11 | 556 | 644 | 126.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHN_9 | 556 | 644 | 126.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:NTHF3&4 | 556 | 644 | 126.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | S:PA_HNTL77 | 556 | 644 | 126.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHN_7 | 556 | 644 | 126.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | B:PACKT4 | 556 | 644 | 126.73
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - FARMVLY | 556 | 644 | 126.73
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | S:PA_HNTL77 | 556 | 644 | 126.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | BECK - PACKARD BP76 230 | 556 | 644 | 126.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: IND PT 3 | 556 | 644 | 126.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B5 | 556 | 644 | 126.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | B:PACKT4 | 556 | 644 | 126.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHS_3 | 556 | 644 | 126.63
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHS_1 | 556 | 644 | 126.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B6 | 556 | 644 | 126.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - CLARKCRNS 36B 345 | 556 | 644 | 126.62
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | S:PA_HNTL77 | 556 | 644 | 126.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE_B | 556 | 644 | 126.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | SB:PA230_R3430 | 556 | 644 | 126.59
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | SB:PA230_R3430 | 556 | 644 | 126.59
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | SB:PA230_R3430 | 556 | 644 | 126.56
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:67&68&BW | 556 | 644 | 126.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HILLSIDE 230/115 4TR | 556 | 644 | 126.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:HILLSIDE | 556 | 644 | 126.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HILL_B412 | 556 | 644 | 126.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | S:PA_HNTL77 | 556 | 644 | 126.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | S:PA_HNTL77 | 556 | 644 | 126.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | S:PA_HNTL77 | 556 | 644 | 126.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | S:PA_HNTL77 | 556 | 644 | 126.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | S:PA_HNTL77 | 556 | 644 | 126.47
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 126.47
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | HUNTLEY - PACKARD 77 230 | 556 | 644 | 126.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:SITHE 1 | 556 | 644 | 126.42
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:SITHE 2 | 556 | 644 | 126.42
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:BETHSTM | 556 | 644 | 126.42
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | S:PA_HNTL77 | 556 | 644 | 126.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | S:PA_HNTL77 | 556 | 644 | 126.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HUNTLEY - ELM 70 230 | 556 | 644 | 126.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HCWC/NWES | 556 | 644 | 126.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:MBWC/NWES | 556 | 644 | 126.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | B:PACKT4 | 556 | 644 | 126.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | B:PACKT4 | 556 | 644 | 126.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | B:PACKT4 | 556 | 644 | 126.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WATRC345_30-3142 | 556 | 644 | 126.32
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | WTRCR - MAINSBRG 30A 345 | 556 | 644 | 126.32
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 126.32
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | SB:PA230_R3430 | 556 | 644 | 126.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WATRC345_B1-3042 | 556 | 644 | 126.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HILL_68-B412 | 556 | 644 | 126.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:120_130 | 556 | 644 | 126.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:130 | 556 | 644 | 126.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:W97&W98 | 556 | 644 | 126.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STNYRDG - HILLSIDE 68B 230 | 556 | 644 | 126.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-WC_30&W-F_171 | 556 | 644 | 126.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 126.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 126.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 126.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 126.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 126.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL77 | 556 | 644 | 126.17
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | SB:PA230_R3430 | 556 | 644 | 126.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL77 | 556 | 644 | 126.14
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL77 | 556 | 644 | 126.12
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 126.1
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 126.1
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R3430 | 556 | 644 | 126.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R3430 | 556 | 644 | 126.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | B:PACKT4 | 556 | 644 | 126.08
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1302 | 556 | 644 | 126.06
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R3430 | 556 | 644 | 126.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:31&41 | 556 | 644 | 126.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | SB:PA230_R3430 | 556 | 644 | 126.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | SB:PA230_R506 | 556 | 644 | 126.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HCMB/NWES | 556 | 644 | 126.03
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | SB:PA230_R3430 | 556 | 644 | 126.02
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R3430 | 556 | 644 | 126.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_42-4182 | 556 | 644 | 126.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R3430 | 556 | 644 | 126.01
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL - DUNKIRK 73 230 | 556 | 644 | 126
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:DUNKG3 | 556 | 644 | 125.98
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL - DUNKIRK 74 230 | 556 | 644 | 125.98
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MAINSBRG - HOMERCITY 30B 345 | 556 | 644 | 125.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | B:PACKT4 | 556 | 644 | 125.96
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK_TSA 345 | SB:PA230_R3430 | 556 | 644 | 125.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK_TSB 345 | SB:PA230_R3430 | 556 | 644 | 125.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | S:PA_HNTL77 | 556 | 644 | 125.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | S:PA_HNTL77 | 556 | 644 | 125.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | S:PA_HNTL77 | 556 | 644 | 125.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | SB:PA230_R3430 | 556 | 644 | 125.93
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3430 | 556 | 644 | 125.9
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:PACKT4 | 556 | 644 | 125.9
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH 345/115 5TR | SB:PA230_R3430 | 556 | 644 | 125.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 125.87
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | SB:PA230_R3430 | 556 | 644 | 125.87
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | B:PACKT4 | 556 | 644 | 125.87
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-MB_30&W-F_171 | 556 | 644 | 125.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | B:PACKT4 | 556 | 644 | 125.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | B:PACKT4 | 556 | 644 | 125.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-1 345 | SB:PA230_R3430 | 556 | 644 | 125.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 125.85
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 125.83
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:KINT_39-B112 | 556 | 644 | 125.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3208 | 556 | 644 | 125.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:KINT_B1-3812 | 556 | 644 | 125.76
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT4 | 556 | 644 | 125.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK_TSA 345 | B:PACKT4 | 556 | 644 | 125.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK_TSB 345 | B:PACKT4 | 556 | 644 | 125.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R915 | 556 | 644 | 125.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:MP11&41 | 556 | 644 | 125.73
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | B:PACKT4 | 556 | 644 | 125.73
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | B:PACKT4 | 556 | 644 | 125.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:PA27&BP76 | 556 | 644 | 125.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | B:PACKT4 | 556 | 644 | 125.7
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | B:PACKT4 | 556 | 644 | 125.7
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | S:PA_HNTL77 | 556 | 644 | 125.69
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | B:PACKT4 | 556 | 644 | 125.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-1 345 | B:PACKT4 | 556 | 644 | 125.67
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 125.66
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 125.66
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 125.66
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_4182 | 556 | 644 | 125.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3202 | 556 | 644 | 125.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - COOPERS 345 SC | 556 | 644 | 125.57
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:61&191 | 556 | 644 | 125.56
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | T:77&80 | 556 | 644 | 125.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:30&40 | 556 | 644 | 125.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 125.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - PACKARD 62 230 | 556 | 644 | 125.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | S:PA_HNTL77 | 556 | 644 | 125.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | PACKARD 230/115 3TR | 556 | 644 | 125.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - PACKARD 61 230 | 556 | 644 | 125.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:77&76 | 556 | 644 | 125.18
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:62&PA27 | 556 | 644 | 125.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | S:PA_HNTL77 | 556 | 644 | 125.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R400 | 556 | 644 | 125.17
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R955 | 556 | 644 | 125.17
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:OSWEGO 5 | 556 | 644 | 125.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R965 | 556 | 644 | 125.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | S:PA_HNTL77 | 556 | 644 | 125.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | S:PA_HNTL77 | 556 | 644 | 125.09
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAG345_3308 | 556 | 644 | 125.06
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | SB:PA230_R506 | 556 | 644 | 125.02
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CNDGUA | 556 | 644 | 125.01
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:MILLST3 | 556 | 644 | 125
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:MLS3&OMS | 556 | 644 | 125
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:250 | 556 | 644 | 125
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA 230/115 1TR | 556 | 644 | 124.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MEYER - CANDQUA 60 230 | 556 | 644 | 124.99
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - KINTIGH 345 | 556 | 644 | 124.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R935 | 556 | 644 | 124.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.94
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FRASER 345 SC | 556 | 644 | 124.93
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:FRAS345_B1-4062 | 556 | 644 | 124.93
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:FRAS345_40-B262 | 556 | 644 | 124.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | SB:PA230_R506 | 556 | 644 | 124.91
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | T:77&80 | 556 | 644 | 124.89
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:FRGT/WRFL | 556 | 644 | 124.89
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.85
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R925 | 556 | 644 | 124.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:OSWEGO 6 | 556 | 644 | 124.82
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:9MIPT1 | 556 | 644 | 124.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R935 | 556 | 644 | 124.79
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | S:PA_HNTL77 | 556 | 644 | 124.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | S:PA_HNTL77 | 556 | 644 | 124.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:90 | 556 | 644 | 124.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE | 556 | 644 | 124.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | S:PA_HNTL77 | 556 | 644 | 124.67
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 61 230 | S:PA_HNTL77 | 556 | 644 | 124.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | SB:PA230_R506 | 556 | 644 | 124.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:FITZPATR | 556 | 644 | 124.59
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:69J&70K | 556 | 644 | 124.53
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:170 | 556 | 644 | 124.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:180 | 556 | 644 | 124.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | S:PA_HNTL77 | 556 | 644 | 124.51
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SEAB&OMS | 556 | 644 | 124.51
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SEABROOK | 556 | 644 | 124.51
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | S:PA_HNTL77 | 556 | 644 | 124.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | S:PA_HNTL77 | 556 | 644 | 124.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._99 | 556 | 644 | 124.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._77 | 556 | 644 | 124.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 61 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC_765_7402 | 556 | 644 | 124.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MSU1_7202>7214>7208>7214 | 556 | 644 | 124.39
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | S:PA_HNTL77 | 556 | 644 | 124.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3308 | 556 | 644 | 124.37
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:MP12&18 | 556 | 644 | 124.37
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HQ-NY 765 | 556 | 644 | 124.37
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:160 | 556 | 644 | 124.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:150 | 556 | 644 | 124.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_3414 | 556 | 644 | 124.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_3514 | 556 | 644 | 124.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | S:PA_HNTL77 | 556 | 644 | 124.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:PECHBTM2 | 556 | 644 | 124.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:W89&W90 | 556 | 644 | 124.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R140 | 556 | 644 | 124.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | SB:PA230_R3430 | 556 | 644 | 124.23
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAW230_2014 | 556 | 644 | 124.22
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.22
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3314 | 556 | 644 | 124.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - N.SCOT99 I8 345 | 556 | 644 | 124.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:F38&F39 | 556 | 644 | 124.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.19
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_2T8082 | 556 | 644 | 124.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | SB:PA230_R3430 | 556 | 644 | 124.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SHLDON - STONYCR 230 | 556 | 644 | 124.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | SB:PA230_R506 | 556 | 644 | 124.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SUSQ1 | 556 | 644 | 124.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3108 | 556 | 644 | 124.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | SB:PA230_R3430 | 556 | 644 | 124.09
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - N.SCOT77 I4 345 | 556 | 644 | 124.06
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | S:PA_HNTL77 | 556 | 644 | 124.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 124.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | B:PACKT4 | 556 | 644 | 124.04
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:F30&F31 | 556 | 644 | 124.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | S:PA_HNTL77 | 556 | 644 | 124.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_376512 | 556 | 644 | 124.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCH_34XC | 556 | 644 | 124
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_31153 | 556 | 644 | 123.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:FV-5M_37&W-F_171 | 556 | 644 | 123.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-SR_37&W-F_171 | 556 | 644 | 123.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - 5MILE 345 | 556 | 644 | 123.98
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | B:PACKT4 | 556 | 644 | 123.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | SB:PA230_R3430 | 556 | 644 | 123.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | SB:PA230_R3430 | 556 | 644 | 123.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | SB:PA230_R3430 | 556 | 644 | 123.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | SB:PA230_R3430 | 556 | 644 | 123.93
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PV345_RNS5 | 556 | 644 | 123.91
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R935 | 556 | 644 | 123.89
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PV345_RNS4 | 556 | 644 | 123.89
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R945 | 556 | 644 | 123.89
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | B:PACKT4 | 556 | 644 | 123.89
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 2TR | SB:PA230_R506 | 556 | 644 | 123.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | SB:PA230_R3430 | 556 | 644 | 123.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | SB:PA230_R3430 | 556 | 644 | 123.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:STONY230 | 556 | 644 | 123.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | S:PA_HNTL77 | 556 | 644 | 123.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SANDY_DC | 556 | 644 | 123.85
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SANDY_DC&OMS | 556 | 644 | 123.85
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LEEDS345_R9293 | 556 | 644 | 123.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SALEMG1 | 556 | 644 | 123.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:HOPECG1 | 556 | 644 | 123.82
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL77 | 556 | 644 | 123.82
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:LIMERCK2 | 556 | 644 | 123.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_3456 | 556 | 644 | 123.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | B:PACKT4 | 556 | 644 | 123.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | B:PACKT4 | 556 | 644 | 123.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | B:PACKT4 | 556 | 644 | 123.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | B:PACKT4 | 556 | 644 | 123.76
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.73
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | SB:PA230_R506 | 556 | 644 | 123.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_34-B382 | 556 | 644 | 123.72
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_B2-3482 | 556 | 644 | 123.72
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HURLEY - ROCKT CMT/MTR-34 345 | 556 | 644 | 123.72
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CMT/MTR-34 345 | 556 | 644 | 123.72
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | S:PA_HNTL77 | 556 | 644 | 123.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | B:PACKT4 | 556 | 644 | 123.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | B:PACKT4 | 556 | 644 | 123.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R3430 | 556 | 644 | 123.66
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R150 | 556 | 644 | 123.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R3430 | 556 | 644 | 123.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R3430 | 556 | 644 | 123.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CLAY345_R160 | 556 | 644 | 123.64
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3908 | 556 | 644 | 123.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3808 | 556 | 644 | 123.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | S:PA_HNTL77 | 556 | 644 | 123.59
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - DEW 13 345 | 556 | 644 | 123.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | S:PA_HNTL77 | 556 | 644 | 123.58
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LEEDS345_R94301 | 556 | 644 | 123.56
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R110 | 556 | 644 | 123.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROCK345_4255 | 556 | 644 | 123.53
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R150 | 556 | 644 | 123.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R160 | 556 | 644 | 123.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:COOP345_B2-4282 | 556 | 644 | 123.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 644 | 123.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 644 | 123.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 1-16 345 | 556 | 644 | 123.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-2 345 | S:PA_HNTL77 | 556 | 644 | 123.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 556 | 644 | 123.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 556 | 644 | 123.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R10 | 556 | 644 | 123.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-1 345 | S:PA_HNTL77 | 556 | 644 | 123.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DUNW345_3 | 556 | 644 | 123.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE345 | 556 | 644 | 123.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HOMERCTY - STOLLRD 37 345 | 556 | 644 | 123.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | 5 MILE - STOLLE 37A 345 | 556 | 644 | 123.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 556 | 644 | 123.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 556 | 644 | 123.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LEEDS345_R92 | 556 | 644 | 123.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3102 | 556 | 644 | 123.45
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | B:PACKT4 | 556 | 644 | 123.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 556 | 644 | 123.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 556 | 644 | 123.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:67&37A | 556 | 644 | 123.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | B:PACKT4 | 556 | 644 | 123.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DUNW345_8 | 556 | 644 | 123.42
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FITZ - EDIC FEI 345 | 556 | 644 | 123.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FITZ 345 | 556 | 644 | 123.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | B:PACKT4 | 556 | 644 | 123.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | S:PA_HNTL77 | 556 | 644 | 123.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | S:PA_HNTL77 | 556 | 644 | 123.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | S:PA_HNTL77 | 556 | 644 | 123.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | S:PA_HNTL77 | 556 | 644 | 123.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | S:PA_HNTL77 | 556 | 644 | 123.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DEWI345_R915 | 556 | 644 | 123.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | S:PA_HNTL77 | 556 | 644 | 123.39
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DEWI345_R130 | 556 | 644 | 123.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DEWI345_R220 | 556 | 644 | 123.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | S:STOLLE345 | 556 | 644 | 123.37
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | VOLNEY - MARCY I9 345 | 556 | 644 | 123.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | VOL - MARCY 19 345 | 556 | 644 | 123.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:VOLN_R925 | 556 | 644 | 123.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:5M-SR_37&W-F_171 | 556 | 644 | 123.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R506 | 556 | 644 | 123.31
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | S:PA_HNTL77 | 556 | 644 | 123.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | S:PA_HNTL77 | 556 | 644 | 123.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3914 | 556 | 644 | 123.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PANN345_3814 | 556 | 644 | 123.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ROCH 345/115 5TR | 556 | 644 | 123.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | S:PA_HNTL77 | 556 | 644 | 123.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | EDIC - FITZ 345 | S:PA_HNTL77 | 556 | 644 | 123.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | S:PA_HNTL77 | 556 | 644 | 123.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | SB:PA230_R506 | 556 | 644 | 123.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:GINNA | 556 | 644 | 123.23
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | SB:PA230_R3430 | 556 | 644 | 123.23
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | SB:PA230_R506 | 556 | 644 | 123.21
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | SB:PA230_R506 | 556 | 644 | 123.21
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL77 | 556 | 644 | 123.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-1 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.15
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-2 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 123.11
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OS - EL - LFYTE 17 345 | S:PA_HNTL77 | 556 | 644 | 123.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | B:PACKT4 | 556 | 644 | 123.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 1TR | S:PA_HNTL77 | 556 | 644 | 123.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 2TR | S:PA_HNTL77 | 556 | 644 | 123.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 3TR | S:PA_HNTL77 | 556 | 644 | 123
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.99
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | S:PA_HNTL77 | 556 | 644 | 122.98
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | S:PA_HNTL77 | 556 | 644 | 122.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | S:PA_HNTL77 | 556 | 644 | 122.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | VOL - MARCY 19 345 | S:PA_HNTL77 | 556 | 644 | 122.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | S:PA_HNTL77 | 556 | 644 | 122.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 1TR | S:PA_HNTL77 | 556 | 644 | 122.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 2TR | S:PA_HNTL77 | 556 | 644 | 122.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | EDIC - FITZ 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | SB:PA230_R506 | 556 | 644 | 122.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.89
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.89
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | SB:PA230_R506 | 556 | 644 | 122.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 3 115 | S:PA_HNTL77 | 556 | 644 | 122.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 10 115 | S:PA_HNTL77 | 556 | 644 | 122.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 11 115 | S:PA_HNTL77 | 556 | 644 | 122.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 5 115 | S:PA_HNTL77 | 556 | 644 | 122.82
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - LM 14 115 | S:PA_HNTL77 | 556 | 644 | 122.82
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LHH - CLAY 7 115 | S:PA_HNTL77 | 556 | 644 | 122.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - VOL 21 345 | S:PA_HNTL77 | 556 | 644 | 122.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FUL - CLAY 4 115 | S:PA_HNTL77 | 556 | 644 | 122.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - WOOD 17 115 | S:PA_HNTL77 | 556 | 644 | 122.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - 9MI1 9 345 | S:PA_HNTL77 | 556 | 644 | 122.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - VOL 20 345 | S:PA_HNTL77 | 556 | 644 | 122.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA 345/115 1TR | S:PA_HNTL77 | 556 | 644 | 122.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA 345/115 2TR | S:PA_HNTL77 | 556 | 644 | 122.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | S:PA_HNTL77 | 556 | 644 | 122.79
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OS - EL - LFYTE 17 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - IND 25 345 | S:PA_HNTL77 | 556 | 644 | 122.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW - VOL 11 345 | S:PA_HNTL77 | 556 | 644 | 122.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW - VOL 12 345 | S:PA_HNTL77 | 556 | 644 | 122.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW 345/115 1TR | S:PA_HNTL77 | 556 | 644 | 122.76
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | S:PA_HNTL77 | 556 | 644 | 122.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | S:PA_HNTL77 | 556 | 644 | 122.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - FITZ 10 345 | S:PA_HNTL77 | 556 | 644 | 122.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | EDIC - MRCY ue 1-7 345 | S:PA_HNTL77 | 556 | 644 | 122.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:SITHE 1 | S:PA_HNTL77 | 556 | 644 | 122.72
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:SITHE 2 | S:PA_HNTL77 | 556 | 644 | 122.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MASS_765_7108 | 556 | 644 | 122.72
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:OSWEGO 5 | S:PA_HNTL77 | 556 | 644 | 122.71
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 1TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.67
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 2TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.67
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 3TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.66
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:OSWEGO 6 | S:PA_HNTL77 | 556 | 644 | 122.66
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | VOL - MARCY 19 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CANDQUA - STNYRDG 68A 230 | 556 | 644 | 122.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | S:AVOCA | 556 | 644 | 122.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.63
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | SB:PA230_R3430 | 556 | 644 | 122.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 1TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 2TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.62
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:STONYRIDGE | 556 | 644 | 122.62
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | SB:PA230_R3430 | 556 | 644 | 122.59
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | SB:PA230_R506 | 556 | 644 | 122.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH 345/115 5TR | S:PA_HNTL77 | 556 | 644 | 122.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-1 345 | S:PA_HNTL77 | 556 | 644 | 122.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 11 115 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 3 115 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 10 115 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.51
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MASS_765_7102 | 556 | 644 | 122.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1302 | 556 | 644 | 122.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - LM 14 115 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 5 115 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LHH - CLAY 7 115 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | SB:PA230_R506 | 556 | 644 | 122.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FUL - CLAY 4 115 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - WOOD 17 115 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - VOL 21 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R506 | 556 | 644 | 122.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R506 | 556 | 644 | 122.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R506 | 556 | 644 | 122.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | T:77&80 | 556 | 644 | 122.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - 9MI1 9 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - VOL 20 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA 345/115 1TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA 345/115 2TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.47
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PA230_R506 | 556 | 644 | 122.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW - VOL 11 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW - VOL 12 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - IND 25 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.45
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | SB:PA230_R506 | 556 | 644 | 122.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R506 | 556 | 644 | 122.44
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW 345/115 1TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | B:PACKT4 | 556 | 644 | 122.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - FITZ 10 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:SITHE 1 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:SITHE 2 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:OSWEGO 5 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.39
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | EDIC - MRCY ue 1-7 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | B:PACKT4 | 556 | 644 | 122.39
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R506 | 556 | 644 | 122.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1302 | 556 | 644 | 122.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | SB:PA230_R506 | 556 | 644 | 122.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1302 | 556 | 644 | 122.29
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | SB:PA230_R3430 | 556 | 644 | 122.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ERIE E - 4 MILE 230 | 556 | 644 | 122.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH 345/115 5TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 122.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | SB:PA230_R3430 | 556 | 644 | 122.12
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:62&BP76 | 556 | 644 | 122.1
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | B:PACKT4 | 556 | 644 | 122.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | SB:PA230_R3430 | 556 | 644 | 122.02
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | SB:PA230_R3430 | 556 | 644 | 121.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | SB:PA230_R3430 | 556 | 644 | 121.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | B:PACKT4 | 556 | 644 | 121.85
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | B:PACKT4 | 556 | 644 | 121.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | B:PACKT4 | 556 | 644 | 121.79
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | B:PACKT4 | 556 | 644 | 121.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | SB:PA230_R3430 | 556 | 644 | 121.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RAIN345_1W | 556 | 644 | 121.66
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT2 | 556 | 644 | 121.66
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDL - FRASER 32 345 | 556 | 644 | 121.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FRASER - OAKDLE 32 345 | 556 | 644 | 121.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RAIN345_9W | 556 | 644 | 121.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:FRAS345_B1-3262 | 556 | 644 | 121.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: RAVENSWOOD | 556 | 644 | 121.64
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:30 | 556 | 644 | 121.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | BWLN - WHAV -LDN 67 345 | 556 | 644 | 121.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT1 | 556 | 644 | 121.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 2TR | 556 | 644 | 121.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B2 | 556 | 644 | 121.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROSE345_30553 | 556 | 644 | 121.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_4-56-2 | 556 | 644 | 121.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | SB:PA230_R3430 | 556 | 644 | 121.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M7TR | 556 | 644 | 121.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_1-56-2 | 556 | 644 | 121.47
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | B:PACKT4 | 556 | 644 | 121.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_6-56-2 | 556 | 644 | 121.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | SB:PA230_R3430 | 556 | 644 | 121.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | SB:PA230_R3430 | 556 | 644 | 121.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:SCRIBA_R230 | 556 | 644 | 121.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:SCRIBA_R925 | 556 | 644 | 121.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:9 MI PT2 | 556 | 644 | 121.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:LADE_3-56-2 | 556 | 644 | 121.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:NOEND | 556 | 644 | 121.39
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - WTRCR 31 345 | 556 | 644 | 121.39
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B3 | 556 | 644 | 121.39
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROSE345_30551 | 556 | 644 | 121.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROSE345_31152 | 556 | 644 | 121.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RMP345_T1500 | 556 | 644 | 121.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON2 | 556 | 644 | 121.33
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | RAMAPO - BRNCHBRG 5018 345 | 556 | 644 | 121.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WATRC345_31-2 | 556 | 644 | 121.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2208 | 556 | 644 | 121.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:RMP345_1500-2X | 556 | 644 | 121.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2214 | 556 | 644 | 121.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS17-20 | 556 | 644 | 121.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2224 | 556 | 644 | 121.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M8TR | 556 | 644 | 121.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M6TR | 556 | 644 | 121.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1724 | 556 | 644 | 121.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1714 | 556 | 644 | 121.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1524 | 556 | 644 | 121.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1514 | 556 | 644 | 121.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE115_1508 | 556 | 644 | 121.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | B:PACKT4 | 556 | 644 | 121.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | SB:PA230_R3430 | 556 | 644 | 121.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2524 | 556 | 644 | 121.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2514 | 556 | 644 | 121.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS21-24 | 556 | 644 | 121.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MOSE230_2508 | 556 | 644 | 121.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | B:PACKT4 | 556 | 644 | 121.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | SB:PA230_R3430 | 556 | 644 | 121.23
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON1 | 556 | 644 | 121.19
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | B:PACKT4 | 556 | 644 | 121.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | SB:PA230_R3430 | 556 | 644 | 121.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3208 | 556 | 644 | 121.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/NWES | 556 | 644 | 121.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SRIPL - ERIE E 69 230 | 556 | 644 | 121.06
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | DUNKIRK - SRIPL 68 230 | 556 | 644 | 121.06
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:SRIPLEY | 556 | 644 | 121.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:AT_R6361 | 556 | 644 | 121.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BESICORP | 556 | 644 | 121.04
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | B:PACKT4 | 556 | 644 | 121.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:EMPIRE | 556 | 644 | 121.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | B:PACKT4 | 556 | 644 | 121.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | S:EMPIRE | 556 | 644 | 120.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | SB:PA230_R3430 | 556 | 644 | 120.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | SB:PA230_R3430 | 556 | 644 | 120.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | SB:PA230_R3430 | 556 | 644 | 120.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | SB:PA230_R3430 | 556 | 644 | 120.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | SB:PA230_R3430 | 556 | 644 | 120.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | SB:PA230_R3430 | 556 | 644 | 120.93
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:72&69 | 556 | 644 | 120.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | SB:PA230_R3430 | 556 | 644 | 120.92
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: IND PT 2 | 556 | 644 | 120.9
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | S:PA_HNTL77 | 556 | 644 | 120.9
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | SB:PA230_R3430 | 556 | 644 | 120.9
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | S:PA_HNTL77 | 556 | 644 | 120.89
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 2TR | S:PA_HNTL77 | 556 | 644 | 120.87
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN GILBOA #3&4 | 556 | 644 | 120.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3302 | 556 | 644 | 120.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | B:PACKT4 | 556 | 644 | 120.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | SB:PA230_R3430 | 556 | 644 | 120.82
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN GILBOA #1&2 | 556 | 644 | 120.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3202 | 556 | 644 | 120.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GILB345_3308 | 556 | 644 | 120.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | BECK - PACKARD BP76 230 | 556 | 644 | 120.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | S:PA_HNTL77 | 556 | 644 | 120.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHN_11 | 556 | 644 | 120.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHN_9 | 556 | 644 | 120.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | S:PA_HNTL77 | 556 | 644 | 120.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | S:PA_HNTL77 | 556 | 644 | 120.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | S:PA_HNTL77 | 556 | 644 | 120.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:NTHF3&4 | 556 | 644 | 120.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHN_7 | 556 | 644 | 120.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | S:PA_HNTL77 | 556 | 644 | 120.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | S:PA_HNTL77 | 556 | 644 | 120.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | B:PACKT4 | 556 | 644 | 120.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | B:PACKT4 | 556 | 644 | 120.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | B:PACKT4 | 556 | 644 | 120.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | B:PACKT4 | 556 | 644 | 120.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | B:PACKT4 | 556 | 644 | 120.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STONYCR - WTHRS 230 | 556 | 644 | 120.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | B:PACKT4 | 556 | 644 | 120.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1302 | 556 | 644 | 120.73
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | B:PACKT4 | 556 | 644 | 120.72
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - FARMVLY | 556 | 644 | 120.71
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: IND PT 3 | 556 | 644 | 120.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | B:PACKT4 | 556 | 644 | 120.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R3430 | 556 | 644 | 120.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | SB:PA230_R506 | 556 | 644 | 120.7
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | SB:PA230_R506 | 556 | 644 | 120.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | SB:PA230_R506 | 556 | 644 | 120.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | SB:PA230_R506 | 556 | 644 | 120.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHS_1 | 556 | 644 | 120.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:BUCHS_3 | 556 | 644 | 120.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | SB:PA230_R506 | 556 | 644 | 120.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | S:PA_HNTL77 | 556 | 644 | 120.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | S:PA_HNTL77 | 556 | 644 | 120.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.6
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | S:PA_HNTL77 | 556 | 644 | 120.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:67&68&BW | 556 | 644 | 120.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R3430 | 556 | 644 | 120.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | B:PACKT4 | 556 | 644 | 120.57
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | SB:PA230_R506 | 556 | 644 | 120.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HILLSIDE 230/115 4TR | 556 | 644 | 120.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:HILLSIDE | 556 | 644 | 120.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HILL_B412 | 556 | 644 | 120.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | S:PA_HNTL77 | 556 | 644 | 120.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | S:PA_HNTL77 | 556 | 644 | 120.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | S:PA_HNTL77 | 556 | 644 | 120.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | S:PA_HNTL77 | 556 | 644 | 120.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 2TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.51
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | B:PACKT4 | 556 | 644 | 120.51
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HUNTLEY - ELM 70 230 | 556 | 644 | 120.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.46
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.46
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | SB:PA230_R3430 | 556 | 644 | 120.44
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:BETHSTM | 556 | 644 | 120.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:SITHE 1 | 556 | 644 | 120.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:SITHE 2 | 556 | 644 | 120.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | S:PA_HNTL77 | 556 | 644 | 120.39
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | T:77&80 | 556 | 644 | 120.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | SB:PA230_R3430 | 556 | 644 | 120.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | SB:PA230_R3430 | 556 | 644 | 120.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | SB:PA230_R506 | 556 | 644 | 120.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | SB:PA230_R506 | 556 | 644 | 120.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | SB:PA230_R506 | 556 | 644 | 120.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | SB:PA230_R506 | 556 | 644 | 120.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HILL_68-B412 | 556 | 644 | 120.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | SB:PA230_R506 | 556 | 644 | 120.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | SB:PA230_R506 | 556 | 644 | 120.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HCWC/NWES | 556 | 644 | 120.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:MBWC/NWES | 556 | 644 | 120.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STNYRDG - HILLSIDE 68B 230 | 556 | 644 | 120.31
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | B:PACKT4 | 556 | 644 | 120.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WTHERS230 | 556 | 644 | 120.31
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:120_130 | 556 | 644 | 120.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:130 | 556 | 644 | 120.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:W97&W98 | 556 | 644 | 120.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WATRC345_30-3142 | 556 | 644 | 120.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | WTRCR - MAINSBRG 30A 345 | 556 | 644 | 120.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL77 | 556 | 644 | 120.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1302 | 556 | 644 | 120.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WATRC345_B1-3042 | 556 | 644 | 120.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL77 | 556 | 644 | 120.27
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-2 345 | SB:PA230_R3430 | 556 | 644 | 120.27
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-1 345 | SB:PA230_R3430 | 556 | 644 | 120.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL77 | 556 | 644 | 120.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | B:PACKT4 | 556 | 644 | 120.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | SB:PA230_R3430 | 556 | 644 | 120.19
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | SB:PA230_R3430 | 556 | 644 | 120.19
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-WC_30&W-F_171 | 556 | 644 | 120.19
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:61&191 | 556 | 644 | 120.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R506 | 556 | 644 | 120.17
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R506 | 556 | 644 | 120.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | B:PACKT4 | 556 | 644 | 120.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R506 | 556 | 644 | 120.13
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 120.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | B:PACKT4 | 556 | 644 | 120.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL - DUNKIRK 73 230 | 556 | 644 | 120.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:DUNKG3 | 556 | 644 | 120.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL - DUNKIRK 74 230 | 556 | 644 | 120.04
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HCMB/NWES | 556 | 644 | 120.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | EDIC - FITZ 345 | SB:PA230_R3430 | 556 | 644 | 120.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-1 345 | B:PACKT4 | 556 | 644 | 120
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-2 345 | B:PACKT4 | 556 | 644 | 120
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 119.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | S:PA_HNTL77 | 556 | 644 | 119.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MAINSBRG - HOMERCITY 30B 345 | 556 | 644 | 119.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:DUNKG4 | 556 | 644 | 119.97
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | SB:PA230_R3430 | 556 | 644 | 119.96
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | T:77&80 | 556 | 644 | 119.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | SB:PA230_R3430 | 556 | 644 | 119.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - PACKARD 62 230 | 556 | 644 | 119.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 119.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R3430 | 556 | 644 | 119.94
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 119.93
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | B:PACKT4 | 556 | 644 | 119.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | B:PACKT4 | 556 | 644 | 119.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - PACKARD 61 230 | 556 | 644 | 119.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-MB_30&W-F_171 | 556 | 644 | 119.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | S:PA_HNTL77 | 556 | 644 | 119.87
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OS - EL - LFYTE 17 345 | SB:PA230_R3430 | 556 | 644 | 119.87
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | SB:PA230_R3430 | 556 | 644 | 119.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | EDIC - FITZ 345 | B:PACKT4 | 556 | 644 | 119.79
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:PA27&BP76 | 556 | 644 | 119.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 1TR | SB:PA230_R3430 | 556 | 644 | 119.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 2TR | SB:PA230_R3430 | 556 | 644 | 119.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 3TR | SB:PA230_R3430 | 556 | 644 | 119.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:62&PA27 | 556 | 644 | 119.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | VOL - MARCY 19 345 | SB:PA230_R3430 | 556 | 644 | 119.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 1TR | SB:PA230_R3430 | 556 | 644 | 119.72
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 2TR | SB:PA230_R3430 | 556 | 644 | 119.72
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | S:PA_HNTL77 | 556 | 644 | 119.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | HUNTLEY - PACKARD 77 230 | 556 | 644 | 119.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | SB:PA230_R506 | 556 | 644 | 119.71
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:KINT_39-B112 | 556 | 644 | 119.64
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OS - EL - LFYTE 17 345 | B:PACKT4 | 556 | 644 | 119.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 3 115 | SB:PA230_R3430 | 556 | 644 | 119.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 10 115 | SB:PA230_R3430 | 556 | 644 | 119.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 11 115 | SB:PA230_R3430 | 556 | 644 | 119.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 5 115 | SB:PA230_R3430 | 556 | 644 | 119.59
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - LM 14 115 | SB:PA230_R3430 | 556 | 644 | 119.59
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | B:PACKT4 | 556 | 644 | 119.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LHH - CLAY 7 115 | SB:PA230_R3430 | 556 | 644 | 119.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - VOL 21 345 | SB:PA230_R3430 | 556 | 644 | 119.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FUL - CLAY 4 115 | SB:PA230_R3430 | 556 | 644 | 119.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - WOOD 17 115 | SB:PA230_R3430 | 556 | 644 | 119.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - VOL 20 345 | SB:PA230_R3430 | 556 | 644 | 119.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA 345/115 1TR | SB:PA230_R3430 | 556 | 644 | 119.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA 345/115 2TR | SB:PA230_R3430 | 556 | 644 | 119.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | SB:PA230_R3430 | 556 | 644 | 119.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 119.56
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - 9MI1 9 345 | SB:PA230_R3430 | 556 | 644 | 119.56
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/WF/NWES | 556 | 644 | 119.56
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:DKSR/WRFL | 556 | 644 | 119.56
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | B:PACKT4 | 556 | 644 | 119.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | B:PACKT4 | 556 | 644 | 119.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:KINT_B1-3812 | 556 | 644 | 119.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - IND 25 345 | SB:PA230_R3430 | 556 | 644 | 119.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/WRFL | 556 | 644 | 119.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | B:PACKT4 | 556 | 644 | 119.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW - VOL 11 345 | SB:PA230_R3430 | 556 | 644 | 119.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW - VOL 12 345 | SB:PA230_R3430 | 556 | 644 | 119.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW 345/115 1TR | SB:PA230_R3430 | 556 | 644 | 119.53
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R3430 | 556 | 644 | 119.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R3430 | 556 | 644 | 119.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 1TR | B:PACKT4 | 556 | 644 | 119.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 2TR | B:PACKT4 | 556 | 644 | 119.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - FITZ 10 345 | SB:PA230_R3430 | 556 | 644 | 119.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 3TR | B:PACKT4 | 556 | 644 | 119.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | EDIC - MRCY ue 1-7 345 | SB:PA230_R3430 | 556 | 644 | 119.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | VOL - MARCY 19 345 | B:PACKT4 | 556 | 644 | 119.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 1TR | B:PACKT4 | 556 | 644 | 119.46
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 2TR | B:PACKT4 | 556 | 644 | 119.46
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:SITHE 1 | SB:PA230_R3430 | 556 | 644 | 119.46
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:SITHE 2 | SB:PA230_R3430 | 556 | 644 | 119.46
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 119.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | S:PA_HNTL77 | 556 | 644 | 119.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | S:PA_HNTL77 | 556 | 644 | 119.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | S:PA_HNTL77 | 556 | 644 | 119.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK_TSA 345 | SB:PA230_R3430 | 556 | 644 | 119.37
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK_TSB 345 | SB:PA230_R3430 | 556 | 644 | 119.37
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | S:PA_HNTL77 | 556 | 644 | 119.37
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 3 115 | B:PACKT4 | 556 | 644 | 119.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 10 115 | B:PACKT4 | 556 | 644 | 119.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 11 115 | B:PACKT4 | 556 | 644 | 119.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | B:PACKT4 | 556 | 644 | 119.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 5 115 | B:PACKT4 | 556 | 644 | 119.33
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - LM 14 115 | B:PACKT4 | 556 | 644 | 119.33
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LHH - CLAY 7 115 | B:PACKT4 | 556 | 644 | 119.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - VOL 21 345 | B:PACKT4 | 556 | 644 | 119.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH 345/115 5TR | SB:PA230_R3430 | 556 | 644 | 119.31
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FUL - CLAY 4 115 | B:PACKT4 | 556 | 644 | 119.31
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - WOOD 17 115 | B:PACKT4 | 556 | 644 | 119.31
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - VOL 20 345 | B:PACKT4 | 556 | 644 | 119.31
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA 345/115 1TR | B:PACKT4 | 556 | 644 | 119.31
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA 345/115 2TR | B:PACKT4 | 556 | 644 | 119.31
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 61 230 | S:PA_HNTL77 | 556 | 644 | 119.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-1 345 | SB:PA230_R3430 | 556 | 644 | 119.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - 9MI1 9 345 | B:PACKT4 | 556 | 644 | 119.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - IND 25 345 | B:PACKT4 | 556 | 644 | 119.29
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | S:PA_HNTL77 | 556 | 644 | 119.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW - VOL 11 345 | B:PACKT4 | 556 | 644 | 119.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW - VOL 12 345 | B:PACKT4 | 556 | 644 | 119.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:PACKT4 | 556 | 644 | 119.27
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW 345/115 1TR | B:PACKT4 | 556 | 644 | 119.27
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | B:PACKT4 | 556 | 644 | 119.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | B:PACKT4 | 556 | 644 | 119.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - FITZ 10 345 | B:PACKT4 | 556 | 644 | 119.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | EDIC - MRCY ue 1-7 345 | B:PACKT4 | 556 | 644 | 119.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:SITHE 1 | B:PACKT4 | 556 | 644 | 119.23
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:SITHE 2 | B:PACKT4 | 556 | 644 | 119.23
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | S:PA_HNTL77 | 556 | 644 | 119.22
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | S:PA_HNTL77 | 556 | 644 | 119.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R955 | 556 | 644 | 119.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:OSWEGO 5 | 556 | 644 | 119.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | SB:PA230_R506 | 556 | 644 | 119.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | SB:PA230_R506 | 556 | 644 | 119.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK_TSA 345 | B:PACKT4 | 556 | 644 | 119.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK_TSB 345 | B:PACKT4 | 556 | 644 | 119.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R965 | 556 | 644 | 119.12
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | S:PA_HNTL77 | 556 | 644 | 119.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 119.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 119.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 119.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH 345/115 5TR | B:PACKT4 | 556 | 644 | 119.08
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | T:77&80 | 556 | 644 | 119.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 119.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:CNDGUA | 556 | 644 | 119.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:MLS3&OMS | 556 | 644 | 119.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:250 | 556 | 644 | 119.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:MILLST3 | 556 | 644 | 119.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MEYER - CANDQUA 60 230 | 556 | 644 | 119
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 61 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 118.98
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | HUNTLEY - PACKARD 77 230 | 556 | 644 | 118.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | T:77&80 | 556 | 644 | 118.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 118.9
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:KINTIGH | 556 | 644 | 118.9
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:FRGT/WRFL | 556 | 644 | 118.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:68&160 | 556 | 644 | 118.87
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 118.85
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R925 | 556 | 644 | 118.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:OSWEGO 6 | 556 | 644 | 118.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 118.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:9MIPT1 | 556 | 644 | 118.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:OSWE_R935 | 556 | 644 | 118.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | S:PA_HNTL77 | 556 | 644 | 118.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | S:PA_HNTL77 | 556 | 644 | 118.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | S:PA_HNTL77 | 556 | 644 | 118.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | S:PA_HNTL77 | 556 | 644 | 118.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | S:PA_HNTL77 | 556 | 644 | 118.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | S:PA_HNTL77 | 556 | 644 | 118.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | SB:PA230_R506 | 556 | 644 | 118.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:FITZPATR | 556 | 644 | 118.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | S:PA_HNTL77 | 556 | 644 | 118.54
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | SB:PA230_R506 | 556 | 644 | 118.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | SB:PA230_R506 | 556 | 644 | 118.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SEABROOK | 556 | 644 | 118.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SEAB&OMS | 556 | 644 | 118.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | SB:PA230_R506 | 556 | 644 | 118.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:73&74 | 556 | 644 | 118.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | SB:PA230_R3430 | 556 | 644 | 118.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 118.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 118.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 118.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 118.46
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 118.46
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 118.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MARC_765_7402 | 556 | 644 | 118.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MSU1_7202>7214>7208>7214 | 556 | 644 | 118.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | SB:PA230_R3430 | 556 | 644 | 118.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | SB:PA230_R506 | 556 | 644 | 118.39
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HQ-NY 765 | 556 | 644 | 118.38
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R3430 | 556 | 644 | 118.38
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | SB:PA230_R3430 | 556 | 644 | 118.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | SB:PA230_R3430 | 556 | 644 | 118.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | B:PACKT4 | 556 | 644 | 118.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | HUNTLEY - PACKARD 77 230 | 556 | 644 | 118.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | B:PACKT4 | 556 | 644 | 118.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | B:PACKT4 | 556 | 644 | 118.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | B:PACKT4 | 556 | 644 | 118.18
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | B:PACKT4 | 556 | 644 | 118.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | S:PA_HNTL77 | 556 | 644 | 118.14
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | SB:PA230_R506 | 556 | 644 | 118.13
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SHLDON - STONYCR 230 | 556 | 644 | 118.08
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | T:77&80 | 556 | 644 | 118.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | SB:PA230_R506 | 556 | 644 | 117.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SANDY_DC | 556 | 644 | 117.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SANDY_DC&OMS | 556 | 644 | 117.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | S:PA_HNTL77 | 556 | 644 | 117.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | SB:PA230_R506 | 556 | 644 | 117.85
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 117.82
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:STONY230 | 556 | 644 | 117.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | SB:PA230_R506 | 556 | 644 | 117.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DUNK230_R1312 | 556 | 644 | 117.71
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | SB:PA230_R506 | 556 | 644 | 117.7
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | SB:PA230_R506 | 556 | 644 | 117.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | SB:PA230_R3430 | 556 | 644 | 117.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | SB:PA230_R506 | 556 | 644 | 117.64
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | SB:PA230_R506 | 556 | 644 | 117.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 117.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | SB:PA230_R3430 | 556 | 644 | 117.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | SB:PA230_R3430 | 556 | 644 | 117.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | SB:PA230_R3430 | 556 | 644 | 117.47
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | SB:PA230_R3430 | 556 | 644 | 117.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | SB:PA230_R3430 | 556 | 644 | 117.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | SB:PA230_R3430 | 556 | 644 | 117.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | SB:PA230_R3430 | 556 | 644 | 117.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | B:PACKT4 | 556 | 644 | 117.37
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | S:PA_HNTL77 | 556 | 644 | 117.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | SB:PA230_R3430 | 556 | 644 | 117.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | SB:PA230_R3430 | 556 | 644 | 117.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | SB:PA230_R3430 | 556 | 644 | 117.33
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | SB:PA230_R3430 | 556 | 644 | 117.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R506 | 556 | 644 | 117.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | SB:PA230_R506 | 556 | 644 | 117.32
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | SB:PA230_R506 | 556 | 644 | 117.32
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | SB:PA230_R506 | 556 | 644 | 117.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | S:PA_HNTL77 | 556 | 644 | 117.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | SB:PA230_R506 | 556 | 644 | 117.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | SB:PA230_R506 | 556 | 644 | 117.31
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL77 | 556 | 644 | 117.29
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | B:PACKT4 | 556 | 644 | 117.29
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | SB:PA230_R506 | 556 | 644 | 117.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | B:PACKT4 | 556 | 644 | 117.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | SB:PA230_R506 | 556 | 644 | 117.27
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:GINNA | 556 | 644 | 117.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | SB:PA230_R3430 | 556 | 644 | 117.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | B:PACKT4 | 556 | 644 | 117.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | B:PACKT4 | 556 | 644 | 117.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | B:PACKT4 | 556 | 644 | 117.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | B:PACKT4 | 556 | 644 | 117.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | B:PACKT4 | 556 | 644 | 117.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R3430 | 556 | 644 | 117.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R3430 | 556 | 644 | 117.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | B:PACKT4 | 556 | 644 | 117.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | B:PACKT4 | 556 | 644 | 117.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | B:PACKT4 | 556 | 644 | 117.11
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | B:PACKT4 | 556 | 644 | 117.11
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | B:Hunt67 | 556 | 644 | 117.11
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R3430 | 556 | 644 | 117.1
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | T:77&80 | 556 | 644 | 117.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 117.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R506 | 556 | 644 | 117.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 116.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | B:PACKT4 | 556 | 644 | 116.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 116.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:62&BP76 | 556 | 644 | 116.93
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1202 | 556 | 644 | 116.91
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | T:77&80 | 556 | 644 | 116.9
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | B:PACKT4 | 556 | 644 | 116.89
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | SB:PA230_R506 | 556 | 644 | 116.89
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1302 | 556 | 644 | 116.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | SB:PA230_R506 | 556 | 644 | 116.87
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | SB:PA230_R506 | 556 | 644 | 116.87
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | B:PACKT4 | 556 | 644 | 116.87
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | SB:PA230_R3430 | 556 | 644 | 116.87
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | B:PACKT4 | 556 | 644 | 116.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | SB:PA230_R506 | 556 | 644 | 116.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | SB:PA230_R3430 | 556 | 644 | 116.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | SB:PA230_R506 | 556 | 644 | 116.82
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | SB:PA230_R3430 | 556 | 644 | 116.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:BRUCE5 | 556 | 644 | 116.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-2 345 | SB:PA230_R506 | 556 | 644 | 116.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-1 345 | SB:PA230_R506 | 556 | 644 | 116.72
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | T:77&80 | 556 | 644 | 116.72
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CANDQUA - STNYRDG 68A 230 | 556 | 644 | 116.71
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | S:AVOCA | 556 | 644 | 116.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R3430 | 556 | 644 | 116.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | B:PACKT4 | 556 | 644 | 116.7
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:STONYRIDGE | 556 | 644 | 116.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MASS_765_7108 | 556 | 644 | 116.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | B:PACKT4 | 556 | 644 | 116.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | S:PA_HNTL77 | 556 | 644 | 116.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 2TR | SB:PA230_R3430 | 556 | 644 | 116.58
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | B:PACKT4 | 556 | 644 | 116.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | SB:PA230_R3430 | 556 | 644 | 116.53
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | B:PACKT4 | 556 | 644 | 116.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | SB:PA230_R506 | 556 | 644 | 116.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | EDIC - FITZ 345 | SB:PA230_R506 | 556 | 644 | 116.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | SB:PA230_R506 | 556 | 644 | 116.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:MASS_765_7102 | 556 | 644 | 116.46
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | T:77&80 | 556 | 644 | 116.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | SB:PA230_R506 | 556 | 644 | 116.42
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R506 | 556 | 644 | 116.42
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OS - EL - LFYTE 17 345 | SB:PA230_R506 | 556 | 644 | 116.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | B:PACKT4 | 556 | 644 | 116.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | WTHRS - MEYER 230 | 556 | 644 | 116.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 1TR | SB:PA230_R506 | 556 | 644 | 116.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 2TR | SB:PA230_R506 | 556 | 644 | 116.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 3TR | SB:PA230_R506 | 556 | 644 | 116.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 116.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 2TR | B:PACKT4 | 556 | 644 | 116.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 1TR | SB:PA230_R506 | 556 | 644 | 116.23
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 2TR | SB:PA230_R506 | 556 | 644 | 116.23
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ERIE E - 4 MILE 230 | 556 | 644 | 116.22
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:MEYER | 556 | 644 | 116.22
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | VOL - MARCY 19 345 | SB:PA230_R506 | 556 | 644 | 116.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 3 115 | SB:PA230_R506 | 556 | 644 | 116.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 10 115 | SB:PA230_R506 | 556 | 644 | 116.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 11 115 | SB:PA230_R506 | 556 | 644 | 116.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | SB:PA230_R506 | 556 | 644 | 116.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 5 115 | SB:PA230_R506 | 556 | 644 | 116.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - LM 14 115 | SB:PA230_R506 | 556 | 644 | 116.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LHH - CLAY 7 115 | SB:PA230_R506 | 556 | 644 | 116.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FUL - CLAY 4 115 | SB:PA230_R506 | 556 | 644 | 116.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - WOOD 17 115 | SB:PA230_R506 | 556 | 644 | 116.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - VOL 21 345 | SB:PA230_R506 | 556 | 644 | 116.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA 345/115 1TR | SB:PA230_R506 | 556 | 644 | 116.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA 345/115 2TR | SB:PA230_R506 | 556 | 644 | 116.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - 9MI1 9 345 | SB:PA230_R506 | 556 | 644 | 116.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - VOL 20 345 | SB:PA230_R506 | 556 | 644 | 116.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - IND 25 345 | SB:PA230_R506 | 556 | 644 | 116.04
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW - VOL 11 345 | SB:PA230_R506 | 556 | 644 | 116.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW - VOL 12 345 | SB:PA230_R506 | 556 | 644 | 116.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | SB:PA230_R3430 | 556 | 644 | 116.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R506 | 556 | 644 | 116.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R506 | 556 | 644 | 116.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OSW 345/115 1TR | SB:PA230_R506 | 556 | 644 | 116.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:SITHE 1 | SB:PA230_R506 | 556 | 644 | 116
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:SITHE 2 | SB:PA230_R506 | 556 | 644 | 116
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SCRIBA - FITZ 10 345 | SB:PA230_R506 | 556 | 644 | 116
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:PA230_R506 | 556 | 644 | 115.99
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:OSWEGO 5 | SB:PA230_R506 | 556 | 644 | 115.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | T:77&80 | 556 | 644 | 115.97
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH 345/115 5TR | SB:PA230_R506 | 556 | 644 | 115.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | SB:PA230_R3430 | 556 | 644 | 115.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | T:77&80 | 556 | 644 | 115.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | T:77&80 | 556 | 644 | 115.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | B:PACKT4 | 556 | 644 | 115.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | B:Hunt67 | 556 | 644 | 115.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:DARLIN1 | 556 | 644 | 115.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | T:77&80 | 556 | 644 | 115.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | T:77&80 | 556 | 644 | 115.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1202 | 556 | 644 | 115.62
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | T:77&80 | 556 | 644 | 115.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | T:77&80 | 556 | 644 | 115.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | SB:PA230_R3430 | 556 | 644 | 115.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | SB:PA230_R3430 | 556 | 644 | 115.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | SB:PA230_R3430 | 556 | 644 | 115.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | B:PACKT4 | 556 | 644 | 115.56
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | SB:PA230_R3430 | 556 | 644 | 115.56
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | SB:PA230_R3430 | 556 | 644 | 115.56
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | T:77&80 | 556 | 644 | 115.56
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | SB:PA230_R3430 | 556 | 644 | 115.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:SCRIBA_R230 | 556 | 644 | 115.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:9 MI PT2 | 556 | 644 | 115.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:SCRIBA_R925 | 556 | 644 | 115.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | SB:PA230_R3430 | 556 | 644 | 115.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | B:PACKT4 | 556 | 644 | 115.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | B:PACKT4 | 556 | 644 | 115.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | B:PACKT4 | 556 | 644 | 115.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | B:PACKT4 | 556 | 644 | 115.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | B:PACKT4 | 556 | 644 | 115.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | B:PACKT4 | 556 | 644 | 115.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | T:77&80 | 556 | 644 | 115.29
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | SB:PA230_R506 | 556 | 644 | 115.17
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | T:77&80 | 556 | 644 | 115.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | B:PACKT4 | 556 | 644 | 115.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | SB:PA230_R506 | 556 | 644 | 115.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:77&80 | 556 | 644 | 115.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | SB:PA230_R3430 | 556 | 644 | 115.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/NWES | 556 | 644 | 115.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | DUNKIRK - SRIPL 68 230 | 556 | 644 | 115.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:SRIPLEY | 556 | 644 | 115.02
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R506 | 556 | 644 | 115.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SRIPL - ERIE E 69 230 | 556 | 644 | 115.01
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | SB:PA230_R506 | 556 | 644 | 115
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | SB:PA230_R506 | 556 | 644 | 115
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | T:77&80 | 556 | 644 | 114.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1302 | 556 | 644 | 114.91
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | S:PA_HNTL77 | 556 | 644 | 114.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1302 | 556 | 644 | 114.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | B:PACKT4 | 556 | 644 | 114.85
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | S:PA_HNTL77 | 556 | 644 | 114.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | S:PA_HNTL77 | 556 | 644 | 114.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | T:77&80 | 556 | 644 | 114.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - ELM 71 230 | T:77&80 | 556 | 644 | 114.76
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | S:PA_HNTL77 | 556 | 644 | 114.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | S:PA_HNTL77 | 556 | 644 | 114.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | SB:PA230_R3430 | 556 | 644 | 114.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STONYCR - WTHRS 230 | 556 | 644 | 114.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 114.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | B:PACKT4 | 556 | 644 | 114.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 114.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 114.46
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | HUNTLEY - PACKARD 77 230 | 556 | 644 | 114.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | HUNTLEY - PACKARD 77 230 | 556 | 644 | 114.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | B:Hunt67 | 556 | 644 | 114.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | SB:PA230_R3430 | 556 | 644 | 114.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | SB:PA230_R3430 | 556 | 644 | 114.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | SB:PA230_R3430 | 556 | 644 | 114.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:WTHERS230 | 556 | 644 | 114.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1202 | 556 | 644 | 114.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R3430 | 556 | 644 | 114.22
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | SB:PA230_R506 | 556 | 644 | 114.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | SB:PA230_R506 | 556 | 644 | 114.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | SB:PA230_R506 | 556 | 644 | 114.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | B:PACKT4 | 556 | 644 | 114.11
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | B:PACKT4 | 556 | 644 | 114.08
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1302 | 556 | 644 | 114.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | B:PACKT4 | 556 | 644 | 114.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | SB:PA230_R506 | 556 | 644 | 114.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | SB:PA230_R506 | 556 | 644 | 114.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:DUNKG4 | 556 | 644 | 114
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | S:PA_HNTL77 | 556 | 644 | 113.99
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | B:PACKT4 | 556 | 644 | 113.94
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | SB:PA230_R506 | 556 | 644 | 113.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | SB:PA230_R506 | 556 | 644 | 113.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | SB:PA230_R506 | 556 | 644 | 113.87
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | SB:PA230_R506 | 556 | 644 | 113.87
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | SB:PA230_R506 | 556 | 644 | 113.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | SB:PA230_R506 | 556 | 644 | 113.85
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | SB:PA230_R506 | 556 | 644 | 113.85
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | SB:PA230_R506 | 556 | 644 | 113.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | SB:HUNT230_R1302 | 556 | 644 | 113.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R506 | 556 | 644 | 113.76
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | HUNTLEY - PACKARD 77 230 | 556 | 644 | 113.71
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R506 | 556 | 644 | 113.7
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R506 | 556 | 644 | 113.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | SB:PA230_R506 | 556 | 644 | 113.56
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | SB:PA230_R506 | 556 | 644 | 113.53
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:DKSR/WRFL | 556 | 644 | 113.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/WF/NWES | 556 | 644 | 113.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/WRFL | 556 | 644 | 113.46
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R506 | 556 | 644 | 113.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | SB:PA230_R506 | 556 | 644 | 113.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | S:PA_HNTL77 | 556 | 644 | 113.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | S:PA_HNTL77 | 556 | 644 | 113.19
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | SB:PA230_R506 | 556 | 644 | 113.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 2TR | SB:PA230_R506 | 556 | 644 | 113.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | S:PA_HNTL77 | 556 | 644 | 113.08
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_R833 | 556 | 644 | 112.98
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | T:77&80 | 556 | 644 | 112.96
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_NEW | 556 | 644 | 112.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | T:77&80 | 556 | 644 | 112.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | HUNTLEY - PACKARD 77 230 | 556 | 644 | 112.93
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:GARD72&79 | 556 | 644 | 112.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | T:77&80 | 556 | 644 | 112.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | T:77&80 | 556 | 644 | 112.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | T:77&80 | 556 | 644 | 112.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | T:77&80 | 556 | 644 | 112.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | T:77&80 | 556 | 644 | 112.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | T:77&80 | 556 | 644 | 112.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 112.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:KINTIGH | 556 | 644 | 112.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:68&160 | 556 | 644 | 112.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | T:77&80 | 556 | 644 | 112.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | SB:HUNT230_R1302 | 556 | 644 | 112.79
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 112.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | T:77&80 | 556 | 644 | 112.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | T:77&80 | 556 | 644 | 112.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_R823 | 556 | 644 | 112.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | T:77&80 | 556 | 644 | 112.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1302 | 556 | 644 | 112.69
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | S:PA_HNTL77 | 556 | 644 | 112.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | SB:PA230_R506 | 556 | 644 | 112.66
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:73&74 | 556 | 644 | 112.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | T:77&80 | 556 | 644 | 112.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | T:77&80 | 556 | 644 | 112.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | T:77&80 | 556 | 644 | 112.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | T:77&80 | 556 | 644 | 112.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1202 | 556 | 644 | 112.23
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | S:HNT_GRD80 | 556 | 644 | 112.22
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HUNTLEY - GARDENVILL 79 230 | 556 | 644 | 112.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | T:77&80 | 556 | 644 | 112.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 112.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 79 230 | S:PA_HNTL77 | 556 | 644 | 112.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HUNTLEY - GARDENVILL 80 230 | 556 | 644 | 112.14
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 112.13
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | SB:PA230_R506 | 556 | 644 | 112.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | SB:PA230_R506 | 556 | 644 | 112.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | SB:PA230_R506 | 556 | 644 | 112.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | SB:PA230_R506 | 556 | 644 | 112.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | SB:PA230_R506 | 556 | 644 | 112.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | SB:PA230_R506 | 556 | 644 | 112.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | SB:PA230_R506 | 556 | 644 | 112.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | T:77&80 | 556 | 644 | 111.99
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | SB:PA230_R506 | 556 | 644 | 111.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_NEW | 556 | 644 | 111.87
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1302 | 556 | 644 | 111.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:DUNK230_R1312 | 556 | 644 | 111.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | SB:PA230_R3430 | 556 | 644 | 111.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | SB:PA230_R3430 | 556 | 644 | 111.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | T:77&80 | 556 | 644 | 111.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | T:77&80 | 556 | 644 | 111.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | T:77&80 | 556 | 644 | 111.73
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | SB:HUNT230_R1302 | 556 | 644 | 111.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | T:77&80 | 556 | 644 | 111.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R3430 | 556 | 644 | 111.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | T:77&80 | 556 | 644 | 111.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | SB:PA230_R3430 | 556 | 644 | 111.6
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | SB:PA230_R3430 | 556 | 644 | 111.6
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | SB:PA230_R506 | 556 | 644 | 111.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | T:77&80 | 556 | 644 | 111.53
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | B:PACKT4 | 556 | 644 | 111.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | T:77&80 | 556 | 644 | 111.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | B:PACKT4 | 556 | 644 | 111.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | T:77&80 | 556 | 644 | 111.44
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | T:77&80 | 556 | 644 | 111.44
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | B:PACKT4 | 556 | 644 | 111.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | B:PACKT4 | 556 | 644 | 111.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | B:PACKT4 | 556 | 644 | 111.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | SB:HUNT230_R1302 | 556 | 644 | 111.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | T:77&80 | 556 | 644 | 111.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | T:77&80 | 556 | 644 | 111.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | T:77&80 | 556 | 644 | 111.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | T:77&80 | 556 | 644 | 111.34
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | T:77&80 | 556 | 644 | 111.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 61 230 | T:77&80 | 556 | 644 | 111.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | SB:PA230_R506 | 556 | 644 | 111.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | T:77&80 | 556 | 644 | 111.19
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | T:77&80 | 556 | 644 | 111.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | T:77&80 | 556 | 644 | 111.18
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | T:77&80 | 556 | 644 | 111.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | SB:PA230_R506 | 556 | 644 | 111.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | B:Hunt67 | 556 | 644 | 111.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1302 | 556 | 644 | 111.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:Hunt67 | 556 | 644 | 111.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1302 | 556 | 644 | 111.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | SB:PA230_R506 | 556 | 644 | 111.09
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | T:77&80 | 556 | 644 | 111.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | T:77&80 | 556 | 644 | 111.03
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R3430 | 556 | 644 | 110.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | SB:HUNT230_R1302 | 556 | 644 | 110.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1202 | 556 | 644 | 110.94
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R506 | 556 | 644 | 110.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | T:77&80 | 556 | 644 | 110.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | T:77&80 | 556 | 644 | 110.83
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:GARD73&80 | 556 | 644 | 110.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | B:Hunt67 | 556 | 644 | 110.79
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-1 345 | T:77&80 | 556 | 644 | 110.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-2 345 | T:77&80 | 556 | 644 | 110.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | SB:PA230_R3430 | 556 | 644 | 110.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | S:PA_HNTL77 | 556 | 644 | 110.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:BRUCE5 | 556 | 644 | 110.73
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | T:77&80 | 556 | 644 | 110.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1202 | 556 | 644 | 110.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | SB:HUNT230_R1302 | 556 | 644 | 110.58
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | T:77&80 | 556 | 644 | 110.58
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | T:77&80 | 556 | 644 | 110.58
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | T:77&80 | 556 | 644 | 110.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | EDIC - FITZ 345 | T:77&80 | 556 | 644 | 110.56
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | B:PACKT4 | 556 | 644 | 110.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | B:PACKT4 | 556 | 644 | 110.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | T:77&80 | 556 | 644 | 110.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R3430 | 556 | 644 | 110.44
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OS - EL - LFYTE 17 345 | T:77&80 | 556 | 644 | 110.42
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | B:Hunt67 | 556 | 644 | 110.37
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | SB:HUNT230_R1302 | 556 | 644 | 110.37
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | SB:HUNT230_R1302 | 556 | 644 | 110.37
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 110.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | T:77&80 | 556 | 644 | 110.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | T:77&80 | 556 | 644 | 110.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_NEW | 556 | 644 | 110.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 1TR | T:77&80 | 556 | 644 | 110.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 2TR | T:77&80 | 556 | 644 | 110.34
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_R873 | 556 | 644 | 110.34
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | T:77&80 | 556 | 644 | 110.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 3TR | T:77&80 | 556 | 644 | 110.33
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | WTHRS - MEYER 230 | 556 | 644 | 110.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | VOL - MARCY 19 345 | T:77&80 | 556 | 644 | 110.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 1TR | T:77&80 | 556 | 644 | 110.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 2TR | T:77&80 | 556 | 644 | 110.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | T:77&80 | 556 | 644 | 110.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | T:77&80 | 556 | 644 | 110.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | T:77&80 | 556 | 644 | 110.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1302 | 556 | 644 | 110.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:MEYER | 556 | 644 | 110.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1202 | 556 | 644 | 110.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 79 230 | B:PACKT4 | 556 | 644 | 110.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | T:77&80 | 556 | 644 | 110.17
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | SB:HUNT230_R1302 | 556 | 644 | 110.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | T:77&80 | 556 | 644 | 110.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | SB:PA230_R3430 | 556 | 644 | 110.13
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | SB:PA230_R3430 | 556 | 644 | 110.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R3430 | 556 | 644 | 109.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | SB:HUNT230_R1302 | 556 | 644 | 109.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | B:PACKT4 | 556 | 644 | 109.93
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | B:PACKT4 | 556 | 644 | 109.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | SB:HUNT230_R1302 | 556 | 644 | 109.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | SB:HUNT230_R1302 | 556 | 644 | 109.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | SB:HUNT230_R1302 | 556 | 644 | 109.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | SB:HUNT230_R1302 | 556 | 644 | 109.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | T:77&80 | 556 | 644 | 109.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | B:PACKT4 | 556 | 644 | 109.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:DARLIN1 | 556 | 644 | 109.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | SB:HUNT230_R1302 | 556 | 644 | 109.51
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | SB:HUNT230_R1302 | 556 | 644 | 109.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | SB:HUNT230_R1302 | 556 | 644 | 109.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | SB:HUNT230_R1302 | 556 | 644 | 109.45
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | B:Hunt67 | 556 | 644 | 109.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | B:Hunt67 | 556 | 644 | 109.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1202 | 556 | 644 | 108.98
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1202 | 556 | 644 | 108.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_R833 | 556 | 644 | 108.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_R823 | 556 | 644 | 108.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | SB:PA230_R506 | 556 | 644 | 108.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | T:77&80 | 556 | 644 | 108.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | SB:PA230_R506 | 556 | 644 | 108.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | T:77&80 | 556 | 644 | 108.53
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | T:77&80 | 556 | 644 | 108.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | T:77&80 | 556 | 644 | 108.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | T:77&80 | 556 | 644 | 108.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R506 | 556 | 644 | 108.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | SB:PA230_R506 | 556 | 644 | 108.37
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | SB:PA230_R506 | 556 | 644 | 108.37
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | T:77&80 | 556 | 644 | 108.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | T:77&80 | 556 | 644 | 108.31
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | T:77&80 | 556 | 644 | 108.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | T:77&80 | 556 | 644 | 108.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | T:77&80 | 556 | 644 | 108.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:GARD72&79 | 556 | 644 | 108.15
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | T:77&80 | 556 | 644 | 107.91
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R506 | 556 | 644 | 107.89
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1302 | 556 | 644 | 107.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | S:PA_HNTL77 | 556 | 644 | 107.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | SB:PA230_R3430 | 556 | 644 | 107.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | T:77&80 | 556 | 644 | 107.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | SB:HUNT230_R1302 | 556 | 644 | 107.71
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | T:77&80 | 556 | 644 | 107.69
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | SB:HUNT230_R1302 | 556 | 644 | 107.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | SB:HUNT230_R1302 | 556 | 644 | 107.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | T:77&80 | 556 | 644 | 107.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | SB:PA230_R506 | 556 | 644 | 107.61
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | SB:HUNT230_R1302 | 556 | 644 | 107.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | SB:HUNT230_R1302 | 556 | 644 | 107.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | SB:HUNT230_R1302 | 556 | 644 | 107.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | SB:HUNT230_R1302 | 556 | 644 | 107.6
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 61 230 | T:77&80 | 556 | 644 | 107.57
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R506 | 556 | 644 | 107.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | B:PACKT4 | 556 | 644 | 107.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | SB:HUNT230_R1302 | 556 | 644 | 107.46
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | SB:HUNT230_R1302 | 556 | 644 | 107.45
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | SB:HUNT230_R1302 | 556 | 644 | 107.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1202 | 556 | 644 | 107.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | S:HNT_GRD80 | 556 | 644 | 107.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | T:77&80 | 556 | 644 | 107.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | T:77&80 | 556 | 644 | 107.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | T:77&80 | 556 | 644 | 107.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HUNTLEY - GARDENVILL 79 230 | 556 | 644 | 107.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 107.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 79 230 | S:PA_HNTL77 | 556 | 644 | 107.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HUNTLEY - GARDENVILL 80 230 | 556 | 644 | 107.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - PACKARD 77 230 | 556 | 644 | 107.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_NEW | 556 | 644 | 107.22
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | T:77&80 | 556 | 644 | 107.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | SB:HUNT230_R1302 | 556 | 644 | 107.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | SB:HUNT230_R1302 | 556 | 644 | 107.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | SB:HUNT230_R1302 | 556 | 644 | 107.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | T:77&80 | 556 | 644 | 107.11
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1302 | 556 | 644 | 107.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | T:77&80 | 556 | 644 | 106.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | T:77&80 | 556 | 644 | 106.97
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | SB:PA230_R506 | 556 | 644 | 106.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | SB:PA230_R506 | 556 | 644 | 106.93
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | T:77&80 | 556 | 644 | 106.92
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | T:77&80 | 556 | 644 | 106.92
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | T:77&80 | 556 | 644 | 106.92
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | T:77&80 | 556 | 644 | 106.91
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | T:77&80 | 556 | 644 | 106.91
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | T:77&80 | 556 | 644 | 106.91
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | T:77&80 | 556 | 644 | 106.9
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | SB:HUNT230_R1302 | 556 | 644 | 106.9
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | SB:HUNT230_NEW | 556 | 644 | 106.9
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_NEW | 556 | 644 | 106.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R506 | 556 | 644 | 106.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | SB:HUNT230_R1302 | 556 | 644 | 106.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_NEW | 556 | 644 | 106.71
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | T:77&80 | 556 | 644 | 106.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | T:77&80 | 556 | 644 | 106.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | SB:HUNT230_R1302 | 556 | 644 | 106.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | SB:HUNT230_R1302 | 556 | 644 | 106.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | SB:HUNT230_R1302 | 556 | 644 | 106.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | SB:HUNT230_R1302 | 556 | 644 | 106.39
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | SB:HUNT230_R1302 | 556 | 644 | 106.38
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 61 230 | SB:HUNT230_R1302 | 556 | 644 | 106.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | T:77&80 | 556 | 644 | 106.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:Hunt67 | 556 | 644 | 106.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1302 | 556 | 644 | 106.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | SB:HUNT230_R1302 | 556 | 644 | 106.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | SB:HUNT230_R1302 | 556 | 644 | 106.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | B:Hunt67 | 556 | 644 | 106.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | SB:HUNT230_R1302 | 556 | 644 | 106
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | T:77&80 | 556 | 644 | 105.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | SB:HUNT230_R1302 | 556 | 644 | 105.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:GARD73&80 | 556 | 644 | 105.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | SB:HUNT230_R1302 | 556 | 644 | 105.94
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | T:77&80 | 556 | 644 | 105.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1202 | 556 | 644 | 105.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | SB:HUNT230_R1302 | 556 | 644 | 105.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | SB:HUNT230_R1302 | 556 | 644 | 105.71
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | SB:HUNT230_R1302 | 556 | 644 | 105.71
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | SB:HUNT230_R1302 | 556 | 644 | 105.71
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R3430 | 556 | 644 | 105.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_R873 | 556 | 644 | 105.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | SB:HUNT230_R1302 | 556 | 644 | 105.54
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | SB:HUNT230_R1302 | 556 | 644 | 105.45
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | T:77&80 | 556 | 644 | 105.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | SB:HUNT230_R1302 | 556 | 644 | 105.42
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | SB:HUNT230_R1302 | 556 | 644 | 105.4
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | SB:HUNT230_R1302 | 556 | 644 | 105.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | SB:HUNT230_R1302 | 556 | 644 | 105.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_NEW | 556 | 644 | 105.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-1 345 | SB:HUNT230_R1302 | 556 | 644 | 105.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL - CLAY PC-2 345 | SB:HUNT230_R1302 | 556 | 644 | 105.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | SB:HUNT230_R1302 | 556 | 644 | 105.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | SB:HUNT230_R1302 | 556 | 644 | 105.19
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | SB:HUNT230_R1302 | 556 | 644 | 105.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | SB:HUNT230_R1302 | 556 | 644 | 105.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | B:PACKT4 | 556 | 644 | 105.11
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | EDIC - FITZ 345 | SB:HUNT230_R1302 | 556 | 644 | 105.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R3430 | 556 | 644 | 105.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | SB:HUNT230_R1302 | 556 | 644 | 104.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | SB:HUNT230_R1302 | 556 | 644 | 104.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | SB:HUNT230_R1302 | 556 | 644 | 104.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | SB:HUNT230_R1302 | 556 | 644 | 104.98
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | SB:HUNT230_R1302 | 556 | 644 | 104.98
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | SB:HUNT230_R1302 | 556 | 644 | 104.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_NEW | 556 | 644 | 104.96
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | SB:HUNT230_R1302 | 556 | 644 | 104.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OS - EL - LFYTE 17 345 | SB:HUNT230_R1302 | 556 | 644 | 104.92
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 1TR | SB:HUNT230_R1302 | 556 | 644 | 104.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 2TR | SB:HUNT230_R1302 | 556 | 644 | 104.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PANL 345/115 3TR | SB:HUNT230_R1302 | 556 | 644 | 104.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | VOL - MARCY 19 345 | SB:HUNT230_R1302 | 556 | 644 | 104.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 1TR | SB:HUNT230_R1302 | 556 | 644 | 104.79
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY 345/115 2TR | SB:HUNT230_R1302 | 556 | 644 | 104.79
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 79 230 | B:PACKT4 | 556 | 644 | 104.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | SB:PA230_R506 | 556 | 644 | 104.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 3 115 | SB:HUNT230_R1302 | 556 | 644 | 104.7
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 11 115 | SB:HUNT230_R1302 | 556 | 644 | 104.7
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - TEAL 10 115 | SB:HUNT230_R1302 | 556 | 644 | 104.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 5 115 | SB:HUNT230_R1302 | 556 | 644 | 104.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - LM 14 115 | SB:HUNT230_R1302 | 556 | 644 | 104.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | SB:HUNT230_R1302 | 556 | 644 | 104.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | SB:HUNT230_R1302 | 556 | 644 | 104.67
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | SB:HUNT230_R1302 | 556 | 644 | 104.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | SB:HUNT230_R1302 | 556 | 644 | 104.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | B:Hunt67 | 556 | 644 | 104.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | T:77&80 | 556 | 644 | 104.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1202 | 556 | 644 | 104.19
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | B:Hunt67 | 556 | 644 | 103.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | T:77&80 | 556 | 644 | 103.94
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | T:77&80 | 556 | 644 | 103.93
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | T:77&80 | 556 | 644 | 103.92
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | T:77&80 | 556 | 644 | 103.92
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1202 | 556 | 644 | 103.79
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | B:Hunt67 | 556 | 644 | 103.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1202 | 556 | 644 | 103.45
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | B:Hunt67 | 556 | 644 | 103.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | SB:HUNT230_R1202 | 556 | 644 | 103.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | SB:HUNT230_R1302 | 556 | 644 | 103.1
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | SB:HUNT230_R1302 | 556 | 644 | 102.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | SB:HUNT230_R1302 | 556 | 644 | 102.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | SB:HUNT230_R1302 | 556 | 644 | 102.95
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | SB:HUNT230_R1302 | 556 | 644 | 102.94
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | SB:HUNT230_R1302 | 556 | 644 | 102.9
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | T:77&80 | 556 | 644 | 102.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | SB:HUNT230_R1302 | 556 | 644 | 102.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | SB:HUNT230_R1302 | 556 | 644 | 102.83
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | SB:HUNT230_R1302 | 556 | 644 | 102.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | T:77&80 | 556 | 644 | 102.76
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | SB:HUNT230_R1302 | 556 | 644 | 102.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | SB:HUNT230_R1302 | 556 | 644 | 102.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | SB:HUNT230_R1302 | 556 | 644 | 102.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | SB:HUNT230_R1302 | 556 | 644 | 102.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | SB:HUNT230_R1302 | 556 | 644 | 102.67
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | SB:HUNT230_R1302 | 556 | 644 | 102.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | T:77&80 | 556 | 644 | 102.64
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | SB:HUNT230_R1302 | 556 | 644 | 102.64
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | SB:HUNT230_R1302 | 556 | 644 | 102.64
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | T:77&80 | 556 | 644 | 102.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R506 | 556 | 644 | 102.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_NEW | 556 | 644 | 102.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | B:Hunt67 | 556 | 644 | 102.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R506 | 556 | 644 | 102.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | SB:HUNT230_R1202 | 556 | 644 | 102.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | SB:HUNT230_R1302 | 556 | 644 | 102.09
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | SB:HUNT230_R1302 | 556 | 644 | 102.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | SB:HUNT230_R1302 | 556 | 644 | 102.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 61 230 | SB:HUNT230_R1302 | 556 | 644 | 101.97
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | SB:HUNT230_NEW | 556 | 644 | 101.89
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1202 | 556 | 644 | 101.73
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - GARDENVILL 80 230 | B:Hunt67 | 556 | 644 | 101.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | SB:HUNT230_R1302 | 556 | 644 | 101.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | SB:HUNT230_R1302 | 556 | 644 | 101.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | SB:HUNT230_R1302 | 556 | 644 | 101.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | SB:HUNT230_R1302 | 556 | 644 | 101.62
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | SB:HUNT230_R1302 | 556 | 644 | 101.57
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | SB:HUNT230_R1302 | 556 | 644 | 101.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | B:Hunt67 | 556 | 644 | 101.42
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | SB:HUNT230_R1302 | 556 | 644 | 101.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | B:Hunt67 | 556 | 644 | 101.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | T:77&80 | 556 | 644 | 101.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | SB:HUNT230_R1302 | 556 | 644 | 101.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1202 | 556 | 644 | 101.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | SB:HUNT230_R1202 | 556 | 644 | 101.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | SB:HUNT230_R1302 | 556 | 644 | 101.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | SB:HUNT230_R1302 | 556 | 644 | 101.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | SB:HUNT230_R1302 | 556 | 644 | 101.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | SB:HUNT230_R1302 | 556 | 644 | 101.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | SB:HUNT230_R1302 | 556 | 644 | 101.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | SB:HUNT230_R1302 | 556 | 644 | 101.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | B:Hunt67 | 556 | 644 | 101.13
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | SB:HUNT230_R1302 | 556 | 644 | 101.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | SB:HUNT230_R1202 | 556 | 644 | 100.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | SB:HUNT230_R1302 | 556 | 644 | 100.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | B:Hunt67 | 556 | 644 | 100.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | B:Hunt67 | 556 | 644 | 100.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | SB:HUNT230_R1202 | 556 | 644 | 100.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | SB:HUNT230_R1302 | 556 | 644 | 100.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | SB:HUNT230_R1302 | 556 | 644 | 100.53
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1202 | 556 | 644 | 100.47
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | B:Hunt67 | 556 | 644 | 100.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | SB:HUNT230_R1202 | 556 | 644 | 100.22
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_NEW | 556 | 644 | 100.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | SB:HUNT230_R1302 | 556 | 644 | 100.13
| 135304 SAWYER78 230 135415 PACKARD2 230 2 Max |  |  |  |  | 150.14
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:ROBI230 | 566 | 654 | 113.65
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 112.57
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | NIAGARA - ROBINSON 64 230 | 566 | 654 | 112.41
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | B:STOLE230 | 566 | 654 | 111.98
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 111.06
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 110.35
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | T:61&64 | 566 | 654 | 109.74
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 109.66
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 109.45
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:GARD230_T7-12 | 566 | 654 | 108.29
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:ROBI230 | 566 | 654 | 107.44
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | B:GARD72&79 | 566 | 654 | 107.25
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 106.88
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | B:STOLE230 | 566 | 654 | 106.13
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 105.8
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | NIAGARA - ROBINSON 64 230 | 566 | 654 | 105.69
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 105.25
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:255_345B302 | 566 | 654 | 105.17
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:NIAG345_3108 | 566 | 654 | 105.11
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | NIAG - NEWROCH 1 345 | 566 | 654 | 105.06
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | B:GARD72&79 | 566 | 654 | 104.96
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 104.75
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 104.55
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | B:GARD72&79 | 566 | 654 | 104.14
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 104
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | SB:GARD230_R823 | 566 | 654 | 103.91
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:255_345B202 | 566 | 654 | 103.87
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | SOMERSET - NEWROCH 1 345 | 566 | 654 | 103.8
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 103.79
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | T:61&64 | 566 | 654 | 103.49
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1502 | 566 | 654 | 103.01
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:GARD230_T7-12 | 566 | 654 | 102.79
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | T:78&79 | 566 | 654 | 102.52
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:GARD230_R823 | 566 | 654 | 102.1
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1502 | 566 | 654 | 102.05
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | B:GARD72&79 | 566 | 654 | 101.76
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | T:78&79 | 566 | 654 | 101.59
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 101.46
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:GARD230_R823 | 566 | 654 | 101.43
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:GARD230_R823 | 566 | 654 | 101.35
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | T:40&41 | 566 | 654 | 101.32
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - ELM 70 230 | 566 | 654 | 101.09
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | B:GARD72&79 | 566 | 654 | 100.66
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1502 | 566 | 654 | 100.52
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | FARMVLY - HOMERCTY | 566 | 654 | 100.31
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - ELM 70 230 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 100.25
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | R:HC-FV_37&W-F_171 | 566 | 654 | 100.19
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | T:41&33 | 566 | 654 | 100.16
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:NIAW230_2014 | 566 | 654 | 100.08
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | T:78&79 | 566 | 654 | 100.05
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 100.05
| 135305 SAWYER80 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 113.65
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:ROBI230 | 566 | 654 | 105.27
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 104.22
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | HUNTLEY - GARDENVILL 79 230 | NIAGARA - ROBINSON 64 230 | 566 | 654 | 104.05
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | HUNTLEY - GARDENVILL 79 230 | B:STOLE230 | 566 | 654 | 103.62
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | HUNTLEY - GARDENVILL 79 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 102.71
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 102
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | HUNTLEY - GARDENVILL 79 230 | T:61&64 | 566 | 654 | 101.38
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | HUNTLEY - GARDENVILL 79 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 101.27
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 101.06
| 135305 SAWYER80 230 135419 SUNY-80 230 1 Max |  |  |  |  | 105.27
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:ROBI230 | 566 | 654 | 105.49
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | S:HNT_GRD80 | 566 | 654 | 104.47
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - GARDENVILL 80 230 | 566 | 654 | 104.45
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 80 230 | NIAGARA - ROBINSON 64 230 | 566 | 654 | 104.27
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 80 230 | B:STOLE230 | 566 | 654 | 103.82
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 80 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 102.92
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | S:HNT_GRD80 | 566 | 654 | 102.24
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | SB:GARD230_R873 | 566 | 654 | 102.22
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - GARDENVILL 80 230 | 566 | 654 | 102.22
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 80 230 | T:61&64 | 566 | 654 | 101.61
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 80 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 101.49
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | S:HNT_GRD80 | 566 | 654 | 101.31
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - GARDENVILL 80 230 | 566 | 654 | 101.29
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_T7-12 | 566 | 654 | 100.09
| 135306 SAWYER79 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 105.49
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:ROBI230 | 566 | 654 | 105.49
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | NIAGARA - ROBINSON 64 230 | S:HNT_GRD80 | 566 | 654 | 104.47
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - GARDENVILL 80 230 | 566 | 654 | 104.45
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | HUNTLEY - GARDENVILL 80 230 | NIAGARA - ROBINSON 64 230 | 566 | 654 | 104.27
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | HUNTLEY - GARDENVILL 80 230 | B:STOLE230 | 566 | 654 | 103.82
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | HUNTLEY - GARDENVILL 80 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 102.92
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | STOLLRD - GARDENVILL 66 230 | S:HNT_GRD80 | 566 | 654 | 102.24
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | NIAGARA - ROBINSON 64 230 | SB:GARD230_R873 | 566 | 654 | 102.22
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - GARDENVILL 80 230 | 566 | 654 | 102.21
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | HUNTLEY - GARDENVILL 80 230 | T:61&64 | 566 | 654 | 101.61
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | HUNTLEY - GARDENVILL 80 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 101.49
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | ROBINSON - STOLLRD 65 230 | S:HNT_GRD80 | 566 | 654 | 101.31
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - GARDENVILL 80 230 | 566 | 654 | 101.29
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_T7-12 | 566 | 654 | 100.09
| 135306 SAWYER79 230 135418 SUNY-79 230 1 Max |  |  |  |  | 105.49
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 106.87
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 104.64
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 226 | 100.54
| 135383 S219-182 115 135496 YNG-182 115 1 Max |  |  |  |  | 106.87
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 206 | 116.22
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 206 | 113.78
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 206 | 109.51
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 206 | 105.27
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 168 | 206 | 100.99
| 135383 S219-182 115 135505 WALDENTP 115 1 Max |  |  |  |  | 116.22
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:ROBI230 | 566 | 654 | 102.26
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | NIAGARA - ROBINSON 64 230 | S:HNT_GRD80 | 566 | 654 | 101.25
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - GARDENVILL 80 230 | 566 | 654 | 101.24
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | HUNTLEY - GARDENVILL 80 230 | NIAGARA - ROBINSON 64 230 | 566 | 654 | 101.06
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | HUNTLEY - GARDENVILL 80 230 | B:STOLE230 | 566 | 654 | 100.6
| 135413 GRDNVL2 230 135418 SUNY-79 230 1 Max |  |  |  |  | 102.26
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:ROBI230 | 566 | 654 | 102.05
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | NIAGARA - ROBINSON 64 230 | B:GARD72&79 | 566 | 654 | 101.33
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 101
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | HUNTLEY - GARDENVILL 79 230 | NIAGARA - ROBINSON 64 230 | 566 | 654 | 100.84
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | HUNTLEY - GARDENVILL 79 230 | B:STOLE230 | 566 | 654 | 100.4
| 135413 GRDNVL2 230 135419 SUNY-80 230 1 Max |  |  |  |  | 102.05
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | T:77&78 | 189 | 250 | 132.74
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 189 | 250 | 131.53
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 189 | 250 | 120.27
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 189 | 250 | 119.19
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | DCT:230:79+80+ELM1-2 | 189 | 250 | 113.2
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 189 | 250 | 112.08
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | T:79&80 | 189 | 250 | 111.4
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 230 | DCT:230:79+80+ELM1-2 | 189 | 250 | 111.28
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 230 | T:79&80 | 189 | 250 | 108.28
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 189 | 250 | 107.42
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | G:NIAG. 4 | T:77&78 | 189 | 250 | 104.55
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | G:NIAG. 5 | T:77&78 | 189 | 250 | 104.55
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | G:NIAG. 6 | T:77&78 | 189 | 250 | 104.55
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | G:NIAG. 7 | T:77&78 | 189 | 250 | 104.5
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 189 | 250 | 104.18
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 189 | 250 | 103.5
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 189 | 250 | 103.5
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 189 | 250 | 101.86
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | T:77&78 | 189 | 250 | 100.73
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 189 | 250 | 100.38
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 189 | 250 | 100.38
| 135415 PACKARD2 230 135460 PACK(N)E 115 1 Max |  |  |  |  | 132.74
Dispatch 2 | 135415 PACKARD2 230 135461 PACK(S)W 115 2 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 190 | 250 | 109.8
Dispatch 1 | 135415 PACKARD2 230 135461 PACK(S)W 115 2 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 190 | 250 | 102.32
Dispatch 2 | 135415 PACKARD2 230 135461 PACK(S)W 115 2 | NIAGARA - PACKARD 61 230 | T:62&BP76 | 190 | 250 | 101.84
| 135415 PACKARD2 230 135461 PACK(S)W 115 2 Max |  |  |  |  | 109.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | T:62&BP76 | 620 | 717 | 165.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:62&BP76 | 620 | 717 | 160.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:62&BP76 | 620 | 717 | 156.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:62&BP76 | 620 | 717 | 156.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:62&BP76 | 620 | 717 | 155.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | T:62&BP76 | 620 | 717 | 152.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R506 | 620 | 717 | 148.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | T:62&BP76 | 620 | 717 | 147.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:62&BP76 | 620 | 717 | 146.36
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | T:62&BP76 | 620 | 717 | 143.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | T:62&BP76 | 620 | 717 | 143.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | T:62&BP76 | 620 | 717 | 143.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | T:62&BP76 | 620 | 717 | 143.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | T:62&BP76 | 620 | 717 | 143.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 1 | T:62&BP76 | 620 | 717 | 143.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 2 | T:62&BP76 | 620 | 717 | 143.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 3 | T:62&BP76 | 620 | 717 | 143.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:62&BP76 | 620 | 717 | 143.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:62&BP76 | 620 | 717 | 143.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:62&BP76 | 620 | 717 | 143.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:62&BP76 | 620 | 717 | 143
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS1 | T:62&BP76 | 620 | 717 | 142.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R506 | 620 | 717 | 142.55
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R506 | 620 | 717 | 142.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:INDEK-OL | T:62&BP76 | 620 | 717 | 142.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LOCKPORT | T:62&BP76 | 620 | 717 | 141.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:JAMESGN7 | T:62&BP76 | 620 | 717 | 141.55
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R506 | 620 | 717 | 141.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 13 345 | T:62&BP76 | 620 | 717 | 141.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | T:62&BP76 | 620 | 717 | 141.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | T:62&BP76 | 620 | 717 | 141.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | T:62&BP76 | 620 | 717 | 141.04
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:62&BP76 | 620 | 717 | 141.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | T:62&BP76 | 620 | 717 | 140.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:OXBOWNUG | T:62&BP76 | 620 | 717 | 140.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS2 | T:62&BP76 | 620 | 717 | 140.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:DUPONT46 | T:62&BP76 | 620 | 717 | 140.77
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:UDG-184 | T:62&BP76 | 620 | 717 | 140.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DEWITT3 - LAFAYTTE 345 | T:62&BP76 | 620 | 717 | 140.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - WATERCURE 69 230 | T:62&BP76 | 620 | 717 | 140.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - ETWANDA 70 230 | T:62&BP76 | 620 | 717 | 140.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-1 345 | T:62&BP76 | 620 | 717 | 140.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-2 345 | T:62&BP76 | 620 | 717 | 140.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - EDIC 2-15 345 | T:62&BP76 | 620 | 717 | 140.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL - CLAY PC-1 345 | T:62&BP76 | 620 | 717 | 140.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL - CLAY PC-2 345 | T:62&BP76 | 620 | 717 | 140.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 5 MILE - STOLLE 37A 345 | T:62&BP76 | 620 | 717 | 140.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HOMERCTY - STOLLRD 37 345 | T:62&BP76 | 620 | 717 | 140.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE 230/115 3TR | T:62&BP76 | 620 | 717 | 140.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 140.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | BECK - PACKARD BP76 230 | 620 | 717 | 139.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R506 | 620 | 717 | 139.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | T:62&PA27 | 620 | 717 | 139.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:OSWEGO 6 | T:62&BP76 | 620 | 717 | 138.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL 230/115 M6TR | T:62&BP76 | 620 | 717 | 138.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL 230/115 M8TR | T:62&BP76 | 620 | 717 | 138.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:FITZPATR | T:62&BP76 | 620 | 717 | 138.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - BECK PA27 230 | T:62&BP76 | 620 | 717 | 138.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:PA27&BP76 | 620 | 717 | 138.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:9MIPT1 | T:62&BP76 | 620 | 717 | 138.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 73 230 | T:62&BP76 | 620 | 717 | 138.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 74 230 | T:62&BP76 | 620 | 717 | 138.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - FARMVLY | T:62&BP76 | 620 | 717 | 138.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STNYRDG - HILLSIDE 68B 230 | T:62&BP76 | 620 | 717 | 138.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - ELM 70 230 | T:62&BP76 | 620 | 717 | 138.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 7-9 | T:62&BP76 | 620 | 717 | 138.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 10-12 | T:62&BP76 | 620 | 717 | 138.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 1-3 | T:62&BP76 | 620 | 717 | 138.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 4-6 | T:62&BP76 | 620 | 717 | 138.06
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:62&BP76 | 620 | 717 | 137.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | SB:PA230_R506 | 620 | 717 | 137.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MEYER - CANDQUA 60 230 | T:62&BP76 | 620 | 717 | 137.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - WTRCR 31 345 | T:62&BP76 | 620 | 717 | 136.97
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:62&BP76 | 620 | 717 | 136.68
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:62&BP76 | 620 | 717 | 136.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | T:62&BP76 | 620 | 717 | 136.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:GINNA | T:62&BP76 | 620 | 717 | 136.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ERIE E - 4 MILE 230 | T:62&BP76 | 620 | 717 | 136.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SHLDON - STONYCR 230 | T:62&BP76 | 620 | 717 | 135.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | T:62&BP76 | 620 | 717 | 135.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DUNKIRK - SRIPL 68 230 | T:62&BP76 | 620 | 717 | 135.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SRIPL - ERIE E 69 230 | T:62&BP76 | 620 | 717 | 135.26
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R506 | 620 | 717 | 134.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 11 | T:62&BP76 | 620 | 717 | 133.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 12 | T:62&BP76 | 620 | 717 | 133.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 13 | T:62&BP76 | 620 | 717 | 133.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 8 | T:62&BP76 | 620 | 717 | 133.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 9 | T:62&BP76 | 620 | 717 | 133.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 10 | T:62&BP76 | 620 | 717 | 133.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | T:62&BP76 | 620 | 717 | 132.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | T:62&BP76 | 620 | 717 | 132.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | T:62&BP76 | 620 | 717 | 132.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCWC/NWES | T:62&BP76 | 620 | 717 | 132.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:MBWC/NWES | T:62&BP76 | 620 | 717 | 132.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 132.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROBI230 | 620 | 717 | 131.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:62&BP76 | 620 | 717 | 131.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - ROBINSON 64 230 | 620 | 717 | 131.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R506 | 620 | 717 | 131.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCMB/NWES | T:62&BP76 | 620 | 717 | 130.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | T:62&BP76 | 620 | 717 | 130.5
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | T:62&BP76 | 620 | 717 | 130.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R506 | 620 | 717 | 130.27
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | T:62&BP76 | 620 | 717 | 130.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:KINTIGH | T:62&BP76 | 620 | 717 | 129.78
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R506 | 620 | 717 | 129.58
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R506 | 620 | 717 | 129.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | T:62&PA27 | 620 | 717 | 129.02
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:62&BP76 | 620 | 717 | 129
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | T:62&BP76 | 620 | 717 | 128.84
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R506 | 620 | 717 | 128.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R506 | 620 | 717 | 128.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | SB:PA230_R506 | 620 | 717 | 128.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | SB:PA230_R506 | 620 | 717 | 128.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:PA230_R506 | 620 | 717 | 127.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:PA230_R506 | 620 | 717 | 127.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:PA230_R506 | 620 | 717 | 127.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:PA230_R506 | 620 | 717 | 127.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | SB:PA230_R506 | 620 | 717 | 127.16
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | T:62&BP76 | 620 | 717 | 127.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | T:62&BP76 | 620 | 717 | 127.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS1 | SB:PA230_R506 | 620 | 717 | 126.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | T:62&BP76 | 620 | 717 | 126.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R506 | 620 | 717 | 126.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | T:62&BP76 | 620 | 717 | 126.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:INDEK-OL | SB:PA230_R506 | 620 | 717 | 126.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | T:62&BP76 | 620 | 717 | 126.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R506 | 620 | 717 | 126.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R506 | 620 | 717 | 126.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:JAMESGN7 | SB:PA230_R506 | 620 | 717 | 125.98
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | T:62&BP76 | 620 | 717 | 125.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LOCKPORT | SB:PA230_R506 | 620 | 717 | 125.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R506 | 620 | 717 | 125.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 13 345 | SB:PA230_R506 | 620 | 717 | 125.73
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 1 | T:62&BP76 | 620 | 717 | 125.69
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 2 | T:62&BP76 | 620 | 717 | 125.69
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 3 | T:62&BP76 | 620 | 717 | 125.69
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:62&BP76 | 620 | 717 | 125.61
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:62&BP76 | 620 | 717 | 125.61
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:62&BP76 | 620 | 717 | 125.61
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:62&BP76 | 620 | 717 | 125.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | SB:PA230_R506 | 620 | 717 | 125.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:5M-SR_37&W-F_171 | SB:PA230_R506 | 620 | 717 | 125.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 5 MILE - STOLLE 37A 345 | SB:PA230_R506 | 620 | 717 | 125.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R506 | 620 | 717 | 125.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS2 | SB:PA230_R506 | 620 | 717 | 125.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R506 | 620 | 717 | 125.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R506 | 620 | 717 | 125.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R506 | 620 | 717 | 125.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R506 | 620 | 717 | 125.24
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | T:62&BP76 | 620 | 717 | 125.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-2 345 | SB:PA230_R506 | 620 | 717 | 125.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-1 345 | SB:PA230_R506 | 620 | 717 | 125.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - EDIC 2-15 345 | SB:PA230_R506 | 620 | 717 | 125.1
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | T:62&BP76 | 620 | 717 | 125.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | SB:PA230_R3430 | 620 | 717 | 125.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL - CLAY PC-1 345 | SB:PA230_R506 | 620 | 717 | 125.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL - CLAY PC-2 345 | SB:PA230_R506 | 620 | 717 | 125.01
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | T:62&BP76 | 620 | 717 | 124.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | B:PACKT4 | 620 | 717 | 124.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:NIAW230_2014 | 620 | 717 | 124.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 124.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | B:STOLE230 | 620 | 717 | 124.34
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS1 | T:62&BP76 | 620 | 717 | 124.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:NIAG345_3108 | 620 | 717 | 123.88
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 13 345 | T:62&BP76 | 620 | 717 | 123.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 123.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - BECK PA27 230 | SB:PA230_R506 | 620 | 717 | 123.57
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:INDEK-OL | T:62&BP76 | 620 | 717 | 123.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:9MIPT1 | SB:PA230_R506 | 620 | 717 | 123.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 1 | SB:PA230_R506 | 620 | 717 | 123.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 2 | SB:PA230_R506 | 620 | 717 | 123.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 3 | SB:PA230_R506 | 620 | 717 | 123.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:255_345B302 | 620 | 717 | 123.32
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DEWITT3 - LAFAYTTE 345 | T:62&BP76 | 620 | 717 | 123.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | ROBINSON - STOLLRD 65 230 | 620 | 717 | 123.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R506 | 620 | 717 | 123.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R506 | 620 | 717 | 123.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAG - NEWROCH 1 345 | 620 | 717 | 123.19
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LOCKPORT | T:62&BP76 | 620 | 717 | 123.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - FARMVLY | SB:PA230_R506 | 620 | 717 | 123.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R506 | 620 | 717 | 123.13
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - EDIC 2-15 345 | T:62&BP76 | 620 | 717 | 123.11
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-2 345 | T:62&BP76 | 620 | 717 | 123.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 122.99
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:JAMESGN7 | T:62&BP76 | 620 | 717 | 122.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - ELM 70 230 | SB:PA230_R506 | 620 | 717 | 122.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 7-9 | SB:PA230_R506 | 620 | 717 | 122.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 10-12 | SB:PA230_R506 | 620 | 717 | 122.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 1-3 | SB:PA230_R506 | 620 | 717 | 122.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 4-6 | SB:PA230_R506 | 620 | 717 | 122.93
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL - CLAY PC-2 345 | T:62&BP76 | 620 | 717 | 122.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL - CLAY PC-1 345 | T:62&BP76 | 620 | 717 | 122.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | STOLLRD - GARDENVILL 66 230 | 620 | 717 | 122.83
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | EDIC - FITZ 345 | T:62&BP76 | 620 | 717 | 122.67
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OS - EL - LFYTE 17 345 | T:62&BP76 | 620 | 717 | 122.56
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL 345/115 1TR | T:62&BP76 | 620 | 717 | 122.5
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL 345/115 2TR | T:62&BP76 | 620 | 717 | 122.5
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL 345/115 3TR | T:62&BP76 | 620 | 717 | 122.48
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | T:62&BP76 | 620 | 717 | 122.43
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | T:62&BP76 | 620 | 717 | 122.43
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | T:62&BP76 | 620 | 717 | 122.42
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY 345/115 1TR | T:62&BP76 | 620 | 717 | 122.36
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY 345/115 2TR | T:62&BP76 | 620 | 717 | 122.36
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 5 MILE - STOLLE 37A 345 | T:62&BP76 | 620 | 717 | 122.35
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | VOL - MARCY 19 345 | T:62&BP76 | 620 | 717 | 122.35
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HOMERCTY - STOLLRD 37 345 | T:62&BP76 | 620 | 717 | 122.34
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:5M-SR_37&W-F_171 | T:62&BP76 | 620 | 717 | 122.3
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | T:62&BP76 | 620 | 717 | 122.29
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:OXBOWNUG | T:62&BP76 | 620 | 717 | 122.29
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 3 115 | T:62&BP76 | 620 | 717 | 122.27
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - TEAL 10 115 | T:62&BP76 | 620 | 717 | 122.27
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - LM 14 115 | T:62&BP76 | 620 | 717 | 122.26
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - TEAL 11 115 | T:62&BP76 | 620 | 717 | 122.26
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 5 115 | T:62&BP76 | 620 | 717 | 122.24
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LHH - CLAY 7 115 | T:62&BP76 | 620 | 717 | 122.23
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FUL - CLAY 4 115 | T:62&BP76 | 620 | 717 | 122.22
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - WOOD 17 115 | T:62&BP76 | 620 | 717 | 122.22
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS2 | T:62&BP76 | 620 | 717 | 122.22
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - VOL 21 345 | T:62&BP76 | 620 | 717 | 122.2
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA 345/115 1TR | T:62&BP76 | 620 | 717 | 122.2
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA 345/115 2TR | T:62&BP76 | 620 | 717 | 122.2
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:DUPONT46 | T:62&BP76 | 620 | 717 | 122.2
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - 9MI1 9 345 | T:62&BP76 | 620 | 717 | 122.19
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - VOL 20 345 | T:62&BP76 | 620 | 717 | 122.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MEYER - CANDQUA 60 230 | SB:PA230_R506 | 620 | 717 | 122.18
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OSW - VOL 11 345 | T:62&BP76 | 620 | 717 | 122.17
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OSW - VOL 12 345 | T:62&BP76 | 620 | 717 | 122.17
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OSW 345/115 1TR | T:62&BP76 | 620 | 717 | 122.17
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - IND 25 345 | T:62&BP76 | 620 | 717 | 122.17
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - FITZ 10 345 | T:62&BP76 | 620 | 717 | 122.13
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:UDG-184 | T:62&BP76 | 620 | 717 | 122.13
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | EDIC - MRCY ue 1-7 345 | T:62&BP76 | 620 | 717 | 122.11
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - WATERCURE 69 230 | T:62&BP76 | 620 | 717 | 122.09
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - ETWANDA 70 230 | T:62&BP76 | 620 | 717 | 122.09
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DEWITT 345/115 2TR | T:62&BP76 | 620 | 717 | 121.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - WTRCR 31 345 | SB:PA230_R506 | 620 | 717 | 121.97
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-1 345 | T:62&BP76 | 620 | 717 | 121.94
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE 230/115 3TR | T:62&BP76 | 620 | 717 | 121.76
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 121.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ERIE E - 4 MILE 230 | SB:PA230_R506 | 620 | 717 | 121.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | SB:PA230_R506 | 620 | 717 | 121.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:GINNA | SB:PA230_R506 | 620 | 717 | 121.28
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | BECK - PACKARD BP76 230 | 620 | 717 | 121.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:255_345B202 | 620 | 717 | 121.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SHLDON - STONYCR 230 | SB:PA230_R506 | 620 | 717 | 121.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SOMERSET - NEWROCH 1 345 | 620 | 717 | 121.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 120.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DUNKIRK - SRIPL 68 230 | SB:PA230_R506 | 620 | 717 | 120.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SRIPL - ERIE E 69 230 | SB:PA230_R506 | 620 | 717 | 120.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:GARD230_T7-12 | 620 | 717 | 120.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | NIAGARA - PACKARD 62 230 | 620 | 717 | 120.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R506 | 620 | 717 | 120.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA 230/115 1TR | 620 | 717 | 120.52
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | T:62&PA27 | 620 | 717 | 120.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:62&PA27 | 620 | 717 | 120.32
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:FITZPATR | T:62&BP76 | 620 | 717 | 120.21
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - BECK PA27 230 | T:62&BP76 | 620 | 717 | 120.13
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R506 | 620 | 717 | 120.02
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:PA27&BP76 | 620 | 717 | 119.97
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:9MIPT1 | T:62&BP76 | 620 | 717 | 119.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:62&PA27 | 620 | 717 | 119.88
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 73 230 | T:62&BP76 | 620 | 717 | 119.77
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 74 230 | T:62&BP76 | 620 | 717 | 119.75
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STNYRDG - HILLSIDE 68B 230 | T:62&BP76 | 620 | 717 | 119.69
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - FARMVLY | T:62&BP76 | 620 | 717 | 119.66
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - WTRCR 31 345 | T:62&BP76 | 620 | 717 | 119.65
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - ELM 70 230 | T:62&BP76 | 620 | 717 | 119.53
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 1-3 | T:62&BP76 | 620 | 717 | 119.48
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 7-9 | T:62&BP76 | 620 | 717 | 119.48
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 10-12 | T:62&BP76 | 620 | 717 | 119.48
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 4-6 | T:62&BP76 | 620 | 717 | 119.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:62&PA27 | 620 | 717 | 119.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 11 | SB:PA230_R506 | 620 | 717 | 119.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 12 | SB:PA230_R506 | 620 | 717 | 119.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 13 | SB:PA230_R506 | 620 | 717 | 119.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 8 | SB:PA230_R506 | 620 | 717 | 119.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 9 | SB:PA230_R506 | 620 | 717 | 119.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 10 | SB:PA230_R506 | 620 | 717 | 119.34
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R506 | 620 | 717 | 119.06
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | T:62&BP76 | 620 | 717 | 118.95
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MEYER - CANDQUA 60 230 | T:62&BP76 | 620 | 717 | 118.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | SB:PA230_R506 | 620 | 717 | 118.55
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | SB:PA230_R506 | 620 | 717 | 118.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3430 | 620 | 717 | 118.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | SB:PA230_R506 | 620 | 717 | 117.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT4 | 620 | 717 | 117.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R506 | 620 | 717 | 117.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCWC/NWES | SB:PA230_R506 | 620 | 717 | 117.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:MBWC/NWES | SB:PA230_R506 | 620 | 717 | 117.79
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:GINNA | T:62&BP76 | 620 | 717 | 117.52
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ERIE E - 4 MILE 230 | T:62&BP76 | 620 | 717 | 117.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | T:62&PA27 | 620 | 717 | 117.25
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SHLDON - STONYCR 230 | T:62&BP76 | 620 | 717 | 117.12
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 11 | T:62&BP76 | 620 | 717 | 117.06
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 12 | T:62&BP76 | 620 | 717 | 117.06
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 13 | T:62&BP76 | 620 | 717 | 117.06
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 8 | T:62&BP76 | 620 | 717 | 117.05
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 9 | T:62&BP76 | 620 | 717 | 117.05
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 10 | T:62&BP76 | 620 | 717 | 117.04
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:62&BP76 | 620 | 717 | 117
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | T:62&BP76 | 620 | 717 | 116.76
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DUNKIRK - SRIPL 68 230 | T:62&BP76 | 620 | 717 | 116.65
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SRIPL - ERIE E 69 230 | T:62&BP76 | 620 | 717 | 116.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:62&PA27 | 620 | 717 | 116.51
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:PA230_R506 | 620 | 717 | 116.43
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:PA230_R506 | 620 | 717 | 116.43
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:PA230_R506 | 620 | 717 | 116.43
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | T:62&BP76 | 620 | 717 | 116.4
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:PA230_R506 | 620 | 717 | 116.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCMB/NWES | SB:PA230_R506 | 620 | 717 | 116.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | SB:PA230_R506 | 620 | 717 | 116.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:40&41 | 620 | 717 | 116.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R506 | 620 | 717 | 116.21
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R506 | 620 | 717 | 115.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:KINTIGH | SB:PA230_R506 | 620 | 717 | 115.86
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | SB:PA230_R506 | 620 | 717 | 115.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:41&33 | 620 | 717 | 115.55
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | SB:PA230_R506 | 620 | 717 | 115.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 115.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | SB:PA230_R506 | 620 | 717 | 114.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:34&42 | 620 | 717 | 114.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | FARMVLY - HOMERCTY | 620 | 717 | 114.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 114.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:HC-FV_37&W-F_171 | 620 | 717 | 114.57
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS1 | SB:PA230_R506 | 620 | 717 | 114.52
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 13 345 | SB:PA230_R506 | 620 | 717 | 114.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R506 | 620 | 717 | 114.25
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | T:62&BP76 | 620 | 717 | 114.18
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:INDEK-OL | SB:PA230_R506 | 620 | 717 | 114.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R506 | 620 | 717 | 113.99
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R506 | 620 | 717 | 113.93
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R506 | 620 | 717 | 113.93
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R506 | 620 | 717 | 113.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LAPER_345_1 | 620 | 717 | 113.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LAPER_345_2 | 620 | 717 | 113.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | LFYTE - CLARKCRNS 36A 345 | 620 | 717 | 113.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LAFAYETT | 620 | 717 | 113.73
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - EDIC 2-15 345 | SB:PA230_R506 | 620 | 717 | 113.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LAFA_ELB | 620 | 717 | 113.7
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-2 345 | SB:PA230_R506 | 620 | 717 | 113.69
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:JAMESGN7 | SB:PA230_R506 | 620 | 717 | 113.64
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LOCKPORT | SB:PA230_R506 | 620 | 717 | 113.63
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | T:62&BP76 | 620 | 717 | 113.63
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:5M-SR_37&W-F_171 | SB:PA230_R506 | 620 | 717 | 113.57
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | T:62&BP76 | 620 | 717 | 113.57
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL - CLAY PC-1 345 | SB:PA230_R506 | 620 | 717 | 113.56
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL - CLAY PC-2 345 | SB:PA230_R506 | 620 | 717 | 113.56
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCWC/NWES | T:62&BP76 | 620 | 717 | 113.53
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:MBWC/NWES | T:62&BP76 | 620 | 717 | 113.53
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R506 | 620 | 717 | 113.51
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 5 MILE - STOLLE 37A 345 | SB:PA230_R506 | 620 | 717 | 113.48
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R506 | 620 | 717 | 113.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:NIAG345_3308 | 620 | 717 | 113.41
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | EDIC - FITZ 345 | SB:PA230_R506 | 620 | 717 | 113.33
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 113.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LAPER_345_3 | 620 | 717 | 113.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LAPER_345_4 | 620 | 717 | 113.28
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROBI230 | 620 | 717 | 113.27
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OS - EL - LFYTE 17 345 | SB:PA230_R506 | 620 | 717 | 113.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:PA230_R506 | 620 | 717 | 113.17
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL 345/115 1TR | SB:PA230_R506 | 620 | 717 | 113.15
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL 345/115 2TR | SB:PA230_R506 | 620 | 717 | 113.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:OAKD345_B5 | 620 | 717 | 113.15
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL 345/115 3TR | SB:PA230_R506 | 620 | 717 | 113.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:OAKD345_B6 | 620 | 717 | 113.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | OAKDLE - CLARKCRNS 36B 345 | 620 | 717 | 113.12
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | SB:PA230_R506 | 620 | 717 | 113.11
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY 345/115 1TR | SB:PA230_R506 | 620 | 717 | 113.08
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY 345/115 2TR | SB:PA230_R506 | 620 | 717 | 113.08
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | VOL - MARCY 19 345 | SB:PA230_R506 | 620 | 717 | 113.04
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 3 115 | SB:PA230_R506 | 620 | 717 | 112.95
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - TEAL 10 115 | SB:PA230_R506 | 620 | 717 | 112.95
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - TEAL 11 115 | SB:PA230_R506 | 620 | 717 | 112.94
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - LM 14 115 | SB:PA230_R506 | 620 | 717 | 112.93
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS2 | SB:PA230_R506 | 620 | 717 | 112.93
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 5 115 | SB:PA230_R506 | 620 | 717 | 112.92
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LHH - CLAY 7 115 | SB:PA230_R506 | 620 | 717 | 112.92
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - WOOD 17 115 | SB:PA230_R506 | 620 | 717 | 112.91
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FUL - CLAY 4 115 | SB:PA230_R506 | 620 | 717 | 112.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - VOL 21 345 | SB:PA230_R506 | 620 | 717 | 112.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R506 | 620 | 717 | 112.89
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - 9MI1 9 345 | SB:PA230_R506 | 620 | 717 | 112.89
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - VOL 20 345 | SB:PA230_R506 | 620 | 717 | 112.89
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA 345/115 1TR | SB:PA230_R506 | 620 | 717 | 112.89
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA 345/115 2TR | SB:PA230_R506 | 620 | 717 | 112.89
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OSW - VOL 11 345 | SB:PA230_R506 | 620 | 717 | 112.87
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OSW - VOL 12 345 | SB:PA230_R506 | 620 | 717 | 112.87
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OSW 345/115 1TR | SB:PA230_R506 | 620 | 717 | 112.87
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - IND 25 345 | SB:PA230_R506 | 620 | 717 | 112.87
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R506 | 620 | 717 | 112.84
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R506 | 620 | 717 | 112.84
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SCRIBA - FITZ 10 345 | SB:PA230_R506 | 620 | 717 | 112.83
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | EDIC - MRCY ue 1-7 345 | SB:PA230_R506 | 620 | 717 | 112.83
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | SB:PA230_R3430 | 620 | 717 | 112.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:COOP345_42-4182 | 620 | 717 | 112.69
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-1 345 | SB:PA230_R506 | 620 | 717 | 112.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:31&41 | 620 | 717 | 112.65
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:DUPONT46 | SB:PA230_R506 | 620 | 717 | 112.61
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - ROBINSON 64 230 | 620 | 717 | 112.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:5MILE_B | 620 | 717 | 112.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:EDIC345_R915 | 620 | 717 | 112.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA 230/115 2TR | 620 | 717 | 112.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA 345/230 4TR | 620 | 717 | 112.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | NIAGARA - PACKARD 62 230 | 620 | 717 | 112.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | NIAGARA - PACKARD 62 230 | 620 | 717 | 112.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 112.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAG - KINTIGH 345 | 620 | 717 | 112.46
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | B:PACKT4 | 620 | 717 | 112.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | NIAGARA - PACKARD 62 230 | 620 | 717 | 112.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 345/230 4TR | NIAGARA - PACKARD 62 230 | 620 | 717 | 112.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:COOP345_4182 | 620 | 717 | 112.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:MP11&41 | 620 | 717 | 112.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MARC345_3202 | 620 | 717 | 112.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MARC345_3208 | 620 | 717 | 112.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | MARCY - COOPERS 345 SC | 620 | 717 | 112.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:77&76 | 620 | 717 | 112.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:EDIC345_R935 | 620 | 717 | 112.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:30&40 | 620 | 717 | 112.01
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCMB/NWES | T:62&BP76 | 620 | 717 | 111.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:EDIC345_R400 | 620 | 717 | 111.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MARC345_3108 | 620 | 717 | 111.84
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | T:62&BP76 | 620 | 717 | 111.83
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | T:62&BP76 | 620 | 717 | 111.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS1 | NIAGARA - PACKARD 62 230 | 620 | 717 | 111.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROCH_3414 | 620 | 717 | 111.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROCH_3514 | 620 | 717 | 111.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 4 | NIAGARA - PACKARD 62 230 | 620 | 717 | 111.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 5 | NIAGARA - PACKARD 62 230 | 620 | 717 | 111.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 6 | NIAGARA - PACKARD 62 230 | 620 | 717 | 111.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | EDIC - FRASER 345 SC | 620 | 717 | 111.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | T:62&PA27 | 620 | 717 | 111.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 1 | NIAGARA - PACKARD 62 230 | 620 | 717 | 111.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 2 | NIAGARA - PACKARD 62 230 | 620 | 717 | 111.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 3 | NIAGARA - PACKARD 62 230 | 620 | 717 | 111.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 7 | NIAGARA - PACKARD 62 230 | 620 | 717 | 111.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:FRAS345_B1-4062 | 620 | 717 | 111.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:FRAS345_40-B262 | 620 | 717 | 111.55
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROCH_2T8082 | 620 | 717 | 111.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:69J&70K | 620 | 717 | 111.5
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:W89&W90 | 620 | 717 | 111.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:INDEK-OL | NIAGARA - PACKARD 62 230 | 620 | 717 | 111.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROCH_34XC | 620 | 717 | 111.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SIN:170 | 620 | 717 | 111.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SIN:180 | 620 | 717 | 111.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | B:N.S._99 | 620 | 717 | 111.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | B:N.S._77 | 620 | 717 | 111.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:EDIC345_R140 | 620 | 717 | 111.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SIN:160 | 620 | 717 | 111.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SIN:150 | 620 | 717 | 111.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:F38&F39 | 620 | 717 | 111.2
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:KINTIGH | T:62&BP76 | 620 | 717 | 111.17
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - BECK PA27 230 | SB:PA230_R506 | 620 | 717 | 111.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:CLAY345_R935 | 620 | 717 | 111.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:MP12&18 | 620 | 717 | 111.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:CLAY345_R945 | 620 | 717 | 111.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SIN:90 | 620 | 717 | 111.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3430 | 620 | 717 | 111.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | MARCY - N.SCOT99 I8 345 | 620 | 717 | 111.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MARC345_3314 | 620 | 717 | 111.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MARC345_3308 | 620 | 717 | 111.07
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:9MIPT1 | SB:PA230_R506 | 620 | 717 | 111.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:5MILE | 620 | 717 | 111.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROCK345_376512 | 620 | 717 | 111.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:F30&F31 | 620 | 717 | 110.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | EDIC - N.SCOT77 I4 345 | 620 | 717 | 110.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROCK345_31153 | 620 | 717 | 110.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3430 | 620 | 717 | 110.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:JAMESGN7 | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT4 | 620 | 717 | 110.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:CLAY345_R150 | 620 | 717 | 110.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:CLAY345_R160 | 620 | 717 | 110.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PV345_RNS5 | 620 | 717 | 110.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:62&PA27 | 620 | 717 | 110.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PV345_RNS4 | 620 | 717 | 110.84
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R506 | 620 | 717 | 110.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:EDIC345_R110 | 620 | 717 | 110.83
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R506 | 620 | 717 | 110.82
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R506 | 620 | 717 | 110.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROCK345_3456 | 620 | 717 | 110.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LEEDS345_R9293 | 620 | 717 | 110.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:EDIC345_R150 | 620 | 717 | 110.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:EDIC345_R160 | 620 | 717 | 110.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT4 | 620 | 717 | 110.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:COOP345_34-B382 | 620 | 717 | 110.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:COOP345_B2-3482 | 620 | 717 | 110.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | COOPERC - ROCKT CMT/MTR-34 345 | 620 | 717 | 110.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | HURLEY - ROCKT CMT/MTR-34 345 | 620 | 717 | 110.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | CLAY - EDIC 1-16 345 | 620 | 717 | 110.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | CLAY - EDIC 2-15 345 | 620 | 717 | 110.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | CLAY - EDIC 2-15 345 | 620 | 717 | 110.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:EDIC345_R10 | 620 | 717 | 110.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PANN345_3908 | 620 | 717 | 110.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PANN345_3808 | 620 | 717 | 110.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MARC345_3102 | 620 | 717 | 110.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA 345/230 5TR | 620 | 717 | 110.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA 345/230 3TR | 620 | 717 | 110.7
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - WTRCR 31 345 | SB:PA230_R506 | 620 | 717 | 110.69
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - FARMVLY | SB:PA230_R506 | 620 | 717 | 110.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | FARMVLY - 5MILE 345 | 620 | 717 | 110.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 13 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | FITZ - EDIC FEI 345 | 620 | 717 | 110.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | EDIC - FITZ 345 | 620 | 717 | 110.65
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - ELM 70 230 | SB:PA230_R506 | 620 | 717 | 110.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | VOLNEY - MARCY I9 345 | 620 | 717 | 110.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | VOL - MARCY 19 345 | 620 | 717 | 110.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:VOLN_R925 | 620 | 717 | 110.62
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 1 | SB:PA230_R506 | 620 | 717 | 110.61
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 2 | SB:PA230_R506 | 620 | 717 | 110.61
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 3 | SB:PA230_R506 | 620 | 717 | 110.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:HC-SR_37&W-F_171 | 620 | 717 | 110.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:FV-5M_37&W-F_171 | 620 | 717 | 110.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROCK345_4255 | 620 | 717 | 110.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:DUNW345_3 | 620 | 717 | 110.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 345/230 3TR | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 345/230 5TR | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:COOP345_B2-4282 | 620 | 717 | 110.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | ROCH 345/115 5TR | 620 | 717 | 110.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | COOPERC - ROCKT CCRT-42 345 | 620 | 717 | 110.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | COOPERC - ROCKT CCRT-42 345 | 620 | 717 | 110.53
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 1-3 | SB:PA230_R506 | 620 | 717 | 110.52
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 7-9 | SB:PA230_R506 | 620 | 717 | 110.52
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 10-12 | SB:PA230_R506 | 620 | 717 | 110.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LEEDS345_R94301 | 620 | 717 | 110.52
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 4-6 | SB:PA230_R506 | 620 | 717 | 110.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LOCKPORT | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.5
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | CLAY - DEW 13 345 | 620 | 717 | 110.5
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:DUNW345_8 | 620 | 717 | 110.5
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROCH_1X8082 | 620 | 717 | 110.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | LEEDS - PV 92 345 | 620 | 717 | 110.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LEEDS345_R92 | 620 | 717 | 110.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | LEEDS - PV 92 345 | 620 | 717 | 110.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | ATHENS - PV 91 345 | 620 | 717 | 110.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | ATHENS - PV 91 345 | 620 | 717 | 110.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:COOP345_3382 | 620 | 717 | 110.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PANN345_3914 | 620 | 717 | 110.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PANN345_3814 | 620 | 717 | 110.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROCH_3408 | 620 | 717 | 110.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROCH_3508 | 620 | 717 | 110.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PANN345_3902 | 620 | 717 | 110.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PANN345_3802 | 620 | 717 | 110.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:DEWI345_R915 | 620 | 717 | 110.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:FRAS345_33-B262 | 620 | 717 | 110.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:DEWI345_R130 | 620 | 717 | 110.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:DEWI345_R220 | 620 | 717 | 110.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:DUNW345_4 | 620 | 717 | 110.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS2 | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:FARR345_2W | 620 | 717 | 110.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:COOP345_B2-3382 | 620 | 717 | 110.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | FRASER - COOPERS 345 SC | 620 | 717 | 110.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:DUNW345_6 | 620 | 717 | 110.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:OXBOWNUG | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.27
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | T:62&BP76 | 620 | 717 | 110.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DEWITT3 - LAFAYTTE 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:DUPONT46 | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - WATERCURE 69 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - ETWANDA 70 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:UDG-184 | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - EDIC 2-15 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 110.14
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | SB:PA230_R506 | 620 | 717 | 110.03
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MEYER - CANDQUA 60 230 | SB:PA230_R506 | 620 | 717 | 109.75
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | T:62&PA27 | 620 | 717 | 109.74
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | SB:PA230_R506 | 620 | 717 | 109.44
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ERIE E - 4 MILE 230 | SB:PA230_R506 | 620 | 717 | 109.2
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | T:62&BP76 | 620 | 717 | 109.16
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | T:62&BP76 | 620 | 717 | 109.02
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | T:62&BP76 | 620 | 717 | 108.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 345/230 4TR | T:62&PA27 | 620 | 717 | 108.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GARDENVILL 230/115 M8TR | 620 | 717 | 108.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GARDENVILL 230/115 M6TR | 620 | 717 | 108.85
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:GINNA | SB:PA230_R506 | 620 | 717 | 108.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | T:62&PA27 | 620 | 717 | 108.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | T:62&PA27 | 620 | 717 | 108.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:OAKD345_B2 | 620 | 717 | 108.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | T:62&PA27 | 620 | 717 | 108.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:SHLDN230 | 620 | 717 | 108.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: NRTPTG3 | 620 | 717 | 108.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: NRTPTG4 | 620 | 717 | 108.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: NRTPTG1 | 620 | 717 | 108.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: NRTPTG2 | 620 | 717 | 108.74
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | T:62&BP76 | 620 | 717 | 108.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: SCS AST | 620 | 717 | 108.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | T:62&PA27 | 620 | 717 | 108.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:CAITH | 620 | 717 | 108.72
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SHLDON - STONYCR 230 | SB:PA230_R506 | 620 | 717 | 108.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: BAYONNE | 620 | 717 | 108.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:GOWANUS_22 | 620 | 717 | 108.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | OAKDLE - WTRCR 31 345 | 620 | 717 | 108.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:OAKD345_B3 | 620 | 717 | 108.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3430 | 620 | 717 | 108.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:72&69 | 620 | 717 | 108.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: POLETTIX | 620 | 717 | 108.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: ATHENS #1 | 620 | 717 | 108.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:9MIPT1 | NIAGARA - PACKARD 62 230 | 620 | 717 | 108.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:W49_3 | 620 | 717 | 108.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:SELKIRK2 | 620 | 717 | 108.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ASTO345_2 | 620 | 717 | 108.57
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:WATRC345_31-2 | 620 | 717 | 108.57
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN:NOEND | 620 | 717 | 108.54
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DUNKIRK - SRIPL 68 230 | SB:PA230_R506 | 620 | 717 | 108.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ASTO345_1 | 620 | 717 | 108.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MOSE230_2214 | 620 | 717 | 108.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN:MOS17-20 | 620 | 717 | 108.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MOSE230_2224 | 620 | 717 | 108.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MOSE230_2208 | 620 | 717 | 108.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:RMP345_T1500 | 620 | 717 | 108.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MOSE115_1724 | 620 | 717 | 108.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MOSE115_1714 | 620 | 717 | 108.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MOSE115_1524 | 620 | 717 | 108.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MOSE115_1514 | 620 | 717 | 108.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MOSE115_1508 | 620 | 717 | 108.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MOSE230_2524 | 620 | 717 | 108.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MOSE230_2514 | 620 | 717 | 108.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN:MOS21-24 | 620 | 717 | 108.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MOSE230_2508 | 620 | 717 | 108.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STNYRDG - HILLSIDE 68B 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 108.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | RAMAPO - BRNCHBRG 5018 345 | 620 | 717 | 108.45
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SRIPL - ERIE E 69 230 | SB:PA230_R506 | 620 | 717 | 108.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:PACKT4 | 620 | 717 | 108.43
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 11 | SB:PA230_R506 | 620 | 717 | 108.42
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 12 | SB:PA230_R506 | 620 | 717 | 108.42
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 13 | SB:PA230_R506 | 620 | 717 | 108.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:RMP345_1500-2X | 620 | 717 | 108.42
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 8 | SB:PA230_R506 | 620 | 717 | 108.41
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 9 | SB:PA230_R506 | 620 | 717 | 108.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | HILLSIDE 230/115 4TR | 620 | 717 | 108.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | B:HILLSIDE | 620 | 717 | 108.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:HILL_B412 | 620 | 717 | 108.41
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 10 | SB:PA230_R506 | 620 | 717 | 108.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | PACKARD 230/115 4TR | 620 | 717 | 108.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:F21&G23M | 620 | 717 | 108.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: ASTORIS | 620 | 717 | 108.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - FARMVLY | NIAGARA - PACKARD 62 230 | 620 | 717 | 108.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 73 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 108.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 74 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 108.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | NIAGARA - PACKARD 62 230 | 620 | 717 | 108.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:W49_1 | 620 | 717 | 108.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:RAIN345_8W | 620 | 717 | 108.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:HILL_68-B412 | 620 | 717 | 108.23
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R506 | 620 | 717 | 108.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | STNYRDG - HILLSIDE 68B 230 | 620 | 717 | 108.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: BOWL PT2 | 620 | 717 | 108.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROSE345_30356 | 620 | 717 | 108.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SIN:30 | 620 | 717 | 108.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | BWLN - WHAV -LDN 67 345 | 620 | 717 | 108.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: BOWL PT1 | 620 | 717 | 108.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | HUNTLEY - ELM 70 230 | 620 | 717 | 108.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROSE345_30553 | 620 | 717 | 108.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS1 | T:62&PA27 | 620 | 717 | 108.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - ELM 70 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 108.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LADE_4-56-2 | 620 | 717 | 108.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LADE_6-56-2 | 620 | 717 | 108.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LADE_1-56-2 | 620 | 717 | 108
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | FARMVLY - FARMVLY | 620 | 717 | 107.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:LADE_3-56-2 | 620 | 717 | 107.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROSE345_31152 | 620 | 717 | 107.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:RAIN345_1W | 620 | 717 | 107.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | B:DUNKG3 | 620 | 717 | 107.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: ROSETON2 | 620 | 717 | 107.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROSE345_30551 | 620 | 717 | 107.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GARDENVILL - DUNKIRK 73 230 | 620 | 717 | 107.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: RAVENSWOOD | 620 | 717 | 107.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GARDENVILL - DUNKIRK 74 230 | 620 | 717 | 107.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:RAIN345_9W | 620 | 717 | 107.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:62&PA27 | 620 | 717 | 107.77
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:62&PA27 | 620 | 717 | 107.77
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:62&PA27 | 620 | 717 | 107.77
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:62&PA27 | 620 | 717 | 107.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: BESICORP | 620 | 717 | 107.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:EMPIRE | 620 | 717 | 107.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:INDEK-OL | T:62&PA27 | 620 | 717 | 107.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 1 | T:62&PA27 | 620 | 717 | 107.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 2 | T:62&PA27 | 620 | 717 | 107.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 3 | T:62&PA27 | 620 | 717 | 107.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: ROSETON1 | 620 | 717 | 107.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 7-9 | NIAGARA - PACKARD 62 230 | 620 | 717 | 107.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 10-12 | NIAGARA - PACKARD 62 230 | 620 | 717 | 107.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:GILB345_3208 | 620 | 717 | 107.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 1-3 | NIAGARA - PACKARD 62 230 | 620 | 717 | 107.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 4-6 | NIAGARA - PACKARD 62 230 | 620 | 717 | 107.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:AT_R6361 | 620 | 717 | 107.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | S:EMPIRE | 620 | 717 | 107.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MEYER - CANDQUA 60 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 107.61
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 107.55
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:HCWC/NWES | 620 | 717 | 107.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:MBWC/NWES | 620 | 717 | 107.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN GILBOA #3&4 | 620 | 717 | 107.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:GILB345_3302 | 620 | 717 | 107.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:WATRC345_30-3142 | 620 | 717 | 107.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | WTRCR - MAINSBRG 30A 345 | 620 | 717 | 107.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:GILB345_3308 | 620 | 717 | 107.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:WATRC345_B1-3042 | 620 | 717 | 107.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:NTHF3&4 | 620 | 717 | 107.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN GILBOA #1&2 | 620 | 717 | 107.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:GILB345_3202 | 620 | 717 | 107.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | SB:PA230_R3430 | 620 | 717 | 107.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - WTRCR 31 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 107.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:HC-WC_30&W-F_171 | 620 | 717 | 107.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | MEYER - CANDQUA 60 230 | 620 | 717 | 107.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:JAMESGN7 | T:62&PA27 | 620 | 717 | 107.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN:SITHE 1 | 620 | 717 | 107.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN:SITHE 2 | 620 | 717 | 107.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | B:PACKT4 | 620 | 717 | 107.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:CNDGUA | 620 | 717 | 107.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:HCMB/NWES | 620 | 717 | 107.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 13 345 | T:62&PA27 | 620 | 717 | 107.05
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | B:STOLE230 | 620 | 717 | 107.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | MAINSBRG - HOMERCITY 30B 345 | 620 | 717 | 107.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: IND PT 2 | 620 | 717 | 107.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN:BETHSTM | 620 | 717 | 107
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 345/230 3TR | T:62&PA27 | 620 | 717 | 106.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 345/230 5TR | T:62&PA27 | 620 | 717 | 106.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:BUCHN_11 | 620 | 717 | 106.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:BUCHN_9 | 620 | 717 | 106.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:HC-MB_30&W-F_171 | 620 | 717 | 106.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:BUCHN_7 | 620 | 717 | 106.91
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:NIAG345_3108 | 620 | 717 | 106.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 106.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN: IND PT 3 | 620 | 717 | 106.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:BUCHS_1 | 620 | 717 | 106.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:BUCHS_3 | 620 | 717 | 106.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | T:62&PA27 | 620 | 717 | 106.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:GINNA | NIAGARA - PACKARD 62 230 | 620 | 717 | 106.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | T:62&PA27 | 620 | 717 | 106.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | T:62&PA27 | 620 | 717 | 106.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS2 | T:62&PA27 | 620 | 717 | 106.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LOCKPORT | T:62&PA27 | 620 | 717 | 106.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:FRGT/WRFL | 620 | 717 | 106.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | T:62&PA27 | 620 | 717 | 106.68
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:255_345B302 | 620 | 717 | 106.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:KINT_39-B112 | 620 | 717 | 106.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DEWITT3 - LAFAYTTE 345 | T:62&PA27 | 620 | 717 | 106.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:OXBOWNUG | T:62&PA27 | 620 | 717 | 106.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - WATERCURE 69 230 | T:62&PA27 | 620 | 717 | 106.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - ETWANDA 70 230 | T:62&PA27 | 620 | 717 | 106.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:DUPONT46 | T:62&PA27 | 620 | 717 | 106.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:KINT_B1-3812 | 620 | 717 | 106.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:67&68&BW | 620 | 717 | 106.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 5 MILE - STOLLE 37A 345 | T:62&PA27 | 620 | 717 | 106.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HOMERCTY - STOLLRD 37 345 | T:62&PA27 | 620 | 717 | 106.56
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 106.55
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAG - NEWROCH 1 345 | 620 | 717 | 106.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SIN:130 | 620 | 717 | 106.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SIN:120_130 | 620 | 717 | 106.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:W97&W98 | 620 | 717 | 106.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SHLDON - STONYCR 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 106.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SHLDON - STONYCR 230 | 620 | 717 | 106.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ERIE E - 4 MILE 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 106.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 106.32
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | SB:PA230_R506 | 620 | 717 | 106.06
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | ROBINSON - STOLLRD 65 230 | 620 | 717 | 106.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:STONY230 | 620 | 717 | 106.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - BECK PA27 230 | 620 | 717 | 105.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - BECK PA27 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 105.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | S:AVOCA | 620 | 717 | 105.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | CANDQUA - STNYRDG 68A 230 | 620 | 717 | 105.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:STONYRIDGE | 620 | 717 | 105.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DUNKIRK - SRIPL 68 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 105.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:OSWE_R955 | 620 | 717 | 105.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN:OSWEGO 5 | 620 | 717 | 105.72
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 105.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SRIPL - ERIE E 69 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 105.71
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:PA230_R506 | 620 | 717 | 105.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:OSWE_R965 | 620 | 717 | 105.69
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | STOLLRD - GARDENVILL 66 230 | 620 | 717 | 105.55
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3430 | 620 | 717 | 105.55
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | SB:PA230_R506 | 620 | 717 | 105.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:9MIPT1 | 620 | 717 | 105.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT4 | 620 | 717 | 105.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:OSWE_R925 | 620 | 717 | 105.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN:OSWEGO 6 | 620 | 717 | 105.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:OSWE_R935 | 620 | 717 | 105.3
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R506 | 620 | 717 | 105.25
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCWC/NWES | SB:PA230_R506 | 620 | 717 | 105.22
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:MBWC/NWES | SB:PA230_R506 | 620 | 717 | 105.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:FITZPATR | 620 | 717 | 105.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:9MIPT1 | T:62&PA27 | 620 | 717 | 105.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:MLS3&OMS | 620 | 717 | 105.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SIN:250 | 620 | 717 | 105.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:MILLST3 | 620 | 717 | 105.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STNYRDG - HILLSIDE 68B 230 | T:62&PA27 | 620 | 717 | 104.99
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3430 | 620 | 717 | 104.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | ERIE E - 4 MILE 230 | 620 | 717 | 104.91
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 104.86
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:255_345B202 | 620 | 717 | 104.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - FARMVLY | T:62&PA27 | 620 | 717 | 104.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 73 230 | T:62&PA27 | 620 | 717 | 104.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 74 230 | T:62&PA27 | 620 | 717 | 104.8
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SOMERSET - NEWROCH 1 345 | 620 | 717 | 104.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:NIAG345_3008 | 620 | 717 | 104.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | T:62&PA27 | 620 | 717 | 104.64
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT4 | 620 | 717 | 104.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:SEABROOK | 620 | 717 | 104.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:SEAB&OMS | 620 | 717 | 104.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - ELM 70 230 | T:62&PA27 | 620 | 717 | 104.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 104.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | STONYCR - WTHRS 230 | 620 | 717 | 104.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MEYER - CANDQUA 60 230 | T:62&PA27 | 620 | 717 | 104.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:EESR/NWES | 620 | 717 | 104.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | DUNKIRK - SRIPL 68 230 | 620 | 717 | 104.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:SRIPLEY | 620 | 717 | 104.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SRIPL - ERIE E 69 230 | 620 | 717 | 104.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 7-9 | T:62&PA27 | 620 | 717 | 103.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 10-12 | T:62&PA27 | 620 | 717 | 103.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 1-3 | T:62&PA27 | 620 | 717 | 103.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 4-6 | T:62&PA27 | 620 | 717 | 103.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MARC_765_7402 | 620 | 717 | 103.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MSU1_7202>7214>7208>7214 | 620 | 717 | 103.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | HQ-NY 765 | 620 | 717 | 103.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - WTRCR 31 345 | T:62&PA27 | 620 | 717 | 103.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:GINNA | 620 | 717 | 103.84
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | SB:PA230_R506 | 620 | 717 | 103.82
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCMB/NWES | SB:PA230_R506 | 620 | 717 | 103.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SANDY_DC | 620 | 717 | 103.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SANDY_DC&OMS | 620 | 717 | 103.76
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:GARD230_T7-12 | 620 | 717 | 103.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MASS_765_7102 | 620 | 717 | 103.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:MASS_765_7108 | 620 | 717 | 103.73
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R506 | 620 | 717 | 103.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | NIAGARA - PACKARD 62 230 | 620 | 717 | 103.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:WTHERS230 | 620 | 717 | 103.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 103.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCWC/NWES | NIAGARA - PACKARD 62 230 | 620 | 717 | 103.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:MBWC/NWES | NIAGARA - PACKARD 62 230 | 620 | 717 | 103.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:BRUCE5 | 620 | 717 | 103.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | B:DUNKG4 | 620 | 717 | 103.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - BECK_TSA 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 103.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - BECK_TSB 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 103.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | T:62&PA27 | 620 | 717 | 103.36
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:KINTIGH | SB:PA230_R506 | 620 | 717 | 103.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - BECK_TSA 345 | 620 | 717 | 103.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - BECK_TSB 345 | 620 | 717 | 103.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:GINNA | T:62&PA27 | 620 | 717 | 103.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 11 | NIAGARA - PACKARD 62 230 | 620 | 717 | 103.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 12 | NIAGARA - PACKARD 62 230 | 620 | 717 | 103.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 13 | NIAGARA - PACKARD 62 230 | 620 | 717 | 103.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 8 | NIAGARA - PACKARD 62 230 | 620 | 717 | 103.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 9 | NIAGARA - PACKARD 62 230 | 620 | 717 | 103.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 10 | NIAGARA - PACKARD 62 230 | 620 | 717 | 103.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SHLDON - STONYCR 230 | T:62&PA27 | 620 | 717 | 103.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | T:62&PA27 | 620 | 717 | 102.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:DKSR/WRFL | 620 | 717 | 102.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:EESR/WF/NWES | 620 | 717 | 102.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ERIE E - 4 MILE 230 | T:62&PA27 | 620 | 717 | 102.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | R:EESR/WRFL | 620 | 717 | 102.85
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:62&PA27 | 620 | 717 | 102.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | G:DARLIN1 | 620 | 717 | 102.81
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:62&PA27 | 620 | 717 | 102.79
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R506 | 620 | 717 | 102.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:73&74 | 620 | 717 | 102.7
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | SB:PA230_R506 | 620 | 717 | 102.6
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R506 | 620 | 717 | 102.5
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:68&160 | 620 | 717 | 102.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCMB/NWES | NIAGARA - PACKARD 62 230 | 620 | 717 | 102.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DUNKIRK - SRIPL 68 230 | T:62&PA27 | 620 | 717 | 102.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SRIPL - ERIE E 69 230 | T:62&PA27 | 620 | 717 | 102.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | NIAGARA - PACKARD 62 230 | 620 | 717 | 102.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | NIAGARA - PACKARD 62 230 | 620 | 717 | 102.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:KINTIGH | NIAGARA - PACKARD 62 230 | 620 | 717 | 102.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:DUNK230_R1312 | 620 | 717 | 102.06
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:62&PA27 | 620 | 717 | 101.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | PACKARD 230/115 3TR | 620 | 717 | 101.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | NIAGARA - PACKARD 62 230 | 620 | 717 | 101.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | GEN:9 MI PT2 | 620 | 717 | 101.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:SCRIBA_R230 | 620 | 717 | 101.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:SCRIBA_R925 | 620 | 717 | 101.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | NIAGARA - PACKARD 62 230 | 620 | 717 | 101.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | WTHRS - MEYER 230 | 620 | 717 | 101.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | B:MEYER | 620 | 717 | 101.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | T:62&PA27 | 620 | 717 | 101.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3430 | 620 | 717 | 100.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | B:PACKT4 | 620 | 717 | 100.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R3430 | 620 | 717 | 100.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | T:62&PA27 | 620 | 717 | 100.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | T:62&PA27 | 620 | 717 | 100.23
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:62&PA27 | 620 | 717 | 100.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCWC/NWES | T:62&PA27 | 620 | 717 | 100.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:MBWC/NWES | T:62&PA27 | 620 | 717 | 100.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT4 | 620 | 717 | 100.11
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 Max |  |  |  |  | 165.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | T:61&64 | 620 | 717 | 163.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | T:61&64 | 620 | 717 | 152.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 1TR | T:61&64 | 620 | 717 | 149.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | T:61&64 | 620 | 717 | 147.8
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | T:61&64 | 620 | 717 | 142.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | T:61&191 | 620 | 717 | 142.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 140
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | BECK - PACKARD BP76 230 | 620 | 717 | 139.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 230 | SB:PA230_R304 | 620 | 717 | 138.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:PA27&BP76 | 620 | 717 | 138.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LFYTE - CLARKCRNS 36A 345 | T:61&64 | 620 | 717 | 138.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - CLARKCRNS 36B 345 | T:61&64 | 620 | 717 | 136.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 2TR | T:61&64 | 620 | 717 | 136.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - KINTIGH 345 | T:61&64 | 620 | 717 | 135.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 4TR | T:61&64 | 620 | 717 | 134.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-FV_37&W-F_171 | T:61&64 | 620 | 717 | 134.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - HOMERCTY | T:61&64 | 620 | 717 | 134.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LOCKPORT | T:61&64 | 620 | 717 | 133.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 230 | T:61&191 | 620 | 717 | 133.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS1 | T:61&64 | 620 | 717 | 133.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R304 | 620 | 717 | 133.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 4 | T:61&64 | 620 | 717 | 133.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 5 | T:61&64 | 620 | 717 | 133.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 6 | T:61&64 | 620 | 717 | 133.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 7 | T:61&64 | 620 | 717 | 133.2
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | T:61&64 | 620 | 717 | 133.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:INDEK-OL | T:61&64 | 620 | 717 | 132.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 1 | T:61&64 | 620 | 717 | 132.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 2 | T:61&64 | 620 | 717 | 132.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 3 | T:61&64 | 620 | 717 | 132.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | T:61&64 | 620 | 717 | 132.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:JAMESGN7 | T:61&64 | 620 | 717 | 132.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 3TR | T:61&64 | 620 | 717 | 132.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 5TR | T:61&64 | 620 | 717 | 132.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 13 345 | T:61&64 | 620 | 717 | 132.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 5TR | T:61&64 | 620 | 717 | 132.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-SR_37&W-F_171 | T:61&64 | 620 | 717 | 132.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:FV-5M_37&W-F_171 | T:61&64 | 620 | 717 | 132.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - 5MILE 345 | T:61&64 | 620 | 717 | 131.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R304 | 620 | 717 | 131.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R304 | 620 | 717 | 131.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - WATERCURE 69 230 | T:61&64 | 620 | 717 | 131.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - ETWANDA 70 230 | T:61&64 | 620 | 717 | 131.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | T:61&64 | 620 | 717 | 131.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DEWITT3 - LAFAYTTE 345 | T:61&64 | 620 | 717 | 131.77
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 5 MILE - STOLLE 37A 345 | T:61&64 | 620 | 717 | 131.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:5M-SR_37&W-F_171 | T:61&64 | 620 | 717 | 131.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HOMERCTY - STOLLRD 37 345 | T:61&64 | 620 | 717 | 131.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS2 | T:61&64 | 620 | 717 | 131.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 230 | T:61&64 | 620 | 717 | 131.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 131.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-1 345 | T:61&64 | 620 | 717 | 131.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-2 345 | T:61&64 | 620 | 717 | 131.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:DUPONT46 | T:61&64 | 620 | 717 | 131.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - SHLDON 67 230 | T:61&64 | 620 | 717 | 131.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:OXBOWNUG | T:61&64 | 620 | 717 | 131.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - EDIC 2-15 345 | T:61&64 | 620 | 717 | 131.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL - CLAY PC-2 345 | T:61&64 | 620 | 717 | 131.55
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE 230/115 3TR | T:61&64 | 620 | 717 | 131.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL - CLAY PC-1 345 | T:61&64 | 620 | 717 | 131.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 2TR | T:61&64 | 620 | 717 | 131.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROBI230 | 620 | 717 | 131.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA - ROBINSON 64 230 | 620 | 717 | 130.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:OSWEGO 6 | T:61&64 | 620 | 717 | 129.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE 230/115 4TR | T:61&64 | 620 | 717 | 129.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:FITZPATR | T:61&64 | 620 | 717 | 129.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 73 230 | T:61&64 | 620 | 717 | 129.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 74 230 | T:61&64 | 620 | 717 | 129.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - FARMVLY | T:61&64 | 620 | 717 | 129.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:9MIPT1 | T:61&64 | 620 | 717 | 129.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - ELM 70 230 | T:61&64 | 620 | 717 | 129.57
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | SB:PA230_R304 | 620 | 717 | 129.33
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | T:61&64 | 620 | 717 | 129.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STNYRDG - HILLSIDE 68B 230 | T:61&64 | 620 | 717 | 129.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 4TR | T:61&64 | 620 | 717 | 128.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 7-9 | T:61&64 | 620 | 717 | 128.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 10-12 | T:61&64 | 620 | 717 | 128.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 1-3 | T:61&64 | 620 | 717 | 128.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 4-6 | T:61&64 | 620 | 717 | 128.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - WTRCR 31 345 | T:61&64 | 620 | 717 | 128.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK PA27 230 | T:61&64 | 620 | 717 | 127.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MEYER - CANDQUA 60 230 | T:61&64 | 620 | 717 | 127.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ERIE E - 4 MILE 230 | T:61&64 | 620 | 717 | 127.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDL - FRASER 32 345 | T:61&64 | 620 | 717 | 127.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:GINNA | T:61&64 | 620 | 717 | 127.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SHLDON - STONYCR 230 | T:61&64 | 620 | 717 | 127.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DUNKIRK - SRIPL 68 230 | T:61&64 | 620 | 717 | 127.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SRIPL - ERIE E 69 230 | T:61&64 | 620 | 717 | 127.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 1TR | SB:PA230_R304 | 620 | 717 | 126.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | T:61&191 | 620 | 717 | 125.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | T:61&191 | 620 | 717 | 125.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CANDQUA - STNYRDG 68A 230 | T:61&64 | 620 | 717 | 125.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | T:61&191 | 620 | 717 | 124.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK_TSA 345 | T:61&64 | 620 | 717 | 124.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK_TSB 345 | T:61&64 | 620 | 717 | 124.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-WC_30&W-F_171 | T:61&64 | 620 | 717 | 124.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WTRCR - MAINSBRG 30A 345 | T:61&64 | 620 | 717 | 124.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HCWC/NWES | T:61&64 | 620 | 717 | 124.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:MBWC/NWES | T:61&64 | 620 | 717 | 124.51
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | T:61&191 | 620 | 717 | 124.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:NIAW230_2014 | 620 | 717 | 124.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 123.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | B:STOLE230 | 620 | 717 | 123.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STONYCR - WTHRS 230 | T:61&64 | 620 | 717 | 123.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:NIAG345_3108 | 620 | 717 | 123.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 123.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HCMB/NWES | T:61&64 | 620 | 717 | 123.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-MB_30&W-F_171 | T:61&64 | 620 | 717 | 123.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 11 | T:61&64 | 620 | 717 | 123.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 12 | T:61&64 | 620 | 717 | 123.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 13 | T:61&64 | 620 | 717 | 123.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 8 | T:61&64 | 620 | 717 | 123.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 9 | T:61&64 | 620 | 717 | 123.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MAINSBRG - HOMERCITY 30B 345 | T:61&64 | 620 | 717 | 123.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 10 | T:61&64 | 620 | 717 | 123.03
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 230 | SB:PA230_R304 | 620 | 717 | 122.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:255_345B302 | 620 | 717 | 122.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | ROBINSON - STOLLRD 65 230 | 620 | 717 | 122.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAG - NEWROCH 1 345 | 620 | 717 | 122.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 122.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | T:61&191 | 620 | 717 | 122.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | STOLLRD - GARDENVILL 66 230 | 620 | 717 | 122.39
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 1TR | T:61&64 | 620 | 717 | 122.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 3TR | T:61&64 | 620 | 717 | 122.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R304 | 620 | 717 | 121.76
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 121.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:KINTIGH | T:61&64 | 620 | 717 | 121.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 1TR | T:61&191 | 620 | 717 | 121.17
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | BECK - PACKARD BP76 230 | 620 | 717 | 120.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R304 | 620 | 717 | 120.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - PACKARD 77 230 | T:61&64 | 620 | 717 | 120.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:255_345B202 | 620 | 717 | 120.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SOMERSET - NEWROCH 1 345 | 620 | 717 | 120.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - PACKARD 78 230 | T:61&64 | 620 | 717 | 120.69
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LFYTE - CLARKCRNS 36A 345 | T:61&64 | 620 | 717 | 120.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 120.5
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:GARD230_T7-12 | 620 | 717 | 120.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 1TR | NIAGARA - PACKARD 61 230 | 620 | 717 | 120.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA 230/115 1TR | 620 | 717 | 120.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - GARDENVILL 80 230 | T:61&64 | 620 | 717 | 119.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 2TR | SB:PA230_R304 | 620 | 717 | 119.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - GARDENVILL 79 230 | T:61&64 | 620 | 717 | 119.74
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:PA27&BP76 | 620 | 717 | 119.71
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - CLARKCRNS 36B 345 | T:61&64 | 620 | 717 | 119.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 1 | SB:PA230_R304 | 620 | 717 | 119.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 2 | SB:PA230_R304 | 620 | 717 | 119.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 3 | SB:PA230_R304 | 620 | 717 | 119.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WTHRS - MEYER 230 | T:61&64 | 620 | 717 | 119.03
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R304 | 620 | 717 | 118.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-FV_37&W-F_171 | SB:PA230_R304 | 620 | 717 | 118.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - HOMERCTY | SB:PA230_R304 | 620 | 717 | 118.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - KINTIGH 345 | SB:PA230_R304 | 620 | 717 | 118.57
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R304 | 620 | 717 | 117.84
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R304 | 620 | 717 | 117.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS1 | SB:PA230_R304 | 620 | 717 | 117.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:INDEK-OL | SB:PA230_R304 | 620 | 717 | 117.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-SR_37&W-F_171 | SB:PA230_R304 | 620 | 717 | 117.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:FV-5M_37&W-F_171 | SB:PA230_R304 | 620 | 717 | 117.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LFYTE - CLARKCRNS 36A 345 | T:61&191 | 620 | 717 | 117.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:JAMESGN7 | SB:PA230_R304 | 620 | 717 | 116.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - 5MILE 345 | SB:PA230_R304 | 620 | 717 | 116.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 13 345 | SB:PA230_R304 | 620 | 717 | 116.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:5M-SR_37&W-F_171 | SB:PA230_R304 | 620 | 717 | 116.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:OXBOWNUG | SB:PA230_R304 | 620 | 717 | 116.39
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - KINTIGH 345 | T:61&64 | 620 | 717 | 116.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LOCKPORT | SB:PA230_R304 | 620 | 717 | 116.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 5 MILE - STOLLE 37A 345 | SB:PA230_R304 | 620 | 717 | 116.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:UDG-184 | SB:PA230_R304 | 620 | 717 | 116.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R304 | 620 | 717 | 116.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 4 | SB:PA230_R304 | 620 | 717 | 116.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 5 | SB:PA230_R304 | 620 | 717 | 116.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 6 | SB:PA230_R304 | 620 | 717 | 116.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - CLARKCRNS 36B 345 | T:61&191 | 620 | 717 | 116.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 7 | SB:PA230_R304 | 620 | 717 | 116.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 5TR | SB:PA230_R304 | 620 | 717 | 116.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:DUPONT46 | SB:PA230_R304 | 620 | 717 | 116.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS2 | SB:PA230_R304 | 620 | 717 | 116.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - PACKARD 78 230 | SB:PA230_R304 | 620 | 717 | 116.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R304 | 620 | 717 | 116.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R304 | 620 | 717 | 116.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R304 | 620 | 717 | 116.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - EDIC 2-15 345 | SB:PA230_R304 | 620 | 717 | 115.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-1 345 | SB:PA230_R304 | 620 | 717 | 115.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-2 345 | SB:PA230_R304 | 620 | 717 | 115.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | SB:PA230_R3230 | 620 | 717 | 115.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:40&41 | 620 | 717 | 115.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | B:PACKT3 | 620 | 717 | 115.68
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-FV_37&W-F_171 | T:61&64 | 620 | 717 | 115.57
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - HOMERCTY | T:61&64 | 620 | 717 | 115.46
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 4TR | T:61&64 | 620 | 717 | 115.45
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 4 | T:61&64 | 620 | 717 | 115.31
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 5 | T:61&64 | 620 | 717 | 115.31
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 6 | T:61&64 | 620 | 717 | 115.31
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 7 | T:61&64 | 620 | 717 | 115.29
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LOCKPORT | T:61&64 | 620 | 717 | 115.27
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 230 | T:61&191 | 620 | 717 | 115.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:41&33 | 620 | 717 | 115.11
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | SB:PA230_R304 | 620 | 717 | 114.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LFYTE - CLARKCRNS 36A 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 114.93
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 4TR | T:61&64 | 620 | 717 | 114.57
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 13 345 | T:61&64 | 620 | 717 | 114.57
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS1 | T:61&64 | 620 | 717 | 114.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:34&42 | 620 | 717 | 114.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL 230/115 M6TR | SB:PA230_R304 | 620 | 717 | 114.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL 230/115 M8TR | SB:PA230_R304 | 620 | 717 | 114.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:9MIPT1 | SB:PA230_R304 | 620 | 717 | 114.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-FV_37&W-F_171 | T:61&191 | 620 | 717 | 114.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | FARMVLY - HOMERCTY | 620 | 717 | 114.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - HOMERCTY | T:61&191 | 620 | 717 | 114.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - CLARKCRNS 36B 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 114.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - FARMVLY | SB:PA230_R304 | 620 | 717 | 114.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:HC-FV_37&W-F_171 | 620 | 717 | 114.15
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:INDEK-OL | T:61&64 | 620 | 717 | 114.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - KINTIGH 345 | T:61&191 | 620 | 717 | 114.11
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 1 | T:61&64 | 620 | 717 | 114.09
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 2 | T:61&64 | 620 | 717 | 114.09
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 3 | T:61&64 | 620 | 717 | 114.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 2TR | T:61&191 | 620 | 717 | 114.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R304 | 620 | 717 | 114.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R304 | 620 | 717 | 114.02
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DEWITT3 - LAFAYTTE 345 | T:61&64 | 620 | 717 | 114.01
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | T:61&64 | 620 | 717 | 113.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 4TR | T:61&191 | 620 | 717 | 113.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R304 | 620 | 717 | 113.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 7-9 | SB:PA230_R304 | 620 | 717 | 113.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 10-12 | SB:PA230_R304 | 620 | 717 | 113.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 1-3 | SB:PA230_R304 | 620 | 717 | 113.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 4-6 | SB:PA230_R304 | 620 | 717 | 113.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-2 345 | T:61&64 | 620 | 717 | 113.88
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - EDIC 2-15 345 | T:61&64 | 620 | 717 | 113.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - ELM 70 230 | SB:PA230_R304 | 620 | 717 | 113.74
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL - CLAY PC-1 345 | T:61&64 | 620 | 717 | 113.71
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL - CLAY PC-2 345 | T:61&64 | 620 | 717 | 113.71
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:JAMESGN7 | T:61&64 | 620 | 717 | 113.71
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 5TR | T:61&64 | 620 | 717 | 113.57
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-SR_37&W-F_171 | T:61&64 | 620 | 717 | 113.56
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:FV-5M_37&W-F_171 | T:61&64 | 620 | 717 | 113.56
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:5M-SR_37&W-F_171 | T:61&64 | 620 | 717 | 113.54
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 5 MILE - STOLLE 37A 345 | T:61&64 | 620 | 717 | 113.53
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HOMERCTY - STOLLRD 37 345 | T:61&64 | 620 | 717 | 113.53
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | EDIC - FITZ 345 | T:61&64 | 620 | 717 | 113.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS1 | T:61&191 | 620 | 717 | 113.42
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | T:61&64 | 620 | 717 | 113.41
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OS - EL - LFYTE 17 345 | T:61&64 | 620 | 717 | 113.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LAPER_345_1 | 620 | 717 | 113.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LAPER_345_2 | 620 | 717 | 113.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | LFYTE - CLARKCRNS 36A 345 | 620 | 717 | 113.36
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 3TR | T:61&64 | 620 | 717 | 113.34
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 5TR | T:61&64 | 620 | 717 | 113.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LAFAYETT | 620 | 717 | 113.3
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - 5MILE 345 | T:61&64 | 620 | 717 | 113.29
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL 345/115 1TR | T:61&64 | 620 | 717 | 113.29
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL 345/115 2TR | T:61&64 | 620 | 717 | 113.29
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL 345/115 3TR | T:61&64 | 620 | 717 | 113.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LAFA_ELB | 620 | 717 | 113.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 1 | T:61&191 | 620 | 717 | 113.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 2 | T:61&191 | 620 | 717 | 113.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 3 | T:61&191 | 620 | 717 | 113.25
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | VOL - MARCY 19 345 | T:61&64 | 620 | 717 | 113.2
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY 345/115 1TR | T:61&64 | 620 | 717 | 113.14
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY 345/115 2TR | T:61&64 | 620 | 717 | 113.14
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - WATERCURE 69 230 | T:61&64 | 620 | 717 | 113.13
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - ETWANDA 70 230 | T:61&64 | 620 | 717 | 113.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MEYER - CANDQUA 60 230 | SB:PA230_R304 | 620 | 717 | 113.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:INDEK-OL | T:61&191 | 620 | 717 | 113.05
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 3 115 | T:61&64 | 620 | 717 | 113.04
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - TEAL 10 115 | T:61&64 | 620 | 717 | 113.04
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:DUPONT46 | T:61&64 | 620 | 717 | 113.03
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - LM 14 115 | T:61&64 | 620 | 717 | 113.02
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - TEAL 11 115 | T:61&64 | 620 | 717 | 113.02
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 5 115 | T:61&64 | 620 | 717 | 113
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LHH - CLAY 7 115 | T:61&64 | 620 | 717 | 113
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - WOOD 17 115 | T:61&64 | 620 | 717 | 113
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS2 | T:61&64 | 620 | 717 | 113
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FUL - CLAY 4 115 | T:61&64 | 620 | 717 | 112.98
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - VOL 21 345 | T:61&64 | 620 | 717 | 112.98
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - VOL 20 345 | T:61&64 | 620 | 717 | 112.97
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA 345/115 1TR | T:61&64 | 620 | 717 | 112.97
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA 345/115 2TR | T:61&64 | 620 | 717 | 112.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:NIAG345_3308 | 620 | 717 | 112.97
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OSW 345/115 1TR | T:61&64 | 620 | 717 | 112.96
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - 9MI1 9 345 | T:61&64 | 620 | 717 | 112.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 4 | T:61&191 | 620 | 717 | 112.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 5 | T:61&191 | 620 | 717 | 112.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 6 | T:61&191 | 620 | 717 | 112.95
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OSW - VOL 11 345 | T:61&64 | 620 | 717 | 112.94
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OSW - VOL 12 345 | T:61&64 | 620 | 717 | 112.94
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - IND 25 345 | T:61&64 | 620 | 717 | 112.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 7 | T:61&191 | 620 | 717 | 112.94
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-1 345 | T:61&64 | 620 | 717 | 112.92
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | EDIC - MRCY ue 1-7 345 | T:61&64 | 620 | 717 | 112.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - WTRCR 31 345 | SB:PA230_R304 | 620 | 717 | 112.92
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - FITZ 10 345 | T:61&64 | 620 | 717 | 112.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:OXBOWNUG | T:61&64 | 620 | 717 | 112.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 112.88
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 230 | T:61&64 | 620 | 717 | 112.88
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROBI230 | 620 | 717 | 112.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LAPER_345_4 | 620 | 717 | 112.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LAPER_345_3 | 620 | 717 | 112.85
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE 230/115 3TR | T:61&64 | 620 | 717 | 112.82
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 2TR | T:61&64 | 620 | 717 | 112.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:OAKD345_B5 | 620 | 717 | 112.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:OAKD345_B6 | 620 | 717 | 112.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | OAKDLE - CLARKCRNS 36B 345 | 620 | 717 | 112.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 4TR | SB:PA230_R304 | 620 | 717 | 112.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:JAMESGN7 | T:61&191 | 620 | 717 | 112.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ERIE E - 4 MILE 230 | SB:PA230_R304 | 620 | 717 | 112.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 13 345 | T:61&191 | 620 | 717 | 112.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDL - FRASER 32 345 | SB:PA230_R304 | 620 | 717 | 112.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:COOP345_42-4182 | 620 | 717 | 112.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:31&41 | 620 | 717 | 112.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:GINNA | SB:PA230_R304 | 620 | 717 | 112.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 3TR | T:61&191 | 620 | 717 | 112.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 5TR | T:61&191 | 620 | 717 | 112.19
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA - ROBINSON 64 230 | 620 | 717 | 112.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:5MILE_B | 620 | 717 | 112.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA 230/115 2TR | 620 | 717 | 112.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SHLDON - STONYCR 230 | SB:PA230_R304 | 620 | 717 | 112.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:EDIC345_R915 | 620 | 717 | 112.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA 345/230 4TR | 620 | 717 | 112.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-FV_37&W-F_171 | NIAGARA - PACKARD 61 230 | 620 | 717 | 112.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - HOMERCTY | NIAGARA - PACKARD 61 230 | 620 | 717 | 112.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - KINTIGH 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 112.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LOCKPORT | T:61&191 | 620 | 717 | 112.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-SR_37&W-F_171 | T:61&191 | 620 | 717 | 112.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:FV-5M_37&W-F_171 | T:61&191 | 620 | 717 | 112.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAG - KINTIGH 345 | 620 | 717 | 112.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 5TR | T:61&191 | 620 | 717 | 112.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS2 | T:61&191 | 620 | 717 | 112
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 2TR | NIAGARA - PACKARD 61 230 | 620 | 717 | 111.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - 5MILE 345 | T:61&191 | 620 | 717 | 111.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:OXBOWNUG | T:61&191 | 620 | 717 | 111.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DEWITT3 - LAFAYTTE 345 | T:61&191 | 620 | 717 | 111.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:DUPONT46 | T:61&191 | 620 | 717 | 111.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 4TR | NIAGARA - PACKARD 61 230 | 620 | 717 | 111.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - WATERCURE 69 230 | T:61&191 | 620 | 717 | 111.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - ETWANDA 70 230 | T:61&191 | 620 | 717 | 111.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 5 MILE - STOLLE 37A 345 | T:61&191 | 620 | 717 | 111.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HOMERCTY - STOLLRD 37 345 | T:61&191 | 620 | 717 | 111.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:COOP345_4182 | 620 | 717 | 111.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:MP11&41 | 620 | 717 | 111.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MARC345_3202 | 620 | 717 | 111.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:5M-SR_37&W-F_171 | T:61&191 | 620 | 717 | 111.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DUNKIRK - SRIPL 68 230 | SB:PA230_R304 | 620 | 717 | 111.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:UDG-184 | T:61&191 | 620 | 717 | 111.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MARC345_3208 | 620 | 717 | 111.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - EDIC 2-15 345 | T:61&191 | 620 | 717 | 111.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | MARCY - COOPERS 345 SC | 620 | 717 | 111.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SRIPL - ERIE E 69 230 | SB:PA230_R304 | 620 | 717 | 111.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:77&76 | 620 | 717 | 111.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:EDIC345_R935 | 620 | 717 | 111.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:30&40 | 620 | 717 | 111.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:EDIC345_R400 | 620 | 717 | 111.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R304 | 620 | 717 | 111.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MARC345_3108 | 620 | 717 | 111.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS1 | NIAGARA - PACKARD 61 230 | 620 | 717 | 111.3
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE 230/115 4TR | T:61&64 | 620 | 717 | 111.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROCH_3414 | 620 | 717 | 111.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROCH_3514 | 620 | 717 | 111.22
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:FITZPATR | T:61&64 | 620 | 717 | 111.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 4 | NIAGARA - PACKARD 61 230 | 620 | 717 | 111.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 5 | NIAGARA - PACKARD 61 230 | 620 | 717 | 111.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 6 | NIAGARA - PACKARD 61 230 | 620 | 717 | 111.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | EDIC - FRASER 345 SC | 620 | 717 | 111.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:FRAS345_B1-4062 | 620 | 717 | 111.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 7 | NIAGARA - PACKARD 61 230 | 620 | 717 | 111.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 1 | NIAGARA - PACKARD 61 230 | 620 | 717 | 111.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 2 | NIAGARA - PACKARD 61 230 | 620 | 717 | 111.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 3 | NIAGARA - PACKARD 61 230 | 620 | 717 | 111.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:FRAS345_40-B262 | 620 | 717 | 111.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROCH_2T8082 | 620 | 717 | 111.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:69J&70K | 620 | 717 | 111.07
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 73 230 | T:61&64 | 620 | 717 | 110.98
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 74 230 | T:61&64 | 620 | 717 | 110.97
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - ELM 70 230 | T:61&64 | 620 | 717 | 110.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:W89&W90 | 620 | 717 | 110.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROCH_34XC | 620 | 717 | 110.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:INDEK-OL | NIAGARA - PACKARD 61 230 | 620 | 717 | 110.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SIN:170 | 620 | 717 | 110.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SIN:180 | 620 | 717 | 110.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | B:N.S._99 | 620 | 717 | 110.89
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:9MIPT1 | T:61&64 | 620 | 717 | 110.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | B:N.S._77 | 620 | 717 | 110.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:EDIC345_R140 | 620 | 717 | 110.83
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - FARMVLY | T:61&64 | 620 | 717 | 110.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SIN:160 | 620 | 717 | 110.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SIN:150 | 620 | 717 | 110.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:F38&F39 | 620 | 717 | 110.77
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:CLAY345_R935 | 620 | 717 | 110.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:MP12&18 | 620 | 717 | 110.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:CLAY345_R945 | 620 | 717 | 110.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SIN:90 | 620 | 717 | 110.68
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - WTRCR 31 345 | T:61&64 | 620 | 717 | 110.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | MARCY - N.SCOT99 I8 345 | 620 | 717 | 110.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MARC345_3314 | 620 | 717 | 110.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MARC345_3308 | 620 | 717 | 110.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 11 | SB:PA230_R304 | 620 | 717 | 110.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 12 | SB:PA230_R304 | 620 | 717 | 110.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 13 | SB:PA230_R304 | 620 | 717 | 110.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 8 | SB:PA230_R304 | 620 | 717 | 110.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 9 | SB:PA230_R304 | 620 | 717 | 110.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:5MILE | 620 | 717 | 110.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 10 | SB:PA230_R304 | 620 | 717 | 110.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROCK345_376512 | 620 | 717 | 110.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:F30&F31 | 620 | 717 | 110.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | EDIC - N.SCOT77 I4 345 | 620 | 717 | 110.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROCK345_31153 | 620 | 717 | 110.55
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:JAMESGN7 | NIAGARA - PACKARD 61 230 | 620 | 717 | 110.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:CLAY345_R150 | 620 | 717 | 110.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:CLAY345_R160 | 620 | 717 | 110.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:PV345_RNS5 | 620 | 717 | 110.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:PV345_RNS4 | 620 | 717 | 110.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:EDIC345_R110 | 620 | 717 | 110.4
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STNYRDG - HILLSIDE 68B 230 | T:61&64 | 620 | 717 | 110.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROCK345_3456 | 620 | 717 | 110.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LEEDS345_R9293 | 620 | 717 | 110.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:EDIC345_R150 | 620 | 717 | 110.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:EDIC345_R160 | 620 | 717 | 110.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:COOP345_34-B382 | 620 | 717 | 110.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:COOP345_B2-3482 | 620 | 717 | 110.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | COOPERC - ROCKT CMT/MTR-34 345 | 620 | 717 | 110.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | HURLEY - ROCKT CMT/MTR-34 345 | 620 | 717 | 110.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | CLAY - EDIC 1-16 345 | 620 | 717 | 110.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | CLAY - EDIC 2-15 345 | 620 | 717 | 110.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | CLAY - EDIC 2-15 345 | 620 | 717 | 110.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:EDIC345_R10 | 620 | 717 | 110.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:PANN345_3908 | 620 | 717 | 110.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:9MIPT1 | T:61&191 | 620 | 717 | 110.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:PANN345_3808 | 620 | 717 | 110.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MARC345_3102 | 620 | 717 | 110.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA 345/230 5TR | 620 | 717 | 110.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA 345/230 3TR | 620 | 717 | 110.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 13 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 110.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | FARMVLY - 5MILE 345 | 620 | 717 | 110.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | EDIC - FITZ 345 | 620 | 717 | 110.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | FITZ - EDIC FEI 345 | 620 | 717 | 110.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | VOLNEY - MARCY I9 345 | 620 | 717 | 110.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | VOL - MARCY 19 345 | 620 | 717 | 110.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:VOLN_R925 | 620 | 717 | 110.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:FV-5M_37&W-F_171 | 620 | 717 | 110.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:HC-SR_37&W-F_171 | 620 | 717 | 110.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STNYRDG - HILLSIDE 68B 230 | T:61&191 | 620 | 717 | 110.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROCK345_4255 | 620 | 717 | 110.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:DUNW345_3 | 620 | 717 | 110.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | ROCH 345/115 5TR | 620 | 717 | 110.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:COOP345_B2-4282 | 620 | 717 | 110.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | COOPERC - ROCKT CCRT-42 345 | 620 | 717 | 110.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | COOPERC - ROCKT CCRT-42 345 | 620 | 717 | 110.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 3TR | NIAGARA - PACKARD 61 230 | 620 | 717 | 110.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 5TR | NIAGARA - PACKARD 61 230 | 620 | 717 | 110.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LEEDS345_R94301 | 620 | 717 | 110.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:DUNW345_8 | 620 | 717 | 110.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LOCKPORT | NIAGARA - PACKARD 61 230 | 620 | 717 | 110.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | CLAY - DEW 13 345 | 620 | 717 | 110.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 4TR | T:61&191 | 620 | 717 | 110.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROCH_1X8082 | 620 | 717 | 110.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 73 230 | T:61&191 | 620 | 717 | 110.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | LEEDS - PV 92 345 | 620 | 717 | 110.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LEEDS345_R92 | 620 | 717 | 110.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | LEEDS - PV 92 345 | 620 | 717 | 110.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 74 230 | T:61&191 | 620 | 717 | 110.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | ATHENS - PV 91 345 | 620 | 717 | 109.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | ATHENS - PV 91 345 | 620 | 717 | 109.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:COOP345_3382 | 620 | 717 | 109.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - FARMVLY | T:61&191 | 620 | 717 | 109.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:PANN345_3914 | 620 | 717 | 109.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:PANN345_3814 | 620 | 717 | 109.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 5TR | NIAGARA - PACKARD 61 230 | 620 | 717 | 109.97
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDL - FRASER 32 345 | T:61&64 | 620 | 717 | 109.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROCH_3408 | 620 | 717 | 109.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROCH_3508 | 620 | 717 | 109.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:PANN345_3902 | 620 | 717 | 109.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:PANN345_3802 | 620 | 717 | 109.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:DEWI345_R915 | 620 | 717 | 109.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:FRAS345_33-B262 | 620 | 717 | 109.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:DEWI345_R130 | 620 | 717 | 109.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:DEWI345_R220 | 620 | 717 | 109.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:DUNW345_4 | 620 | 717 | 109.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS2 | NIAGARA - PACKARD 61 230 | 620 | 717 | 109.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:FARR345_2W | 620 | 717 | 109.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:COOP345_B2-3382 | 620 | 717 | 109.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | FRASER - COOPERS 345 SC | 620 | 717 | 109.87
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 1-3 | T:61&64 | 620 | 717 | 109.86
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 4-6 | T:61&64 | 620 | 717 | 109.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:DUNW345_6 | 620 | 717 | 109.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:OXBOWNUG | NIAGARA - PACKARD 61 230 | 620 | 717 | 109.85
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 7-9 | T:61&64 | 620 | 717 | 109.84
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 10-12 | T:61&64 | 620 | 717 | 109.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-SR_37&W-F_171 | NIAGARA - PACKARD 61 230 | 620 | 717 | 109.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:FV-5M_37&W-F_171 | NIAGARA - PACKARD 61 230 | 620 | 717 | 109.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - 5MILE 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 109.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DEWITT3 - LAFAYTTE 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 109.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:DUPONT46 | NIAGARA - PACKARD 61 230 | 620 | 717 | 109.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3230 | 620 | 717 | 109.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - WATERCURE 69 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 109.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - ETWANDA 70 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 109.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - ELM 70 230 | T:61&191 | 620 | 717 | 109.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:UDG-184 | NIAGARA - PACKARD 61 230 | 620 | 717 | 109.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - EDIC 2-15 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 109.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 620 | 717 | 109.58
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | T:61&191 | 620 | 717 | 109.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STONYCR - WTHRS 230 | SB:PA230_R304 | 620 | 717 | 109.5
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R304 | 620 | 717 | 109.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 7-9 | T:61&191 | 620 | 717 | 109.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 10-12 | T:61&191 | 620 | 717 | 109.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 1-3 | T:61&191 | 620 | 717 | 109.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 4-6 | T:61&191 | 620 | 717 | 109.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MEYER - CANDQUA 60 230 | T:61&191 | 620 | 717 | 109.28
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 2TR | T:61&64 | 620 | 717 | 109.21
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MEYER - CANDQUA 60 230 | T:61&64 | 620 | 717 | 109.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-WC_30&W-F_171 | SB:PA230_R304 | 620 | 717 | 109.1
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ERIE E - 4 MILE 230 | T:61&64 | 620 | 717 | 109.08
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | T:61&191 | 620 | 717 | 109.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R304 | 620 | 717 | 108.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - WTRCR 31 345 | T:61&191 | 620 | 717 | 108.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HCWC/NWES | SB:PA230_R304 | 620 | 717 | 108.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:MBWC/NWES | SB:PA230_R304 | 620 | 717 | 108.96
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK PA27 230 | T:61&64 | 620 | 717 | 108.84
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:GINNA | T:61&64 | 620 | 717 | 108.78
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R304 | 620 | 717 | 108.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDL - FRASER 32 345 | T:61&191 | 620 | 717 | 108.47
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DUNKIRK - SRIPL 68 230 | T:61&64 | 620 | 717 | 108.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GARDENVILL 230/115 M6TR | 620 | 717 | 108.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GARDENVILL 230/115 M8TR | 620 | 717 | 108.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:OAKD345_B2 | 620 | 717 | 108.4
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SRIPL - ERIE E 69 230 | T:61&64 | 620 | 717 | 108.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:GINNA | T:61&191 | 620 | 717 | 108.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:SHLDN230 | 620 | 717 | 108.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: NRTPTG3 | 620 | 717 | 108.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: NRTPTG4 | 620 | 717 | 108.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: NRTPTG1 | 620 | 717 | 108.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: NRTPTG2 | 620 | 717 | 108.32
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SHLDON - STONYCR 230 | T:61&64 | 620 | 717 | 108.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: SCS AST | 620 | 717 | 108.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:CAITH | 620 | 717 | 108.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: BAYONNE | 620 | 717 | 108.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:GOWANUS_22 | 620 | 717 | 108.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | OAKDLE - WTRCR 31 345 | 620 | 717 | 108.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:OAKD345_B3 | 620 | 717 | 108.25
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | T:61&191 | 620 | 717 | 108.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:72&69 | 620 | 717 | 108.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: POLETTIX | 620 | 717 | 108.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: ATHENS #1 | 620 | 717 | 108.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:9MIPT1 | NIAGARA - PACKARD 61 230 | 620 | 717 | 108.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:W49_3 | 620 | 717 | 108.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:SELKIRK2 | 620 | 717 | 108.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ASTO345_2 | 620 | 717 | 108.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:WATRC345_31-2 | 620 | 717 | 108.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN:NOEND | 620 | 717 | 108.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ASTO345_1 | 620 | 717 | 108.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SHLDON - STONYCR 230 | T:61&191 | 620 | 717 | 108.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MOSE230_2214 | 620 | 717 | 108.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN:MOS17-20 | 620 | 717 | 108.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MOSE230_2224 | 620 | 717 | 108.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MOSE230_2208 | 620 | 717 | 108.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:RMP345_T1500 | 620 | 717 | 108.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MOSE115_1714 | 620 | 717 | 108.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MOSE115_1724 | 620 | 717 | 108.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MOSE115_1514 | 620 | 717 | 108.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MOSE115_1524 | 620 | 717 | 108.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MOSE115_1508 | 620 | 717 | 108.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MOSE230_2524 | 620 | 717 | 108.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MOSE230_2514 | 620 | 717 | 108.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN:MOS21-24 | 620 | 717 | 108.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MOSE230_2508 | 620 | 717 | 108.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | RAMAPO - BRNCHBRG 5018 345 | 620 | 717 | 108.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STNYRDG - HILLSIDE 68B 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 108.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | PACKARD 230/115 4TR | 620 | 717 | 108.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ERIE E - 4 MILE 230 | T:61&191 | 620 | 717 | 108.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:RMP345_1500-2X | 620 | 717 | 108
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CANDQUA - STNYRDG 68A 230 | T:61&191 | 620 | 717 | 108
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | HILLSIDE 230/115 4TR | 620 | 717 | 107.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | B:HILLSIDE | 620 | 717 | 107.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:HILL_B412 | 620 | 717 | 107.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:F21&G23M | 620 | 717 | 107.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: ASTORIS | 620 | 717 | 107.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - FARMVLY | NIAGARA - PACKARD 61 230 | 620 | 717 | 107.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 73 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 107.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 74 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 107.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 4TR | NIAGARA - PACKARD 61 230 | 620 | 717 | 107.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:W49_1 | 620 | 717 | 107.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:RAIN345_8W | 620 | 717 | 107.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:HILL_68-B412 | 620 | 717 | 107.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | STNYRDG - HILLSIDE 68B 230 | 620 | 717 | 107.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: BOWL PT2 | 620 | 717 | 107.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROSE345_30356 | 620 | 717 | 107.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SIN:30 | 620 | 717 | 107.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | BWLN - WHAV -LDN 67 345 | 620 | 717 | 107.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: BOWL PT1 | 620 | 717 | 107.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | HUNTLEY - ELM 70 230 | 620 | 717 | 107.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK PA27 230 | T:61&191 | 620 | 717 | 107.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROSE345_30553 | 620 | 717 | 107.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LADE_4-56-2 | 620 | 717 | 107.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - ELM 70 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 107.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HCMB/NWES | SB:PA230_R304 | 620 | 717 | 107.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LADE_6-56-2 | 620 | 717 | 107.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-MB_30&W-F_171 | SB:PA230_R304 | 620 | 717 | 107.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LADE_1-56-2 | 620 | 717 | 107.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | FARMVLY - FARMVLY | 620 | 717 | 107.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:LADE_3-56-2 | 620 | 717 | 107.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROSE345_31152 | 620 | 717 | 107.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:RAIN345_1W | 620 | 717 | 107.5
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | B:DUNKG3 | 620 | 717 | 107.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: ROSETON2 | 620 | 717 | 107.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROSE345_30551 | 620 | 717 | 107.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GARDENVILL - DUNKIRK 73 230 | 620 | 717 | 107.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: RAVENSWOOD | 620 | 717 | 107.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GARDENVILL - DUNKIRK 74 230 | 620 | 717 | 107.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R304 | 620 | 717 | 107.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:RAIN345_9W | 620 | 717 | 107.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DUNKIRK - SRIPL 68 230 | T:61&191 | 620 | 717 | 107.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SRIPL - ERIE E 69 230 | T:61&191 | 620 | 717 | 107.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:KINTIGH | SB:PA230_R304 | 620 | 717 | 107.35
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 1TR | SB:PA230_R304 | 620 | 717 | 107.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: BESICORP | 620 | 717 | 107.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:EMPIRE | 620 | 717 | 107.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: ROSETON1 | 620 | 717 | 107.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 7-9 | NIAGARA - PACKARD 61 230 | 620 | 717 | 107.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 10-12 | NIAGARA - PACKARD 61 230 | 620 | 717 | 107.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:GILB345_3208 | 620 | 717 | 107.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:AT_R6361 | 620 | 717 | 107.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | S:EMPIRE | 620 | 717 | 107.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 1-3 | NIAGARA - PACKARD 61 230 | 620 | 717 | 107.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 4-6 | NIAGARA - PACKARD 61 230 | 620 | 717 | 107.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MEYER - CANDQUA 60 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 107.19
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 107.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:HCWC/NWES | 620 | 717 | 107.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:MBWC/NWES | 620 | 717 | 107.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN GILBOA #3&4 | 620 | 717 | 107.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:GILB345_3302 | 620 | 717 | 107.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:WATRC345_30-3142 | 620 | 717 | 107.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | WTRCR - MAINSBRG 30A 345 | 620 | 717 | 107.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:GILB345_3308 | 620 | 717 | 107.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:WATRC345_B1-3042 | 620 | 717 | 107
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:NTHF3&4 | 620 | 717 | 106.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN GILBOA #1&2 | 620 | 717 | 106.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:GILB345_3202 | 620 | 717 | 106.98
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 1 | SB:PA230_R304 | 620 | 717 | 106.95
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 2 | SB:PA230_R304 | 620 | 717 | 106.95
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 3 | SB:PA230_R304 | 620 | 717 | 106.95
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CANDQUA - STNYRDG 68A 230 | T:61&64 | 620 | 717 | 106.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - WTRCR 31 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 106.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:HC-WC_30&W-F_171 | 620 | 717 | 106.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | MEYER - CANDQUA 60 230 | 620 | 717 | 106.91
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | T:61&191 | 620 | 717 | 106.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN:SITHE 1 | 620 | 717 | 106.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN:SITHE 2 | 620 | 717 | 106.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:CNDGUA | 620 | 717 | 106.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:HCMB/NWES | 620 | 717 | 106.66
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | B:STOLE230 | 620 | 717 | 106.64
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 3TR | T:61&64 | 620 | 717 | 106.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | MAINSBRG - HOMERCITY 30B 345 | 620 | 717 | 106.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: IND PT 2 | 620 | 717 | 106.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN:BETHSTM | 620 | 717 | 106.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:BUCHN_11 | 620 | 717 | 106.54
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 11 | T:61&64 | 620 | 717 | 106.53
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 12 | T:61&64 | 620 | 717 | 106.53
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 13 | T:61&64 | 620 | 717 | 106.53
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 8 | T:61&64 | 620 | 717 | 106.52
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 9 | T:61&64 | 620 | 717 | 106.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:BUCHN_9 | 620 | 717 | 106.52
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 10 | T:61&64 | 620 | 717 | 106.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:HC-MB_30&W-F_171 | 620 | 717 | 106.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:BUCHN_7 | 620 | 717 | 106.5
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:NIAG345_3108 | 620 | 717 | 106.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDL - FRASER 32 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 106.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN: IND PT 3 | 620 | 717 | 106.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:BUCHS_1 | 620 | 717 | 106.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:BUCHS_3 | 620 | 717 | 106.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:GINNA | NIAGARA - PACKARD 61 230 | 620 | 717 | 106.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:FRGT/WRFL | 620 | 717 | 106.28
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:255_345B302 | 620 | 717 | 106.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:KINT_39-B112 | 620 | 717 | 106.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:KINT_B1-3812 | 620 | 717 | 106.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:67&68&BW | 620 | 717 | 106.17
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK_TSA 345 | T:61&64 | 620 | 717 | 106.15
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK_TSB 345 | T:61&64 | 620 | 717 | 106.15
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 106.15
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAG - NEWROCH 1 345 | 620 | 717 | 106.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SIN:130 | 620 | 717 | 106.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SIN:120_130 | 620 | 717 | 106.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:W97&W98 | 620 | 717 | 106.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SHLDON - STONYCR 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 106.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SHLDON - STONYCR 230 | 620 | 717 | 105.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WTHRS - MEYER 230 | SB:PA230_R304 | 620 | 717 | 105.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STONYCR - WTHRS 230 | T:61&191 | 620 | 717 | 105.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ERIE E - 4 MILE 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 105.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CANDQUA - STNYRDG 68A 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 105.91
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-WC_30&W-F_171 | T:61&64 | 620 | 717 | 105.72
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | ROBINSON - STOLLRD 65 230 | 620 | 717 | 105.66
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WTRCR - MAINSBRG 30A 345 | T:61&64 | 620 | 717 | 105.65
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HCWC/NWES | T:61&64 | 620 | 717 | 105.62
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:MBWC/NWES | T:61&64 | 620 | 717 | 105.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:STONY230 | 620 | 717 | 105.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA - BECK PA27 230 | 620 | 717 | 105.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK PA27 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 105.57
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | S:AVOCA | 620 | 717 | 105.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | CANDQUA - STNYRDG 68A 230 | 620 | 717 | 105.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:STONYRIDGE | 620 | 717 | 105.45
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-FV_37&W-F_171 | SB:PA230_R304 | 620 | 717 | 105.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DUNKIRK - SRIPL 68 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 105.34
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 105.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:OSWE_R955 | 620 | 717 | 105.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN:OSWEGO 5 | 620 | 717 | 105.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SRIPL - ERIE E 69 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 105.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:OSWE_R965 | 620 | 717 | 105.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-WC_30&W-F_171 | T:61&191 | 620 | 717 | 105.26
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 4TR | SB:PA230_R304 | 620 | 717 | 105.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WTRCR - MAINSBRG 30A 345 | T:61&191 | 620 | 717 | 105.21
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - HOMERCTY | SB:PA230_R304 | 620 | 717 | 105.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HCWC/NWES | T:61&191 | 620 | 717 | 105.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:MBWC/NWES | T:61&191 | 620 | 717 | 105.19
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | STOLLRD - GARDENVILL 66 230 | 620 | 717 | 105.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK_TSA 345 | T:61&191 | 620 | 717 | 105.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK_TSB 345 | T:61&191 | 620 | 717 | 105.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:9MIPT1 | 620 | 717 | 104.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:OSWE_R925 | 620 | 717 | 104.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN:OSWEGO 6 | 620 | 717 | 104.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:OSWE_R935 | 620 | 717 | 104.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - KINTIGH 345 | SB:PA230_R304 | 620 | 717 | 104.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 11 | T:61&191 | 620 | 717 | 104.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 12 | T:61&191 | 620 | 717 | 104.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 13 | T:61&191 | 620 | 717 | 104.84
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STONYCR - WTHRS 230 | T:61&64 | 620 | 717 | 104.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 8 | T:61&191 | 620 | 717 | 104.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 9 | T:61&191 | 620 | 717 | 104.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 10 | T:61&191 | 620 | 717 | 104.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:FITZPATR | 620 | 717 | 104.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SIN:250 | 620 | 717 | 104.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:MLS3&OMS | 620 | 717 | 104.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:MILLST3 | 620 | 717 | 104.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | ERIE E - 4 MILE 230 | 620 | 717 | 104.51
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 104.46
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:255_345B202 | 620 | 717 | 104.44
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SOMERSET - NEWROCH 1 345 | 620 | 717 | 104.35
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HCMB/NWES | T:61&64 | 620 | 717 | 104.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:NIAG345_3008 | 620 | 717 | 104.28
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-MB_30&W-F_171 | T:61&64 | 620 | 717 | 104.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:SEAB&OMS | 620 | 717 | 104.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:SEABROOK | 620 | 717 | 104.19
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS1 | SB:PA230_R304 | 620 | 717 | 104.18
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MAINSBRG - HOMERCITY 30B 345 | T:61&64 | 620 | 717 | 104.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R304 | 620 | 717 | 104.04
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 13 345 | SB:PA230_R304 | 620 | 717 | 104.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R304 | 620 | 717 | 103.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HCMB/NWES | T:61&191 | 620 | 717 | 103.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STONYCR - WTHRS 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 103.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-MB_30&W-F_171 | T:61&191 | 620 | 717 | 103.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:KINTIGH | T:61&191 | 620 | 717 | 103.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | STONYCR - WTHRS 230 | 620 | 717 | 103.78
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:INDEK-OL | SB:PA230_R304 | 620 | 717 | 103.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MAINSBRG - HOMERCITY 30B 345 | T:61&191 | 620 | 717 | 103.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:EESR/NWES | 620 | 717 | 103.68
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-SR_37&W-F_171 | SB:PA230_R304 | 620 | 717 | 103.67
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:FV-5M_37&W-F_171 | SB:PA230_R304 | 620 | 717 | 103.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | DUNKIRK - SRIPL 68 230 | 620 | 717 | 103.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:SRIPLEY | 620 | 717 | 103.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SRIPL - ERIE E 69 230 | 620 | 717 | 103.64
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R304 | 620 | 717 | 103.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MSU1_7202>7214>7208>7214 | 620 | 717 | 103.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MARC_765_7402 | 620 | 717 | 103.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | HQ-NY 765 | 620 | 717 | 103.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:GINNA | 620 | 717 | 103.44
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - EDIC 2-15 345 | SB:PA230_R304 | 620 | 717 | 103.4
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:GARD230_T7-12 | 620 | 717 | 103.37
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-2 345 | SB:PA230_R304 | 620 | 717 | 103.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SANDY_DC | 620 | 717 | 103.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SANDY_DC&OMS | 620 | 717 | 103.36
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:JAMESGN7 | SB:PA230_R304 | 620 | 717 | 103.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MASS_765_7102 | 620 | 717 | 103.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:MASS_765_7108 | 620 | 717 | 103.33
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:5M-SR_37&W-F_171 | SB:PA230_R304 | 620 | 717 | 103.25
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL - CLAY PC-1 345 | SB:PA230_R304 | 620 | 717 | 103.25
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL - CLAY PC-2 345 | SB:PA230_R304 | 620 | 717 | 103.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-WC_30&W-F_171 | NIAGARA - PACKARD 61 230 | 620 | 717 | 103.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:WTHERS230 | 620 | 717 | 103.24
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - 5MILE 345 | SB:PA230_R304 | 620 | 717 | 103.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3230 | 620 | 717 | 103.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WTRCR - MAINSBRG 30A 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 103.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HCWC/NWES | NIAGARA - PACKARD 61 230 | 620 | 717 | 103.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:MBWC/NWES | NIAGARA - PACKARD 61 230 | 620 | 717 | 103.19
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 5 MILE - STOLLE 37A 345 | SB:PA230_R304 | 620 | 717 | 103.18
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HOMERCTY - STOLLRD 37 345 | SB:PA230_R304 | 620 | 717 | 103.17
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 4 | SB:PA230_R304 | 620 | 717 | 103.12
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 5 | SB:PA230_R304 | 620 | 717 | 103.12
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 6 | SB:PA230_R304 | 620 | 717 | 103.12
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 7 | SB:PA230_R304 | 620 | 717 | 103.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:BRUCE5 | 620 | 717 | 103.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WTHRS - MEYER 230 | T:61&191 | 620 | 717 | 103.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | B:DUNKG4 | 620 | 717 | 103.04
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | EDIC - FITZ 345 | SB:PA230_R304 | 620 | 717 | 103.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK_TSA 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 102.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK_TSB 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 102.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3230 | 620 | 717 | 102.97
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LOCKPORT | SB:PA230_R304 | 620 | 717 | 102.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA - BECK_TSA 345 | 620 | 717 | 102.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA - BECK_TSB 345 | 620 | 717 | 102.94
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - PACKARD 77 230 | T:61&64 | 620 | 717 | 102.92
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OS - EL - LFYTE 17 345 | SB:PA230_R304 | 620 | 717 | 102.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 620 | 717 | 102.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:OXBOWNUG | SB:PA230_R304 | 620 | 717 | 102.88
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL 345/115 1TR | SB:PA230_R304 | 620 | 717 | 102.85
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL 345/115 2TR | SB:PA230_R304 | 620 | 717 | 102.85
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL 345/115 3TR | SB:PA230_R304 | 620 | 717 | 102.84
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - PACKARD 78 230 | T:61&64 | 620 | 717 | 102.82
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:UDG-184 | SB:PA230_R304 | 620 | 717 | 102.81
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY 345/115 1TR | SB:PA230_R304 | 620 | 717 | 102.76
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY 345/115 2TR | SB:PA230_R304 | 620 | 717 | 102.76
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | VOL - MARCY 19 345 | SB:PA230_R304 | 620 | 717 | 102.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 620 | 717 | 102.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 11 | NIAGARA - PACKARD 61 230 | 620 | 717 | 102.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 12 | NIAGARA - PACKARD 61 230 | 620 | 717 | 102.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 13 | NIAGARA - PACKARD 61 230 | 620 | 717 | 102.73
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:DUPONT46 | SB:PA230_R304 | 620 | 717 | 102.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 8 | NIAGARA - PACKARD 61 230 | 620 | 717 | 102.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 9 | NIAGARA - PACKARD 61 230 | 620 | 717 | 102.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 10 | NIAGARA - PACKARD 61 230 | 620 | 717 | 102.68
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 3 115 | SB:PA230_R304 | 620 | 717 | 102.67
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - TEAL 10 115 | SB:PA230_R304 | 620 | 717 | 102.67
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 5TR | SB:PA230_R304 | 620 | 717 | 102.66
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - LM 14 115 | SB:PA230_R304 | 620 | 717 | 102.66
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - TEAL 11 115 | SB:PA230_R304 | 620 | 717 | 102.66
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 5 115 | SB:PA230_R304 | 620 | 717 | 102.64
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LHH - CLAY 7 115 | SB:PA230_R304 | 620 | 717 | 102.64
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FUL - CLAY 4 115 | SB:PA230_R304 | 620 | 717 | 102.63
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - WOOD 17 115 | SB:PA230_R304 | 620 | 717 | 102.63
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - VOL 21 345 | SB:PA230_R304 | 620 | 717 | 102.63
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA 345/115 1TR | SB:PA230_R304 | 620 | 717 | 102.62
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA 345/115 2TR | SB:PA230_R304 | 620 | 717 | 102.62
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS2 | SB:PA230_R304 | 620 | 717 | 102.62
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - 9MI1 9 345 | SB:PA230_R304 | 620 | 717 | 102.61
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - VOL 20 345 | SB:PA230_R304 | 620 | 717 | 102.61
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - IND 25 345 | SB:PA230_R304 | 620 | 717 | 102.6
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OSW - VOL 11 345 | SB:PA230_R304 | 620 | 717 | 102.59
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OSW - VOL 12 345 | SB:PA230_R304 | 620 | 717 | 102.59
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OSW 345/115 1TR | SB:PA230_R304 | 620 | 717 | 102.59
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - PACKARD 78 230 | SB:PA230_R304 | 620 | 717 | 102.58
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R304 | 620 | 717 | 102.58
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R304 | 620 | 717 | 102.58
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SCRIBA - FITZ 10 345 | SB:PA230_R304 | 620 | 717 | 102.56
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | EDIC - MRCY ue 1-7 345 | SB:PA230_R304 | 620 | 717 | 102.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:DKSR/WRFL | 620 | 717 | 102.5
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:EESR/WF/NWES | 620 | 717 | 102.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | R:EESR/WRFL | 620 | 717 | 102.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 3TR | T:61&191 | 620 | 717 | 102.46
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-1 345 | SB:PA230_R304 | 620 | 717 | 102.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | G:DARLIN1 | 620 | 717 | 102.41
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | SB:PA230_R3230 | 620 | 717 | 102.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:73&74 | 620 | 717 | 102.31
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:KINTIGH | T:61&64 | 620 | 717 | 102.28
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | B:PACKT3 | 620 | 717 | 102.16
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - GARDENVILL 80 230 | T:61&64 | 620 | 717 | 102.11
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LFYTE - CLARKCRNS 36A 345 | T:61&191 | 620 | 717 | 102.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:68&160 | 620 | 717 | 102.02
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - GARDENVILL 79 230 | T:61&64 | 620 | 717 | 101.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HCMB/NWES | NIAGARA - PACKARD 61 230 | 620 | 717 | 101.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-MB_30&W-F_171 | NIAGARA - PACKARD 61 230 | 620 | 717 | 101.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MAINSBRG - HOMERCITY 30B 345 | NIAGARA - PACKARD 61 230 | 620 | 717 | 101.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:KINTIGH | NIAGARA - PACKARD 61 230 | 620 | 717 | 101.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:DUNK230_R1312 | 620 | 717 | 101.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | PACKARD 230/115 3TR | 620 | 717 | 101.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 3TR | NIAGARA - PACKARD 61 230 | 620 | 717 | 101.46
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - CLARKCRNS 36B 345 | T:61&191 | 620 | 717 | 101.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:SCRIBA_R925 | 620 | 717 | 101.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:SCRIBA_R230 | 620 | 717 | 101.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | GEN:9 MI PT2 | 620 | 717 | 101.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WTHRS - MEYER 230 | NIAGARA - PACKARD 61 230 | 620 | 717 | 101.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | WTHRS - MEYER 230 | 620 | 717 | 100.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | B:MEYER | 620 | 717 | 100.85
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:9MIPT1 | SB:PA230_R304 | 620 | 717 | 100.8
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - FARMVLY | SB:PA230_R304 | 620 | 717 | 100.6
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R304 | 620 | 717 | 100.57
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R304 | 620 | 717 | 100.57
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R304 | 620 | 717 | 100.56
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - WTRCR 31 345 | SB:PA230_R304 | 620 | 717 | 100.47
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 1-3 | SB:PA230_R304 | 620 | 717 | 100.37
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 7-9 | SB:PA230_R304 | 620 | 717 | 100.37
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 10-12 | SB:PA230_R304 | 620 | 717 | 100.37
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 4-6 | SB:PA230_R304 | 620 | 717 | 100.36
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - ELM 70 230 | SB:PA230_R304 | 620 | 717 | 100.33
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | WTHRS - MEYER 230 | T:61&64 | 620 | 717 | 100.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - PACKARD 77 230 | T:61&191 | 620 | 717 | 100.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - PACKARD 78 230 | T:61&191 | 620 | 717 | 100.04
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 Max |  |  |  |  | 163.93
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | T:61&64 | 500 | 587 | 137.67
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | T:61&64 | 500 | 587 | 122.03
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | T:61&191 | 500 | 587 | 117.37
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | NIAGARA - PACKARD 62 230 | 500 | 587 | 115
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - PACKARD 61 230 | 500 | 587 | 115
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | T:62&PA27 | 500 | 587 | 114.21
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R3430 | 500 | 587 | 112
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | B:PACKT4 | 500 | 587 | 111.8
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | T:61&191 | 500 | 587 | 104.42
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R3230 | 500 | 587 | 103.17
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | B:PACKT3 | 500 | 587 | 103.01
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R3430 | 500 | 587 | 102.25
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | B:PACKT4 | 500 | 587 | 102.08
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | NIAGARA - PACKARD 62 230 | 500 | 587 | 101.65
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - PACKARD 61 230 | 500 | 587 | 101.64
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | T:62&PA27 | 500 | 587 | 101.49
| 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 Max |  |  |  |  | 137.67
Dispatch 2 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 206 | 105.69
Dispatch 1 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 206 | 102.87
Dispatch 2 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 206 | 100.07
| 135432 AM.S-182 115 135505 WALDENTP 115 1 Max |  |  |  |  | 105.69
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 185 | 125.2
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 185 | 124.54
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 185 | 114.09
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 185 | 110.71
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 145 | 185 | 101.35
| 135433 AMHST-38 115 135472 S129-38 115 1 Max |  |  |  |  | 125.2
Dispatch 1 | 135433 AMHST-38 115 135477 S140-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 102.49
Dispatch 2 | 135433 AMHST-38 115 135477 S140-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 101.91
| 135433 AMHST-38 115 135477 S140-38 115 1 Max |  |  |  |  | 102.49
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 185 | 124.36
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 185 | 123.71
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 185 | 113.32
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 185 | 109.97
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 145 | 185 | 100.63
| 135434 AMHST-39 115 135473 S129-39 115 1 Max |  |  |  |  | 124.36
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 185 | 124.35
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 185 | 123.67
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 185 | 113.31
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 185 | 109.97
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 145 | 185 | 100.62
| 135434 AMHST-39 115 135478 S140-39 115 1 Max |  |  |  |  | 124.35
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 239 | 283 | 104.09
| 135435 SUMIT PK 115 135454 MLPN-129 115 1 Max |  |  |  |  | 104.09
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 139 | 183 | 123.56
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 139 | 183 | 121.33
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 139 | 183 | 119.58
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 139 | 183 | 114.59
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 139 | 183 | 113.41
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 139 | 183 | 110.94
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 139 | 183 | 107.3
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 139 | 183 | 107.21
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 139 | 183 | 107.09
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 139 | 183 | 107.09
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 139 | 183 | 107.05
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | FARMVLY - HOMERCTY | T:77&78 | 139 | 183 | 106.18
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 139 | 183 | 105.69
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 139 | 183 | 105.15
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 139 | 183 | 104.89
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 139 | 183 | 104.68
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 139 | 183 | 104.68
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 139 | 183 | 104.06
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 139 | 183 | 103.96
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 139 | 183 | 103.96
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 139 | 183 | 103.72
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 139 | 183 | 103.72
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 139 | 183 | 103.2
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 139 | 183 | 103.09
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 139 | 183 | 102.54
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 139 | 183 | 101.99
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 139 | 183 | 101.73
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | FARMVLY - HOMERCTY | T:77&78 | 139 | 183 | 101.47
| 135437 CLSP-181 115 135495 YNG-181 115 1 Max |  |  |  |  | 123.56
Dispatch 1 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 206 | 114.09
Dispatch 2 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 206 | 113.58
Dispatch 2 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 206 | 103.76
Dispatch 1 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 206 | 100.68
| 135441 FMC-39 115 135451 HUNTLEY1 115 1 Max |  |  |  |  | 114.09
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 185 | 127.1
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 185 | 126.53
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 185 | 115.59
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 185 | 112.17
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 145 | 185 | 103.32
| 135441 FMC-39 115 135473 S129-39 115 1 Max |  |  |  |  | 127.1
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 117.18
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 115.64
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 226 | 111.45
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 174 | 226 | 108.16
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 226 | 106.75
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 226 | 105.15
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 226 | 102.47
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 226 | 101.96
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 174 | 226 | 101.11
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 174 | 226 | 101.11
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 226 | 100.79
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 174 | 226 | 100.19
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 226 | 100.03
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 226 | 100.03
| 135442 ECWA-181 115 135458 NI.B-181 115 1 Max |  |  |  |  | 117.18
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 116.23
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 114.7
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 226 | 110.7
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 174 | 226 | 107.4
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 226 | 106.03
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 226 | 104.62
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 226 | 101.91
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 226 | 101.42
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 174 | 226 | 100.61
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 174 | 226 | 100.6
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 226 | 100.28
| 135442 ECWA-181 115 135495 YNG-181 115 1 Max |  |  |  |  | 116.23
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 117.69
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 115.93
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 226 | 110.02
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 226 | 105.6
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 174 | 226 | 104.66
| 135443 ECWA-182 115 135459 NI.B-182 115 1 Max |  |  |  |  | 117.69
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 117.85
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 116.09
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 226 | 110.18
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 226 | 105.76
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 174 | 226 | 104.71
| 135443 ECWA-182 115 135496 YNG-182 115 1 Max |  |  |  |  | 117.85
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 108 | 104.91
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 108 | 104.32
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 108 | 103.89
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 108 | 103.27
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | LFYTE - CLARKCRNS 36A 345 | T:73&74 | 88 | 108 | 101.85
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:73&74 | 88 | 108 | 101.71
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 108 | 101.54
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 108 | 100.96
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 108 | 100.96
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 108 | 100.36
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 108 | 100.35
| 135445 FORD-142 115 135484 S55-142 115 1 Max |  |  |  |  | 104.91
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 126.03
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 226 | 124.46
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 226 | 116.6
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 174 | 226 | 112.89
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 226 | 111.76
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 226 | 104.74
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 174 | 226 | 103.94
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 226 | 102.53
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 226 | 102.39
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 226 | 101
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 226 | 100.61
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 226 | 100.61
| 135449 GR.I-182 115 135459 NI.B-182 115 1 Max |  |  |  |  | 126.03
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 265 | 119.58
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 265 | 117.98
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 200 | 265 | 109.59
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 200 | 265 | 108.03
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 200 | 265 | 105.03
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 200 | 265 | 100.89
| 135449 GR.I-182 115 135538 LONG-182 115 1 Max |  |  |  |  | 119.58
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 160 | 206 | 134.06
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 160 | 206 | 130.84
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 160 | 206 | 124.69
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 160 | 206 | 118.41
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 160 | 206 | 118.39
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 110.8
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 160 | 206 | 109.77
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 160 | 206 | 108.41
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 160 | 206 | 107.45
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 160 | 206 | 107.36
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 106.05
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 160 | 206 | 105.95
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 105.88
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 160 | 206 | 105.32
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 160 | 206 | 105.32
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 160 | 206 | 104.35
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 160 | 206 | 104.35
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 160 | 206 | 104.29
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 160 | 206 | 103.39
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 160 | 206 | 103.21
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 160 | 206 | 102.94
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | FARMVLY - HOMERCTY | T:77&78 | 160 | 206 | 102.76
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 160 | 206 | 102.29
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 160 | 206 | 101.87
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 160 | 206 | 101.87
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 100.91
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 160 | 206 | 100.31
| 135450 GRDNVL1 115 135453 LONG-180 115 1 Max |  |  |  |  | 134.06
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 108 | 102.73
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 108 | 102.15
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 108 | 101.64
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 108 | 101.03
| 135450 GRDNVL1 115 135475 S139-141 115 1 Max |  |  |  |  | 102.73
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 185 | 128.21
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 185 | 127.64
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 185 | 116.58
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 185 | 113.12
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 145 | 185 | 104.32
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 145 | 185 | 100.58
| 135451 HUNTLEY1 115 135472 S129-38 115 1 Max |  |  |  |  | 128.21
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 168 | 206 | 121.23
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 168 | 206 | 116.46
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 206 | 111.02
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 206 | 109.02
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 206 | 107.02
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 230 | DCT:230:79+80+ELM1-2 | 168 | 206 | 105.79
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 230 | DCT:230:79+80+ELM1-2 | 168 | 206 | 103.99
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 230 | T:79&80 | 168 | 206 | 103.85
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 206 | 103.31
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 230 | T:79&80 | 168 | 206 | 101.69
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | SB:PA230_R3430 | 168 | 206 | 100.93
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | SB:PA230_R506 | 168 | 206 | 100.69
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | B:PACKT4 | 168 | 206 | 100.64
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 168 | 206 | 100.52
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 Max |  |  |  |  | 121.23
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 168 | 206 | 125
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 168 | 206 | 119.66
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 206 | 114.97
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 206 | 112.85
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 206 | 110.35
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 230 | DCT:230:79+80+ELM1-2 | 168 | 206 | 108.44
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 230 | DCT:230:79+80+ELM1-2 | 168 | 206 | 106.61
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 230 | T:79&80 | 168 | 206 | 106.51
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 206 | 106.49
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 168 | 206 | 104.38
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 230 | T:79&80 | 168 | 206 | 104.33
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | SB:PA230_R3430 | 168 | 206 | 103.22
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 168 | 206 | 103.13
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | SB:PA230_R506 | 168 | 206 | 102.98
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | B:PACKT4 | 168 | 206 | 102.92
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 168 | 206 | 102.76
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | T:77&78 | 168 | 206 | 102.7
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 168 | 206 | 102.61
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | T:77&78 | 168 | 206 | 102.37
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 168 | 206 | 102.26
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 168 | 206 | 102.12
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 168 | 206 | 101.98
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 168 | 206 | 101.98
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | T:77&78 | 168 | 206 | 101.76
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 206 | 101.5
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 206 | 101.26
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 168 | 206 | 101.21
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 168 | 206 | 101.21
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 168 | 206 | 100.8
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | T:77&78 | 168 | 206 | 100.44
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 168 | 206 | 100.4
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 168 | 206 | 100.3
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 168 | 206 | 100.29
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 168 | 206 | 100.27
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 168 | 206 | 100.22
| 135451 HUNTLEY1 115 135562 S214-133 115 1 Max |  |  |  |  | 125
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 143 | 180 | 111.24
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 143 | 180 | 111.1
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 143 | 180 | 109.32
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 143 | 180 | 109.23
| 135452 LOCKPORT 115 135851 SHEL-113 115 1 Max |  |  |  |  | 111.24
Dispatch 2 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 199 | 199 | 102.39
Dispatch 2 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 199 | 199 | 102.21
Dispatch 1 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 199 | 199 | 100.52
Dispatch 1 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 199 | 199 | 100.38
| 135452 LOCKPORT 115 135872 SOUR-111 115 1 Max |  |  |  |  | 102.39
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 143 | 180 | 115.28
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 143 | 180 | 115.12
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 143 | 180 | 113.31
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 143 | 180 | 113.21
| 135452 LOCKPORT 115 135876 TELRDTP1 115 1 Max |  |  |  |  | 115.28
Dispatch 2 | 135453 LONG-180 115 147850 NIAG115E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 265 | 109.95
Dispatch 1 | 135453 LONG-180 115 147850 NIAG115E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 265 | 107.21
Dispatch 2 | 135453 LONG-180 115 147850 NIAG115E 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 200 | 265 | 101.75
| 135453 LONG-180 115 147850 NIAG115E 115 1 Max |  |  |  |  | 109.95
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 239 | 298 | 103.31
| 135454 MLPN-129 115 135461 PACK(S)W 115 1 Max |  |  |  |  | 103.31
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 239 | 298 | 103.98
| 135455 MLPN-130 115 135461 PACK(S)W 115 1 Max |  |  |  |  | 103.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 160 | 206 | 140.95
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 160 | 206 | 139.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 160 | 206 | 132.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 160 | 206 | 130.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 160 | 206 | 126.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 160 | 206 | 126.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 160 | 206 | 123.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 160 | 206 | 122.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 160 | 206 | 121.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 160 | 206 | 121.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 160 | 206 | 121.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 160 | 206 | 121.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 160 | 206 | 121.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 160 | 206 | 120.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 160 | 206 | 120.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 160 | 206 | 119.3
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 160 | 206 | 118.91
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 160 | 206 | 116.85
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 160 | 206 | 116.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:77&78 | 160 | 206 | 116.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 114.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 160 | 206 | 114.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 160 | 206 | 113.89
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 160 | 206 | 113.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 160 | 206 | 112.43
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 111.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 111.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:77&78 | 160 | 206 | 111.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ERIE E - 4 MILE 230 | T:77&78 | 160 | 206 | 110.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 160 | 206 | 110.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DUNKIRK - SRIPL 68 230 | T:77&78 | 160 | 206 | 110.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SRIPL - ERIE E 69 230 | T:77&78 | 160 | 206 | 109.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | T:77&78 | 160 | 206 | 109.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - KINTIGH 345 | T:77&78 | 160 | 206 | 109.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | T:77&78 | 160 | 206 | 109.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 160 | 206 | 109.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 160 | 206 | 109.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CLAY - DEW 13 345 | T:77&78 | 160 | 206 | 108.92
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 160 | 206 | 108.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:JAMESGN7 | T:77&78 | 160 | 206 | 108.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 160 | 206 | 108.31
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 107.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 160 | 206 | 107.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 160 | 206 | 107.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 160 | 206 | 107.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 160 | 206 | 106.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 160 | 206 | 106.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 160 | 206 | 106.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 160 | 206 | 106.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 160 | 206 | 106.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R506 | 160 | 206 | 106.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 160 | 206 | 106.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 160 | 206 | 106.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 160 | 206 | 105.85
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ERIE E - 4 MILE 230 | T:77&78 | 160 | 206 | 105.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 160 | 206 | 105.57
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DUNKIRK - SRIPL 68 230 | T:77&78 | 160 | 206 | 105.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | T:77&78 | 160 | 206 | 105.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 104.97
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - KINTIGH 345 | T:77&78 | 160 | 206 | 104.93
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | T:77&78 | 160 | 206 | 104.91
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SRIPL - ERIE E 69 230 | T:77&78 | 160 | 206 | 104.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | T:77&78 | 160 | 206 | 104.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | T:77&78 | 160 | 206 | 103.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | T:77&78 | 160 | 206 | 103.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 230 | T:79&80 | 160 | 206 | 103.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 160 | 206 | 103.13
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 160 | 206 | 103.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 160 | 206 | 103.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 160 | 206 | 102.84
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R506 | 160 | 206 | 102.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 160 | 206 | 102.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 160 | 206 | 102.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 160 | 206 | 102.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 160 | 206 | 102.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 160 | 206 | 102.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 160 | 206 | 102.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | T:77&78 | 160 | 206 | 102.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 101.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | T:77&78 | 160 | 206 | 101.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | T:77&78 | 160 | 206 | 101.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 160 | 206 | 100.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 160 | 206 | 100.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 206 | 100.04
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 Max |  |  |  |  | 140.95
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 265 | 124.43
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 265 | 122.81
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 200 | 265 | 113.62
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 200 | 265 | 112.79
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 200 | 265 | 109.02
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 200 | 265 | 105.4
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 200 | 265 | 103.63
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 200 | 265 | 102.61
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 200 | 265 | 102.44
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 200 | 265 | 102.44
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 200 | 265 | 101.75
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 200 | 265 | 100.94
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 200 | 265 | 100.63
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 200 | 265 | 100.63
| 135460 PACK(N)E 115 135538 LONG-182 115 1 Max |  |  |  |  | 124.43
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | NIAGARA - PACKARD 62 230 | T:61&191 | 247 | 328 | 127.84
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | PACKARD 230/115 3TR | T:61&191 | 247 | 328 | 119.26
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | NIAGARA - PACKARD 62 230 | T:61&191 | 247 | 328 | 113.19
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 247 | 328 | 109.69
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | PACKARD 230/115 3TR | T:61&191 | 247 | 328 | 109.48
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | ROBINSON - STOLLRD 65 230 | T:61&191 | 247 | 328 | 108.48
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | STOLLRD - GARDENVILL 66 230 | T:61&191 | 247 | 328 | 108.05
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LFYTE - CLARKCRNS 36A 345 | T:61&191 | 247 | 328 | 106.59
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | OAKDLE - CLARKCRNS 36B 345 | T:61&191 | 247 | 328 | 106.25
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | R:HC-FV_37&W-F_171 | T:61&191 | 247 | 328 | 106.06
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | FARMVLY - HOMERCTY | T:61&191 | 247 | 328 | 105.98
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | G:HOORKN86 | T:61&191 | 247 | 328 | 105.73
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | G:HOORKN85 | T:61&191 | 247 | 328 | 105.67
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | BECK - PACKARD BP76 230 | T:61&191 | 247 | 328 | 105.53
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | HUNTLEY - PACKARD 78 230 | T:61&191 | 247 | 328 | 104.79
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | HUNTLEY - PACKARD 77 230 | T:61&191 | 247 | 328 | 104.77
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | HUNTLEY - GARDENVILL 79 230 | T:61&191 | 247 | 328 | 104.59
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | HUNTLEY - GARDENVILL 80 230 | T:61&191 | 247 | 328 | 104.56
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 247 | 328 | 102.86
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | FARMVLY - FARMVLY | T:61&191 | 247 | 328 | 101.29
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | STONYCR - WTHRS 230 | T:61&191 | 247 | 328 | 101
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | G:GINNA | T:61&191 | 247 | 328 | 100.73
| 135460 PACK(N)E 115 147850 NIAG115E 115 2 Max |  |  |  |  | 127.84
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 108 | 102.7
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 108 | 102.12
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 108 | 101.61
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 108 | 101
| 135475 S139-141 115 135483 S55-141 115 1 Max |  |  |  |  | 102.7
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 239 | 298 | 103.59
| 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 Max |  |  |  |  | 103.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 168 | 206 | 129.03
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 168 | 206 | 122.9
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 206 | 118.96
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 206 | 116.84
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 206 | 113.72
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 230 | DCT:230:79+80+ELM1-2 | 168 | 206 | 111.34
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 206 | 109.81
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 230 | DCT:230:79+80+ELM1-2 | 168 | 206 | 109.48
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 230 | T:79&80 | 168 | 206 | 109.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 168 | 206 | 108.29
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 230 | T:79&80 | 168 | 206 | 107.2
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 168 | 206 | 107.07
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 168 | 206 | 106.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 168 | 206 | 106.03
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 168 | 206 | 106.03
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 168 | 206 | 105.88
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | T:77&78 | 168 | 206 | 105.85
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | SB:PA230_R3430 | 168 | 206 | 105.79
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 168 | 206 | 105.69
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | SB:PA230_R506 | 168 | 206 | 105.55
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | B:PACKT4 | 168 | 206 | 105.5
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | T:77&78 | 168 | 206 | 105.47
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 168 | 206 | 105.2
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | T:77&78 | 168 | 206 | 104.95
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 168 | 206 | 104.89
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 168 | 206 | 104.89
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 206 | 104.44
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 206 | 104.21
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 168 | 206 | 104.14
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 168 | 206 | 104.04
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | T:77&78 | 168 | 206 | 103.63
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 168 | 206 | 103.61
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 168 | 206 | 103.61
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 168 | 206 | 103.46
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 168 | 206 | 103.42
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 168 | 206 | 103.34
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 168 | 206 | 103.2
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | T:77&78 | 168 | 206 | 103.18
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:LOCKPORT | T:77&78 | 168 | 206 | 102.99
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:DUPONT46 | T:77&78 | 168 | 206 | 102.86
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 168 | 206 | 102.82
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | T:77&78 | 168 | 206 | 102.73
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 206 | 102.43
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | T:77&78 | 168 | 206 | 102.09
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 168 | 206 | 102.05
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | NIAGARA 230/115 2TR | 168 | 206 | 102.05
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | PACKARD 230/115 4TR | 168 | 206 | 102.01
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 168 | 206 | 101.96
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 168 | 206 | 101.86
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 168 | 206 | 101.64
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 206 | 101.34
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 168 | 206 | 101.33
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 206 | 101.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | SB:NIAW230_2014 | 168 | 206 | 100.76
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 168 | 206 | 100.61
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 168 | 206 | 100.61
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 168 | 206 | 100.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 168 | 206 | 100.57
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 168 | 206 | 100.57
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 168 | 206 | 100.56
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 168 | 206 | 100.5
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 168 | 206 | 100.49
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 168 | 206 | 100.29
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 168 | 206 | 100.26
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 168 | 206 | 100.25
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | T:77&78 | 168 | 206 | 100.07
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 168 | 206 | 100.02
| 135497 ZRMN-133 115 135562 S214-133 115 1 Max |  |  |  |  | 129.03
Dispatch 1 | 135861 MORTIMER 115 149011 S82-1115 115 1 | ROCH - PANNELL RP-1 345 | SB:PANN345_3902 | 258.1 | 357.9 | 104.97
Dispatch 1 | 135861 MORTIMER 115 149011 S82-1115 115 1 | ROCH - PANNELL RP-2 345 | SB:PANN345_3802 | 258.1 | 357.9 | 104.97
Dispatch 1 | 135861 MORTIMER 115 149011 S82-1115 115 1 | ROCH - PANNELL RP-1 345 | SB:PANN345_3908 | 258.1 | 357.9 | 104.94
Dispatch 1 | 135861 MORTIMER 115 149011 S82-1115 115 1 | ROCH - PANNELL RP-2 345 | SB:PANN345_3808 | 258.1 | 357.9 | 104.94
Dispatch 1 | 135861 MORTIMER 115 149011 S82-1115 115 1 | ROCH - PANNELL RP-1 345 | ROCH - PANNELL RP-2 345 | 258.1 | 357.9 | 104.53
Dispatch 1 | 135861 MORTIMER 115 149011 S82-1115 115 1 | ROCH - PANNELL RP-2 345 | ROCH - PANNELL RP-1 345 | 258.1 | 357.9 | 104.53
Dispatch 1 | 135861 MORTIMER 115 149011 S82-1115 115 1 | ROCH - PANNELL RP-1 345 | SB:ROCH_3408 | 258.1 | 357.9 | 103.88
Dispatch 1 | 135861 MORTIMER 115 149011 S82-1115 115 1 | ROCH - PANNELL RP-2 345 | SB:ROCH_3508 | 258.1 | 357.9 | 103.88
Dispatch 2 | 135861 MORTIMER 115 149011 S82-1115 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 258.1 | 357.9 | 103.75
Dispatch 2 | 135861 MORTIMER 115 149011 S82-1115 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 258.1 | 357.9 | 101.15
Dispatch 1 | 135861 MORTIMER 115 149011 S82-1115 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 258.1 | 357.9 | 100.41
| 135861 MORTIMER 115 149011 S82-1115 115 1 Max |  |  |  |  | 104.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 192 | 239 | 188.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 192 | 239 | 183.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | T:62&BP76 | 192 | 239 | 172.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 192 | 239 | 166.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 192 | 239 | 166.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 192 | 239 | 165.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:77&78 | 192 | 239 | 163.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 162.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 192 | 239 | 158.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | T:79&80 | 192 | 239 | 158.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:61&64 | 192 | 239 | 156.69
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | T:77&78 | 192 | 239 | 153.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 192 | 239 | 152.35
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 192 | 239 | 145.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | DCT:230:79+80+ELM1-2 | 192 | 239 | 142.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:77&78 | 192 | 239 | 142.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:77&78 | 192 | 239 | 142.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:77&78 | 192 | 239 | 142.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:77&78 | 192 | 239 | 142.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:79&80 | 192 | 239 | 140.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 139.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:79&80 | 192 | 239 | 137.89
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 192 | 239 | 137.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R304 | 192 | 239 | 137
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3230 | 192 | 239 | 136.35
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 192 | 239 | 136.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 131.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 131.44
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R304 | 192 | 239 | 131.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 192 | 239 | 130.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3230 | 192 | 239 | 130.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 192 | 239 | 129.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | T:77&78 | 192 | 239 | 129.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 192 | 239 | 129.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | T:77&78 | 192 | 239 | 129.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:61&64 | 192 | 239 | 129.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 192 | 239 | 128.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 192 | 239 | 128.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 192 | 239 | 128.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 192 | 239 | 128.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R506 | 192 | 239 | 128.13
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 192 | 239 | 128.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 192 | 239 | 128.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 192 | 239 | 128.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 192 | 239 | 127.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 192 | 239 | 127.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 127.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | T:77&78 | 192 | 239 | 127.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 192 | 239 | 127.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 192 | 239 | 127.31
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 192 | 239 | 126.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | DCT:230:79+80+ELM1-2 | 192 | 239 | 126.53
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | DCT:230:79+80+ELM1-2 | 192 | 239 | 126.53
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | DCT:230:79+80+ELM1-2 | 192 | 239 | 126.53
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | DCT:230:79+80+ELM1-2 | 192 | 239 | 126.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 192 | 239 | 125.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 192 | 239 | 125.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | T:77&78 | 192 | 239 | 125.75
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | T:77&78 | 192 | 239 | 125.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:79&80 | 192 | 239 | 125.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:79&80 | 192 | 239 | 125.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:79&80 | 192 | 239 | 125.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:79&80 | 192 | 239 | 125.07
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | T:77&78 | 192 | 239 | 124.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 192 | 239 | 124.53
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 192 | 239 | 124.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 192 | 239 | 124.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 192 | 239 | 124.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 192 | 239 | 124.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 192 | 239 | 124.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:BLISS1 | T:77&78 | 192 | 239 | 124.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 192 | 239 | 124.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R304 | 192 | 239 | 123.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 192 | 239 | 123.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3230 | 192 | 239 | 123.44
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 192 | 239 | 122.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 192 | 239 | 122.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:PA230_R304 | 192 | 239 | 122.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:PA230_R304 | 192 | 239 | 122.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:PA230_R304 | 192 | 239 | 122.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:PA230_R304 | 192 | 239 | 122.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:PA230_R3230 | 192 | 239 | 121.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:PA230_R3230 | 192 | 239 | 121.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:PA230_R3230 | 192 | 239 | 121.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | B:PACKT3 | 192 | 239 | 121.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | B:PACKT3 | 192 | 239 | 121.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | B:PACKT3 | 192 | 239 | 121.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:PA230_R3230 | 192 | 239 | 121.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | B:PACKT3 | 192 | 239 | 121.77
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:61&64 | 192 | 239 | 121.48
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | T:62&BP76 | 192 | 239 | 120.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:ROBI230 | 192 | 239 | 120.07
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | B:PACKT3 | 192 | 239 | 119.94
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R3230 | 192 | 239 | 119.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:OSWEGO 6 | T:77&78 | 192 | 239 | 119.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:9MIPT1 | T:77&78 | 192 | 239 | 119.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 192 | 239 | 119.64
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAGARA - ROBINSON 64 230 | 192 | 239 | 119.63
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:FITZPATR | T:77&78 | 192 | 239 | 119.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | T:77&78 | 192 | 239 | 119.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 192 | 239 | 119.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 7-9 | T:77&78 | 192 | 239 | 119.36
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 10-12 | T:77&78 | 192 | 239 | 119.36
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 1-3 | T:77&78 | 192 | 239 | 119.35
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 4-6 | T:77&78 | 192 | 239 | 119.35
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 1 | T:77&78 | 192 | 239 | 119.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 2 | T:77&78 | 192 | 239 | 119.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 3 | T:77&78 | 192 | 239 | 119.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | T:77&78 | 192 | 239 | 119.28
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | T:77&78 | 192 | 239 | 119.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 192 | 239 | 119.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:GINNA | T:77&78 | 192 | 239 | 119.06
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 192 | 239 | 117.88
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:61&64 | 192 | 239 | 117.78
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 192 | 239 | 117.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | T:77&78 | 192 | 239 | 117.09
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 192 | 239 | 116.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | T:77&78 | 192 | 239 | 116.67
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 116.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:61&64 | 192 | 239 | 116.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:61&64 | 192 | 239 | 116.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:61&64 | 192 | 239 | 116.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 192 | 239 | 116.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:61&64 | 192 | 239 | 116.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCWC/NWES | T:77&78 | 192 | 239 | 116.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:MBWC/NWES | T:77&78 | 192 | 239 | 116.11
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:77&78 | 192 | 239 | 115.94
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | B:PACKT4 | 192 | 239 | 115.82
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R3430 | 192 | 239 | 115.74
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:255_345B302 | 192 | 239 | 115.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:NIAG345_3108 | 192 | 239 | 115.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | T:77&78 | 192 | 239 | 115.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | NIAG - NEWROCH 1 345 | 192 | 239 | 115.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1302 | 192 | 239 | 114.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCMB/NWES | T:77&78 | 192 | 239 | 114.8
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 192 | 239 | 114.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 192 | 239 | 114.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 192 | 239 | 114.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 192 | 239 | 114.63
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 192 | 239 | 114.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 192 | 239 | 114.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 114.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | DCT:230:79+80+ELM1-2 | 192 | 239 | 114.35
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | T:78&79 | 192 | 239 | 114.35
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1502 | 192 | 239 | 114.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | T:77&80 | 192 | 239 | 113.87
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | PACKARD 230/115 3TR | 192 | 239 | 113.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 8 | T:77&78 | 192 | 239 | 113.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 9 | T:77&78 | 192 | 239 | 113.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 11 | T:77&78 | 192 | 239 | 113.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 12 | T:77&78 | 192 | 239 | 113.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 13 | T:77&78 | 192 | 239 | 113.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 10 | T:77&78 | 192 | 239 | 113.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | PACKARD 230/115 3TR | 192 | 239 | 113.59
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_NEW | 192 | 239 | 113.28
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | SB:255_345B302 | 192 | 239 | 113.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | NIAG - NEWROCH 1 345 | 192 | 239 | 113.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | T:79&80 | 192 | 239 | 113.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | T:62&PA27 | 192 | 239 | 113.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:ROBI230 | 192 | 239 | 112.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | T:79&80 | 192 | 239 | 112.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R506 | 192 | 239 | 112.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 112.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAGARA - ROBINSON 64 230 | 192 | 239 | 112.72
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - ELM 70 230 | T:79&80 | 192 | 239 | 112.7
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | T:79&80 | 192 | 239 | 112.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | SB:NIAG345_3108 | 192 | 239 | 112.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1402 | 192 | 239 | 112.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:ROBI230 | 192 | 239 | 112.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | NIAGARA - ROBINSON 64 230 | 192 | 239 | 112.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 192 | 239 | 112.31
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 192 | 239 | 112.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | NIAGARA - PACKARD 62 230 | 192 | 239 | 112.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - PACKARD 61 230 | 192 | 239 | 112.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | B:Hunt68 | 192 | 239 | 112.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 112.07
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:HUNT230_R1202 | 192 | 239 | 111.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_NEW | 192 | 239 | 111.43
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:GARD230_R823 | 192 | 239 | 111.28
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | T:61&64 | 192 | 239 | 111.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | B:Hunt67 | 192 | 239 | 111.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 192 | 239 | 111.16
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | T:61&64 | 192 | 239 | 111.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:GARD230_R833 | 192 | 239 | 110.77
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:255_345B202 | 192 | 239 | 110.74
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.72
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.72
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | T:79&80 | 192 | 239 | 110.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT4 | 192 | 239 | 110.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 110.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:PA230_R3430 | 192 | 239 | 110.59
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | T:79&80 | 192 | 239 | 110.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:79&80 | 192 | 239 | 110.42
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:77&78 | 192 | 239 | 110.37
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:77&78 | 192 | 239 | 110.37
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:77&78 | 192 | 239 | 110.37
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:77&78 | 192 | 239 | 110.23
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 192 | 239 | 110.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 192 | 239 | 110.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - ELM 70 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 109.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | DCT:230:79+80+ELM1-2 | 192 | 239 | 109.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | T:61&64 | 192 | 239 | 109.88
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 109.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:BLISS1 | DCT:230:79+80+ELM1-2 | 192 | 239 | 109.64
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | DCT:230:79+80+ELM1-2 | 192 | 239 | 109.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1302 | 192 | 239 | 109.28
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 109.28
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 109.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:INDEK-OL | DCT:230:79+80+ELM1-2 | 192 | 239 | 109.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | T:79&80 | 192 | 239 | 109.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | T:79&80 | 192 | 239 | 109.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | T:79&80 | 192 | 239 | 109.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:KINTIGH | T:77&78 | 192 | 239 | 108.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R506 | 192 | 239 | 108.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:255_345B302 | 192 | 239 | 108.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:78&79 | 192 | 239 | 108.64
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R3230 | 192 | 239 | 108.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R304 | 192 | 239 | 108.59
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_R1302 | 192 | 239 | 108.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | B:PACKT3 | 192 | 239 | 108.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1502 | 192 | 239 | 108.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R304 | 192 | 239 | 108.49
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 192 | 239 | 108.48
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 192 | 239 | 108.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R3230 | 192 | 239 | 108.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | B:PACKT3 | 192 | 239 | 108.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | T:79&80 | 192 | 239 | 108.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | T:79&80 | 192 | 239 | 108.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:NIAG345_3108 | 192 | 239 | 108.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | NIAG - NEWROCH 1 345 | 192 | 239 | 108.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | NIAGARA - ROBINSON 64 230 | 192 | 239 | 108.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:ROBI230 | 192 | 239 | 108.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | NIAGARA - ROBINSON 64 230 | 192 | 239 | 108.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:ROBI230 | 192 | 239 | 108.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | NIAGARA - ROBINSON 64 230 | 192 | 239 | 108.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:ROBI230 | 192 | 239 | 108.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:77&80 | 192 | 239 | 108.16
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | NIAGARA - ROBINSON 64 230 | 192 | 239 | 108.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:ROBI230 | 192 | 239 | 108.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_NEW | 192 | 239 | 108.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:BLISS1 | T:79&80 | 192 | 239 | 108.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | T:79&80 | 192 | 239 | 108.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:79&80 | 192 | 239 | 107.94
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | T:79&80 | 192 | 239 | 107.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | B:Hunt68 | 192 | 239 | 107.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | SB:PA230_R304 | 192 | 239 | 107.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | PACKARD 230/115 3TR | 192 | 239 | 107.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R823 | 192 | 239 | 107.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1502 | 192 | 239 | 107.55
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 192 | 239 | 107.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | SB:PA230_R3230 | 192 | 239 | 107.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | B:PACKT3 | 192 | 239 | 107.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1402 | 192 | 239 | 107.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | B:GARD72&79 | 192 | 239 | 107.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_R1202 | 192 | 239 | 107.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | T:78&79 | 192 | 239 | 107.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:Hunt68 | 192 | 239 | 107.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | T:77&80 | 192 | 239 | 107.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | PACKARD 230/115 3TR | 192 | 239 | 107.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | PACKARD 230/115 3TR | 192 | 239 | 107.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | PACKARD 230/115 3TR | 192 | 239 | 107.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1402 | 192 | 239 | 107.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R833 | 192 | 239 | 107.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | PACKARD 230/115 3TR | 192 | 239 | 107.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | S:HNT_GRD80 | 192 | 239 | 106.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - GARDENVILL 80 230 | 192 | 239 | 106.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - GARDENVILL 79 230 | 192 | 239 | 106.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1202 | 192 | 239 | 106.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:PACKT4 | 192 | 239 | 106.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3430 | 192 | 239 | 106.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:HUNT230_R1302 | 192 | 239 | 106.62
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 192 | 239 | 106.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:Hunt67 | 192 | 239 | 106.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R304 | 192 | 239 | 106.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R304 | 192 | 239 | 106.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:GARD230_R873 | 192 | 239 | 106.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | SB:PA230_R304 | 192 | 239 | 105.99
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:61&64 | 192 | 239 | 105.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 192 | 239 | 105.8
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3230 | 192 | 239 | 105.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 192 | 239 | 105.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3230 | 192 | 239 | 105.63
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | SB:PA230_R3230 | 192 | 239 | 105.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | B:GARD73&80 | 192 | 239 | 105.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | B:PACKT3 | 192 | 239 | 105.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:78&79 | 192 | 239 | 105.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | T:61&64 | 192 | 239 | 105.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | B:Hunt67 | 192 | 239 | 105.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:61&191 | 192 | 239 | 105.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:77&80 | 192 | 239 | 105.36
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:HUNT230_R1502 | 192 | 239 | 105.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:9MIPT1 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.04
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 192 | 239 | 104.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:FITZPATR | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 7-9 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 10-12 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 1-3 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 4-6 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:HUNT230_NEW | 192 | 239 | 104.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - GARDENVILL 79 230 | 192 | 239 | 104.59
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:255_345B202 | 192 | 239 | 104.56
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 1 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 2 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 3 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | S:HNT_GRD80 | 192 | 239 | 104.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | B:GARD72&79 | 192 | 239 | 104.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:GINNA | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.44
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - GARDENVILL 80 230 | 192 | 239 | 104.43
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SOMERSET - NEWROCH 1 345 | 192 | 239 | 104.43
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:255_345B302 | 192 | 239 | 104.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:255_345B302 | 192 | 239 | 104.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:255_345B302 | 192 | 239 | 104.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:255_345B302 | 192 | 239 | 104.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | NIAGARA - ROBINSON 64 230 | 192 | 239 | 104.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:GARD230_R823 | 192 | 239 | 104.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | NIAGARA - ROBINSON 64 230 | 192 | 239 | 104.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | NIAG - NEWROCH 1 345 | 192 | 239 | 104.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | NIAG - NEWROCH 1 345 | 192 | 239 | 104.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | NIAG - NEWROCH 1 345 | 192 | 239 | 104.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | NIAG - NEWROCH 1 345 | 192 | 239 | 103.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:NIAG345_3108 | 192 | 239 | 103.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:NIAG345_3108 | 192 | 239 | 103.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:NIAG345_3108 | 192 | 239 | 103.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:NIAG345_3108 | 192 | 239 | 103.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:GARD230_R833 | 192 | 239 | 103.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | SB:GARD230_R873 | 192 | 239 | 103.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:9MIPT1 | T:79&80 | 192 | 239 | 103.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:FITZPATR | T:79&80 | 192 | 239 | 103.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 1-3 | T:79&80 | 192 | 239 | 103.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 7-9 | T:79&80 | 192 | 239 | 103.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 10-12 | T:79&80 | 192 | 239 | 103.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 4-6 | T:79&80 | 192 | 239 | 103.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:HUNT230_R1402 | 192 | 239 | 103.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | T:61&64 | 192 | 239 | 103.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R304 | 192 | 239 | 103.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 1 | T:79&80 | 192 | 239 | 103.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 2 | T:79&80 | 192 | 239 | 103.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 3 | T:79&80 | 192 | 239 | 103.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL78 | 192 | 239 | 103.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | T:79&80 | 192 | 239 | 103.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 78 230 | 192 | 239 | 103.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | B:GARD73&80 | 192 | 239 | 103.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | SB:PA230_R304 | 192 | 239 | 103.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | B:Hunt68 | 192 | 239 | 103.16
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R304 | 192 | 239 | 103.16
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:GINNA | T:79&80 | 192 | 239 | 103.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1302 | 192 | 239 | 103.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | T:79&80 | 192 | 239 | 103.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL77 | 192 | 239 | 103.07
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 77 230 | 192 | 239 | 103.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 230 | 192 | 239 | 102.94
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:HUNT230_R1202 | 192 | 239 | 102.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | B:PACKT3 | 192 | 239 | 102.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 230 | 192 | 239 | 102.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | SB:PA230_R3230 | 192 | 239 | 102.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | B:PACKT3 | 192 | 239 | 102.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R3230 | 192 | 239 | 102.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3230 | 192 | 239 | 102.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | B:PACKT3 | 192 | 239 | 102.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | B:Hunt67 | 192 | 239 | 102.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | SB:PA230_R304 | 192 | 239 | 102.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R304 | 192 | 239 | 102.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R506 | 192 | 239 | 102.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:78&79 | 192 | 239 | 102.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:ROBI230 | 192 | 239 | 102.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1502 | 192 | 239 | 102.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:ROBI230 | 192 | 239 | 102.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | SB:PA230_R3230 | 192 | 239 | 102.3
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 192 | 239 | 102.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R3230 | 192 | 239 | 102.28
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | B:PACKT3 | 192 | 239 | 102.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT3 | 192 | 239 | 102.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:77&80 | 192 | 239 | 102.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_NEW | 192 | 239 | 102.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:GARD72&79 | 192 | 239 | 101.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 101.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - GARDENVILL 79 230 | 192 | 239 | 101.82
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - GARDENVILL 80 230 | 192 | 239 | 101.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:HUNT230_R1302 | 192 | 239 | 101.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:HUNT230_R1302 | 192 | 239 | 101.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:HUNT230_R1302 | 192 | 239 | 101.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | S:HNT_GRD80 | 192 | 239 | 101.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:HUNT230_R1302 | 192 | 239 | 101.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:255_345B202 | 192 | 239 | 101.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:255_345B202 | 192 | 239 | 101.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:255_345B202 | 192 | 239 | 101.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:255_345B202 | 192 | 239 | 101.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 101.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 101.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 101.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1402 | 192 | 239 | 101.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | DCT:230:79+80+ELM1-2 | 192 | 239 | 101.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 101.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:GARD230_R873 | 192 | 239 | 101.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:Hunt68 | 192 | 239 | 101.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 192 | 239 | 101.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | SB:PA230_R304 | 192 | 239 | 101.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:PA230_R506 | 192 | 239 | 101.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:PA230_R506 | 192 | 239 | 101.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:PA230_R506 | 192 | 239 | 101.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 192 | 239 | 101.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:PA230_R506 | 192 | 239 | 101.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 101.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCWC/NWES | DCT:230:79+80+ELM1-2 | 192 | 239 | 101.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:MBWC/NWES | DCT:230:79+80+ELM1-2 | 192 | 239 | 101.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:78&79 | 192 | 239 | 101.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:78&79 | 192 | 239 | 101.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:78&79 | 192 | 239 | 101.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:GARD73&80 | 192 | 239 | 101
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1202 | 192 | 239 | 100.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:78&79 | 192 | 239 | 100.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:HOORKN85 | SB:PA230_R304 | 192 | 239 | 100.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:HOORKN86 | SB:PA230_R304 | 192 | 239 | 100.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:MODERNLF | SB:PA230_R304 | 192 | 239 | 100.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | T:79&80 | 192 | 239 | 100.88
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:HUNT230_R1502 | 192 | 239 | 100.87
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:HUNT230_R1502 | 192 | 239 | 100.87
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:HUNT230_R1502 | 192 | 239 | 100.87
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT4 | 192 | 239 | 100.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 192 | 239 | 100.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | T:61&64 | 192 | 239 | 100.8
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:HUNT230_R1502 | 192 | 239 | 100.8
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R304 | 192 | 239 | 100.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R304 | 192 | 239 | 100.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:77&80 | 192 | 239 | 100.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:77&80 | 192 | 239 | 100.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:77&80 | 192 | 239 | 100.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3430 | 192 | 239 | 100.74
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 192 | 239 | 100.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:77&80 | 192 | 239 | 100.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 192 | 239 | 100.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:Hunt67 | 192 | 239 | 100.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 192 | 239 | 100.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:HOORKN85 | SB:PA230_R3230 | 192 | 239 | 100.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:HUNT230_NEW | 192 | 239 | 100.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:HUNT230_NEW | 192 | 239 | 100.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:HUNT230_NEW | 192 | 239 | 100.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:HOORKN86 | SB:PA230_R3230 | 192 | 239 | 100.59
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:MODERNLF | SB:PA230_R3230 | 192 | 239 | 100.59
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | SB:PA230_R3230 | 192 | 239 | 100.56
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:HUNT230_NEW | 192 | 239 | 100.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:HOORKN85 | B:PACKT3 | 192 | 239 | 100.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:HOORKN86 | B:PACKT3 | 192 | 239 | 100.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:MODERNLF | B:PACKT3 | 192 | 239 | 100.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | B:PACKT3 | 192 | 239 | 100.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | T:79&80 | 192 | 239 | 100.28
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 Max |  |  |  |  | 188.32
| Grand Max |  |  |  |  | 188.32

## N-2_ETC_OH_1000_Fixed
SERIES REACTORS ON 77 AND 78 LINES BY-PASSED
Niagara Dispatch | Monitored Facility | First Contingency | Second Contingency | Rate Base (MVA) | Rate Cont (MVA) | Final AC %Loading
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 474 | 478 | 121.64
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 474 | 478 | 117.06
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 474 | 478 | 116.93
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 115.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 115.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 115.43
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 115.42
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 474 | 478 | 112.68
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 112.45
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 112.21
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 111.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 111.49
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt68 | 474 | 478 | 102.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt67 | 474 | 478 | 101.99
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 474 | 478 | 101.14
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 474 | 478 | 100.94
| 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  |  |  | 121.64
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 238 | 306 | 102.39
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | B:MEYER | 238 | 306 | 101.45
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | WTHRS - MEYER 230 | 238 | 306 | 101.4
| 130815 HINMN115 115 131611 HARIS115 115 1 Max |  |  |  |  | 102.39
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 220 | 280 | 100.75
| 130815 HINMN115 115 135452 LOCKPORT 115 1 Max |  |  |  |  | 100.75
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 566 | 755 | 121.52
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 118.44
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 230 | 566 | 755 | 118.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 566 | 755 | 117.77
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 566 | 755 | 117.75
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 566 | 755 | 116.84
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 566 | 755 | 116.77
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 116.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 566 | 755 | 115.53
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 115.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 566 | 755 | 115.22
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL78 | 566 | 755 | 114.88
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 566 | 755 | 113.58
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 113.14
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 566 | 755 | 113
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 566 | 755 | 112.53
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 566 | 755 | 112.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 111.8
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 230 | 566 | 755 | 111.73
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 566 | 755 | 111.73
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - NEWROCH 1 345 | 566 | 755 | 111.3
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 566 | 755 | 111.29
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 566 | 755 | 111.2
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 111.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 110.42
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 566 | 755 | 110.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | B:PACKT3 | 566 | 755 | 110.1
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SOMERSET - NEWROCH 1 345 | 566 | 755 | 110.04
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 566 | 755 | 110.01
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 109.78
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 566 | 755 | 109.58
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 566 | 755 | 108.85
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL78 | 566 | 755 | 108.23
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 107.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 566 | 755 | 107.51
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | B:PACKT3 | 566 | 755 | 107.27
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 566 | 755 | 106.91
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - HOMERCTY | 566 | 755 | 106.52
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 566 | 755 | 106.51
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT3 | 566 | 755 | 106.45
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-FV_37&W-F_171 | 566 | 755 | 106.41
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 106.25
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 566 | 755 | 106.21
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - NEWROCH 1 345 | 566 | 755 | 106.2
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 105.57
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA 230/115 1TR | 566 | 755 | 105.48
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 105.47
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | LFYTE - CLARKCRNS 36A 345 | 566 | 755 | 105.22
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 78 230 | 566 | 755 | 104.9
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SOMERSET - NEWROCH 1 345 | 566 | 755 | 104.83
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | PACKARD 230/115 3TR | 566 | 755 | 104.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - CLARKCRNS 36B 345 | 566 | 755 | 104.51
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE_B | 566 | 755 | 104.39
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-FV_37&W-F_171 | B:PACKT3 | 566 | 755 | 104.19
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 566 | 755 | 104.15
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - HOMERCTY | B:PACKT3 | 566 | 755 | 104.14
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - KINTIGH 345 | B:PACKT3 | 566 | 755 | 104.03
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 78 230 | 566 | 755 | 103.92
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - COOPERS 345 SC | 566 | 755 | 103.62
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS1 | B:PACKT3 | 566 | 755 | 103.47
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - KINTIGH 345 | 566 | 755 | 103.29
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FRASER 345 SC | 566 | 755 | 103.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:INDEK-OL | B:PACKT3 | 566 | 755 | 103.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 103.04
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 78 230 | 566 | 755 | 103.01
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 102.8
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:170 | 566 | 755 | 102.76
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:180 | 566 | 755 | 102.76
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._99 | 566 | 755 | 102.7
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | Any combination resulting in the loss of two out of three Sawyer transformers under N-1 (Towers 77&78, 77&80) or N-1-1 (any combination of the 77, 79, 80 lines) | 566 | 755 | 102.65
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL78 | 566 | 755 | 102.65
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:JAMESGN7 | B:PACKT3 | 566 | 755 | 102.64
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:160 | 566 | 755 | 102.63
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:150 | 566 | 755 | 102.63
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:PECHBTM2 | 566 | 755 | 102.58
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-SR_37&W-F_171 | B:PACKT3 | 566 | 755 | 102.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:FV-5M_37&W-F_171 | B:PACKT3 | 566 | 755 | 102.55
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:90 | 566 | 755 | 102.54
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - N.SCOT99 I8 345 | 566 | 755 | 102.51
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS1 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 102.49
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE | 566 | 755 | 102.47
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:SUSQ1 | 566 | 755 | 102.42
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 13 345 | B:PACKT3 | 566 | 755 | 102.39
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - N.SCOT77 I4 345 | 566 | 755 | 102.38
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - 5MILE 345 | B:PACKT3 | 566 | 755 | 102.26
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - 5MILE 345 | 566 | 755 | 102.26
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:FV-5M_37&W-F_171 | 566 | 755 | 102.26
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-SR_37&W-F_171 | 566 | 755 | 102.26
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:SALEMG1 | 566 | 755 | 102.18
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:HOPECG1 | 566 | 755 | 102.18
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | G:LIMERCK2 | 566 | 755 | 102.17
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | HURLEY - ROCKT CMT/MTR-34 345 | 566 | 755 | 102.11
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CMT/MTR-34 345 | 566 | 755 | 102.11
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:INDEK-OL | HUNTLEY - PACKARD 78 230 | 566 | 755 | 102.11
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 4 | B:PACKT3 | 566 | 755 | 102.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 5 | B:PACKT3 | 566 | 755 | 102.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 6 | B:PACKT3 | 566 | 755 | 102.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:NIAG. 7 | B:PACKT3 | 566 | 755 | 102.08
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS2 | B:PACKT3 | 566 | 755 | 102.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 566 | 755 | 102.02
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - DEW 13 345 | 566 | 755 | 101.99
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DEWITT3 - LAFAYTTE 345 | B:PACKT3 | 566 | 755 | 101.97
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT3 | 566 | 755 | 101.96
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - WATERCURE 69 230 | B:PACKT3 | 566 | 755 | 101.95
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - ETWANDA 70 230 | B:PACKT3 | 566 | 755 | 101.95
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 566 | 755 | 101.93
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 566 | 755 | 101.93
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 1-16 345 | 566 | 755 | 101.92
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 566 | 755 | 101.92
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 566 | 755 | 101.92
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - BECK_TSA 345 | B:PACKT3 | 566 | 755 | 101.9
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - BECK_TSB 345 | B:PACKT3 | 566 | 755 | 101.9
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH 345/115 5TR | B:PACKT3 | 566 | 755 | 101.9
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 566 | 755 | 101.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 566 | 755 | 101.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL78 | 566 | 755 | 101.88
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 566 | 755 | 101.87
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 566 | 755 | 101.87
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - EDIC 2-15 345 | B:PACKT3 | 566 | 755 | 101.85
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:5M-SR_37&W-F_171 | B:PACKT3 | 566 | 755 | 101.84
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FITZ 345 | 566 | 755 | 101.84
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FITZ - EDIC FEI 345 | 566 | 755 | 101.84
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 5 MILE - STOLLE 37A 345 | B:PACKT3 | 566 | 755 | 101.82
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HOMERCTY - STOLLRD 37 345 | B:PACKT3 | 566 | 755 | 101.82
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-1 345 | B:PACKT3 | 566 | 755 | 101.82
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-2 345 | B:PACKT3 | 566 | 755 | 101.82
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PACKARD 230/115 4TR | B:PACKT3 | 566 | 755 | 101.81
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | VOL - MARCY 19 345 | 566 | 755 | 101.8
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | VOLNEY - MARCY I9 345 | 566 | 755 | 101.8
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:JAMESGN7 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 101.65
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - HOMERCTY | 566 | 755 | 101.53
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | B:PACKT3 | 566 | 755 | 101.52
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-FV_37&W-F_171 | 566 | 755 | 101.43
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 101.41
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | S:PA_HNTL78 | 566 | 755 | 101.34
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 101.27
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 101.2
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 101.2
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:BLISS2 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 101.07
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 101.04
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 100.99
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 100.97
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 100.97
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 100.87
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-1 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 100.82
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 100.82
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT3 | 566 | 755 | 100.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 78 230 | 566 | 755 | 100.47
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDL - FRASER 32 345 | 566 | 755 | 100.41
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | FRASER - OAKDLE 32 345 | 566 | 755 | 100.41
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT2 | 566 | 755 | 100.4
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 2TR | B:PACKT3 | 566 | 755 | 100.39
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: RAVENSWOOD | 566 | 755 | 100.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:30 | 566 | 755 | 100.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | BWLN - WHAV -LDN 67 345 | 566 | 755 | 100.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT1 | 566 | 755 | 100.37
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | PACKARD 230/115 3TR | S:PA_HNTL78 | 566 | 755 | 100.35
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | FARMVLY - FARMVLY | B:PACKT3 | 566 | 755 | 100.31
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M7TR | B:PACKT3 | 566 | 755 | 100.28
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 2TR | 566 | 755 | 100.26
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | LFYTE - CLARKCRNS 36A 345 | 566 | 755 | 100.19
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - WTRCR 31 345 | 566 | 755 | 100.19
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:NOEND | 566 | 755 | 100.18
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M7TR | 566 | 755 | 100.13
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 1-3 | B:PACKT3 | 566 | 755 | 100.13
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 4-6 | B:PACKT3 | 566 | 755 | 100.13
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 7-9 | B:PACKT3 | 566 | 755 | 100.13
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | G:LEW 10-12 | B:PACKT3 | 566 | 755 | 100.13
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | RAMAPO - BRNCHBRG 5018 345 | 566 | 755 | 100.12
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON2 | 566 | 755 | 100.12
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS17-20 | 566 | 755 | 100.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M6TR | B:PACKT3 | 566 | 755 | 100.08
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | GARDENVILL 230/115 M8TR | B:PACKT3 | 566 | 755 | 100.08
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS21-24 | 566 | 755 | 100.06
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 121.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 556 | 704 | 139.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL78 | 556 | 704 | 136.25
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 136.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 230 | 556 | 704 | 135.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 556 | 704 | 135.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 556 | 704 | 135.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 556 | 704 | 134.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 556 | 704 | 134.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 556 | 704 | 133.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 133.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 556 | 704 | 132.91
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 556 | 704 | 132.91
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 132.64
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 556 | 704 | 132.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 556 | 704 | 130.78
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 556 | 704 | 130.77
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 130.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 556 | 704 | 130.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 556 | 704 | 129.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL78 | 556 | 704 | 129.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 128.9
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 230 | 556 | 704 | 128.83
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 556 | 704 | 128.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - NEWROCH 1 345 | 556 | 704 | 128.41
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 556 | 704 | 128.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 556 | 704 | 128.25
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 128.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 556 | 704 | 127.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 127.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 556 | 704 | 127.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SOMERSET - NEWROCH 1 345 | 556 | 704 | 127.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 556 | 704 | 127.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 556 | 704 | 126.98
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | B:PACKT3 | 556 | 704 | 126.94
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 126.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 556 | 704 | 125.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 556 | 704 | 124.96
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 124.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | B:PACKT3 | 556 | 704 | 123.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 556 | 704 | 123.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - HOMERCTY | 556 | 704 | 123.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL78 | 556 | 704 | 123.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-FV_37&W-F_171 | 556 | 704 | 123.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT3 | 556 | 704 | 123.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - NEWROCH 1 345 | 556 | 704 | 122.95
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 122.94
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 556 | 704 | 122.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL78 | 556 | 704 | 122.36
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 122.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 122.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA 230/115 1TR | 556 | 704 | 122.03
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | LFYTE - CLARKCRNS 36A 345 | 556 | 704 | 121.82
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | S:PA_HNTL78 | 556 | 704 | 121.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SOMERSET - NEWROCH 1 345 | 556 | 704 | 121.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 121.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | PACKARD 230/115 3TR | 556 | 704 | 121.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - CLARKCRNS 36B 345 | 556 | 704 | 121.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE_B | 556 | 704 | 120.98
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | B:PACKT3 | 556 | 704 | 120.63
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | S:PA_HNTL78 | 556 | 704 | 120.6
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | B:PACKT3 | 556 | 704 | 120.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | B:PACKT3 | 556 | 704 | 120.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 120.36
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - COOPERS 345 SC | 556 | 704 | 120.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | B:PACKT3 | 556 | 704 | 119.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | S:PA_HNTL78 | 556 | 704 | 119.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - KINTIGH 345 | 556 | 704 | 119.7
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | S:PA_HNTL78 | 556 | 704 | 119.67
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FRASER 345 SC | 556 | 704 | 119.49
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 119.46
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | S:PA_HNTL78 | 556 | 704 | 119.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 78 230 | 556 | 704 | 119.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | B:PACKT3 | 556 | 704 | 119.39
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 119.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:170 | 556 | 704 | 119.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:180 | 556 | 704 | 119.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:90 | 556 | 704 | 119.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._99 | 556 | 704 | 119.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | S:PA_HNTL78 | 556 | 704 | 119.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE | 556 | 704 | 119.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._77 | 556 | 704 | 119.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:160 | 556 | 704 | 118.99
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:150 | 556 | 704 | 118.99
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | B:PACKT3 | 556 | 704 | 118.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | B:PACKT3 | 556 | 704 | 118.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:PECHBTM2 | 556 | 704 | 118.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | B:PACKT3 | 556 | 704 | 118.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - N.SCOT99 I8 345 | 556 | 704 | 118.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 118.81
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SUSQ1 | 556 | 704 | 118.76
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - N.SCOT77 I4 345 | 556 | 704 | 118.72
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-SR_37&W-F_171 | 556 | 704 | 118.68
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:FV-5M_37&W-F_171 | 556 | 704 | 118.68
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - 5MILE 345 | 556 | 704 | 118.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | S:PA_HNTL78 | 556 | 704 | 118.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | B:PACKT3 | 556 | 704 | 118.64
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | B:PACKT3 | 556 | 704 | 118.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SALEMG1 | 556 | 704 | 118.5
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:HOPECG1 | 556 | 704 | 118.49
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:LIMERCK2 | 556 | 704 | 118.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HURLEY - ROCKT CMT/MTR-34 345 | 556 | 704 | 118.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CMT/MTR-34 345 | 556 | 704 | 118.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | HUNTLEY - PACKARD 78 230 | 556 | 704 | 118.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | B:PACKT3 | 556 | 704 | 118.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 4 | B:PACKT3 | 556 | 704 | 118.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 5 | B:PACKT3 | 556 | 704 | 118.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 6 | B:PACKT3 | 556 | 704 | 118.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | B:PACKT3 | 556 | 704 | 118.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | B:PACKT3 | 556 | 704 | 118.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 7 | B:PACKT3 | 556 | 704 | 118.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - DEW 13 345 | 556 | 704 | 118.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | B:PACKT3 | 556 | 704 | 118.27
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT3 | 556 | 704 | 118.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 704 | 118.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 704 | 118.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 1-16 345 | 556 | 704 | 118.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 556 | 704 | 118.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 556 | 704 | 118.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | B:PACKT3 | 556 | 704 | 118.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | B:PACKT3 | 556 | 704 | 118.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | B:PACKT3 | 556 | 704 | 118.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | S:PA_HNTL78 | 556 | 704 | 118.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 556 | 704 | 118.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 556 | 704 | 118.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 556 | 704 | 118.15
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 556 | 704 | 118.15
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FITZ - EDIC FEI 345 | 556 | 704 | 118.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FITZ 345 | 556 | 704 | 118.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - BECK_TSA 345 | B:PACKT3 | 556 | 704 | 118.1
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - BECK_TSB 345 | B:PACKT3 | 556 | 704 | 118.1
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH 345/115 5TR | B:PACKT3 | 556 | 704 | 118.1
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | VOLNEY - MARCY I9 345 | 556 | 704 | 118.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | VOL - MARCY 19 345 | 556 | 704 | 118.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | B:PACKT3 | 556 | 704 | 118.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | B:PACKT3 | 556 | 704 | 118.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | B:PACKT3 | 556 | 704 | 118.01
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 4TR | B:PACKT3 | 556 | 704 | 118
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL78 | 556 | 704 | 117.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | S:PA_HNTL78 | 556 | 704 | 117.9
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - HOMERCTY | 556 | 704 | 117.88
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | S:PA_HNTL78 | 556 | 704 | 117.84
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | S:PA_HNTL78 | 556 | 704 | 117.84
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | B:PACKT3 | 556 | 704 | 117.83
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-FV_37&W-F_171 | 556 | 704 | 117.8
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.6
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | S:PA_HNTL78 | 556 | 704 | 117.6
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.53
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.53
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | S:PA_HNTL78 | 556 | 704 | 117.53
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | S:PA_HNTL78 | 556 | 704 | 117.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | S:PA_HNTL78 | 556 | 704 | 117.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL78 | 556 | 704 | 117.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | S:PA_HNTL78 | 556 | 704 | 117.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | S:PA_HNTL78 | 556 | 704 | 117.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | S:PA_HNTL78 | 556 | 704 | 117.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | S:PA_HNTL78 | 556 | 704 | 117.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | S:PA_HNTL78 | 556 | 704 | 117.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | S:PA_HNTL78 | 556 | 704 | 117.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.2
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL78 | 556 | 704 | 117.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 117.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT3 | 556 | 704 | 116.94
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 116.72
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FRASER - OAKDLE 32 345 | 556 | 704 | 116.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDL - FRASER 32 345 | 556 | 704 | 116.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT2 | 556 | 704 | 116.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: RAVENSWOOD | 556 | 704 | 116.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:30 | 556 | 704 | 116.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | BWLN - WHAV -LDN 67 345 | 556 | 704 | 116.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT1 | 556 | 704 | 116.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | B:PACKT3 | 556 | 704 | 116.5
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 2TR | 556 | 704 | 116.44
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | LFYTE - CLARKCRNS 36A 345 | 556 | 704 | 116.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | B:PACKT3 | 556 | 704 | 116.38
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | B:PACKT3 | 556 | 704 | 116.37
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - WTRCR 31 345 | 556 | 704 | 116.34
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:NOEND | 556 | 704 | 116.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M7TR | 556 | 704 | 116.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | RAMAPO - BRNCHBRG 5018 345 | 556 | 704 | 116.25
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON2 | 556 | 704 | 116.25
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS17-20 | 556 | 704 | 116.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS21-24 | 556 | 704 | 116.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | B:PACKT3 | 556 | 704 | 116.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | B:PACKT3 | 556 | 704 | 116.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | B:PACKT3 | 556 | 704 | 116.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | B:PACKT3 | 556 | 704 | 116.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | B:PACKT3 | 556 | 704 | 116.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | B:PACKT3 | 556 | 704 | 116.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON1 | 556 | 704 | 116.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M6TR | 556 | 704 | 116.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M8TR | 556 | 704 | 116.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BESICORP | 556 | 704 | 116
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:EMPIRE | 556 | 704 | 115.99
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | B:PACKT3 | 556 | 704 | 115.97
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | B:PACKT3 | 556 | 704 | 115.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | B:PACKT3 | 556 | 704 | 115.95
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | B:PACKT3 | 556 | 704 | 115.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:EMPIRE | 556 | 704 | 115.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: IND PT 2 | 556 | 704 | 115.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN GILBOA #3&4 | 556 | 704 | 115.83
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN GILBOA #1&2 | 556 | 704 | 115.79
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:NTHF3&4 | 556 | 704 | 115.76
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - FARMVLY | 556 | 704 | 115.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | S:PA_HNTL78 | 556 | 704 | 115.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | BECK - PACKARD BP76 230 | 556 | 704 | 115.71
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | S:PA_HNTL78 | 556 | 704 | 115.68
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: IND PT 3 | 556 | 704 | 115.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - CLARKCRNS 36B 345 | 556 | 704 | 115.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE_B | 556 | 704 | 115.61
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | B:PACKT3 | 556 | 704 | 115.6
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | S:PA_HNTL78 | 556 | 704 | 115.59
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | B:PACKT3 | 556 | 704 | 115.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | B:PACKT3 | 556 | 704 | 115.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | B:PACKT3 | 556 | 704 | 115.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HILLSIDE 230/115 4TR | 556 | 704 | 115.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:HILLSIDE | 556 | 704 | 115.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 115.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | S:PA_HNTL78 | 556 | 704 | 115.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | S:PA_HNTL78 | 556 | 704 | 115.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | S:PA_HNTL78 | 556 | 704 | 115.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | S:PA_HNTL78 | 556 | 704 | 115.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | S:PA_HNTL78 | 556 | 704 | 115.46
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | HUNTLEY - PACKARD 78 230 | 556 | 704 | 115.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:SITHE 1 | 556 | 704 | 115.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:SITHE 2 | 556 | 704 | 115.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:BETHSTM | 556 | 704 | 115.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - ELM 70 230 | 556 | 704 | 115.39
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | S:PA_HNTL78 | 556 | 704 | 115.39
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | S:PA_HNTL78 | 556 | 704 | 115.39
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HCWC/NWES | 556 | 704 | 115.38
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:MBWC/NWES | 556 | 704 | 115.38
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | WTRCR - MAINSBRG 30A 345 | 556 | 704 | 115.35
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 115.34
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:130 | 556 | 704 | 115.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:120_130 | 556 | 704 | 115.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STNYRDG - HILLSIDE 68B 230 | 556 | 704 | 115.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-WC_30&W-F_171 | 556 | 704 | 115.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 115.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 115.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 115.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 115.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 115.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL78 | 556 | 704 | 115.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL78 | 556 | 704 | 115.16
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL78 | 556 | 704 | 115.15
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 115.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 115.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HCMB/NWES | 556 | 704 | 115.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL - DUNKIRK 73 230 | 556 | 704 | 115.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:DUNKG3 | 556 | 704 | 115.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL - DUNKIRK 74 230 | 556 | 704 | 115.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MAINSBRG - HOMERCITY 30B 345 | 556 | 704 | 115.03
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | B:PACKT3 | 556 | 704 | 115
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | B:PACKT3 | 556 | 704 | 115
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | S:PA_HNTL78 | 556 | 704 | 114.98
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | S:PA_HNTL78 | 556 | 704 | 114.98
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | S:PA_HNTL78 | 556 | 704 | 114.98
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-MB_30&W-F_171 | 556 | 704 | 114.94
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 114.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 114.91
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 114.89
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | S:PA_HNTL78 | 556 | 704 | 114.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 114.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 114.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 114.73
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | B:PACKT3 | 556 | 704 | 114.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - COOPERS 345 SC | 556 | 704 | 114.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | B:PACKT3 | 556 | 704 | 114.53
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 114.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - PACKARD 62 230 | 556 | 704 | 114.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | PACKARD 230/115 3TR | 556 | 704 | 114.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | S:PA_HNTL78 | 556 | 704 | 114.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | B:PACKT3 | 556 | 704 | 114.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | B:PACKT3 | 556 | 704 | 114.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | B:PACKT3 | 556 | 704 | 114.41
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - PACKARD 61 230 | 556 | 704 | 114.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | S:PA_HNTL78 | 556 | 704 | 114.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:OSWEGO 5 | 556 | 704 | 114.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | S:PA_HNTL78 | 556 | 704 | 114.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | B:PACKT3 | 556 | 704 | 114.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | S:PA_HNTL78 | 556 | 704 | 114.2
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA 230/115 1TR | 556 | 704 | 114.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:MILLST3 | 556 | 704 | 114.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:MLS3&OMS | 556 | 704 | 114.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:250 | 556 | 704 | 114.14
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MEYER - CANDQUA 60 230 | 556 | 704 | 114.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - KINTIGH 345 | 556 | 704 | 114.11
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 114.08
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FRASER 345 SC | 556 | 704 | 114.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:FRGT/WRFL | 556 | 704 | 114.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 78 230 | 556 | 704 | 114
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 114
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:OSWEGO 6 | 556 | 704 | 113.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | B:PACKT3 | 556 | 704 | 113.97
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:9MIPT1 | 556 | 704 | 113.97
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | B:PACKT3 | 556 | 704 | 113.97
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 113.96
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | S:PA_HNTL78 | 556 | 704 | 113.88
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | S:PA_HNTL78 | 556 | 704 | 113.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:90 | 556 | 704 | 113.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE | 556 | 704 | 113.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | S:PA_HNTL78 | 556 | 704 | 113.82
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | S:PA_HNTL78 | 556 | 704 | 113.81
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:FITZPATR | 556 | 704 | 113.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:170 | 556 | 704 | 113.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:180 | 556 | 704 | 113.71
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SEAB&OMS | 556 | 704 | 113.7
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SEABROOK | 556 | 704 | 113.7
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | S:PA_HNTL78 | 556 | 704 | 113.67
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | S:PA_HNTL78 | 556 | 704 | 113.67
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 113.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._99 | 556 | 704 | 113.64
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | S:PA_HNTL78 | 556 | 704 | 113.64
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | B:PACKT3 | 556 | 704 | 113.61
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:N.S._77 | 556 | 704 | 113.59
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 113.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 113.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HQ-NY 765 | 556 | 704 | 113.57
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | S:PA_HNTL78 | 556 | 704 | 113.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:160 | 556 | 704 | 113.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:150 | 556 | 704 | 113.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 113.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | B:PACKT3 | 556 | 704 | 113.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | B:PACKT3 | 556 | 704 | 113.53
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:PECHBTM2 | 556 | 704 | 113.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MARCY - N.SCOT99 I8 345 | 556 | 704 | 113.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | HUNTLEY - PACKARD 78 230 | 556 | 704 | 113.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 113.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS1 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 113.39
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SHLDON - STONYCR 230 | 556 | 704 | 113.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SUSQ1 | 556 | 704 | 113.34
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | B:PACKT3 | 556 | 704 | 113.33
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | B:PACKT3 | 556 | 704 | 113.33
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | B:PACKT3 | 556 | 704 | 113.33
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | B:PACKT3 | 556 | 704 | 113.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | B:PACKT3 | 556 | 704 | 113.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 113.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | B:PACKT3 | 556 | 704 | 113.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - N.SCOT77 I4 345 | 556 | 704 | 113.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | B:PACKT3 | 556 | 704 | 113.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | S:PA_HNTL78 | 556 | 704 | 113.26
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | S:PA_HNTL78 | 556 | 704 | 113.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:FV-5M_37&W-F_171 | 556 | 704 | 113.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-SR_37&W-F_171 | 556 | 704 | 113.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - 5MILE 345 | 556 | 704 | 113.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | B:PACKT3 | 556 | 704 | 113.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SANDY_DC | 556 | 704 | 113.09
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SANDY_DC&OMS | 556 | 704 | 113.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SALEMG1 | 556 | 704 | 113.08
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | S:PA_HNTL78 | 556 | 704 | 113.08
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:HOPECG1 | 556 | 704 | 113.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:LIMERCK2 | 556 | 704 | 113.06
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 113.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CMT/MTR-34 345 | 556 | 704 | 112.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HURLEY - ROCKT CMT/MTR-34 345 | 556 | 704 | 112.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:INDEK-OL | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - DEW 13 345 | 556 | 704 | 112.85
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.84
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | S:PA_HNTL78 | 556 | 704 | 112.83
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 704 | 112.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 704 | 112.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 1-16 345 | 556 | 704 | 112.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 556 | 704 | 112.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CLAY - EDIC 2-15 345 | 556 | 704 | 112.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HOMERCTY - STOLLRD 37 345 | 556 | 704 | 112.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE345 | 556 | 704 | 112.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | 5 MILE - STOLLE 37A 345 | 556 | 704 | 112.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | B:PACKT3 | 556 | 704 | 112.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 556 | 704 | 112.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | LEEDS - PV 92 345 | 556 | 704 | 112.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 556 | 704 | 112.72
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ATHENS - PV 91 345 | 556 | 704 | 112.72
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | B:PACKT3 | 556 | 704 | 112.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | B:PACKT3 | 556 | 704 | 112.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | EDIC - FITZ 345 | 556 | 704 | 112.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FITZ - EDIC FEI 345 | 556 | 704 | 112.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:STOLLE345 | 556 | 704 | 112.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | S:PA_HNTL78 | 556 | 704 | 112.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | S:PA_HNTL78 | 556 | 704 | 112.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | S:PA_HNTL78 | 556 | 704 | 112.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | S:PA_HNTL78 | 556 | 704 | 112.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | S:PA_HNTL78 | 556 | 704 | 112.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | VOL - MARCY 19 345 | 556 | 704 | 112.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | VOLNEY - MARCY I9 345 | 556 | 704 | 112.65
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | S:PA_HNTL78 | 556 | 704 | 112.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:5M-SR_37&W-F_171 | 556 | 704 | 112.61
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ROCH 345/115 5TR | 556 | 704 | 112.58
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | S:PA_HNTL78 | 556 | 704 | 112.57
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | S:PA_HNTL78 | 556 | 704 | 112.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | S:PA_HNTL78 | 556 | 704 | 112.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:JAMESGN7 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | S:PA_HNTL78 | 556 | 704 | 112.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:GINNA | 556 | 704 | 112.53
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | S:PA_HNTL78 | 556 | 704 | 112.52
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL78 | 556 | 704 | 112.44
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | B:PACKT3 | 556 | 704 | 112.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.43
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.41
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | B:PACKT3 | 556 | 704 | 112.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | B:PACKT3 | 556 | 704 | 112.35
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | B:PACKT3 | 556 | 704 | 112.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | B:PACKT3 | 556 | 704 | 112.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 4 | B:PACKT3 | 556 | 704 | 112.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 5 | B:PACKT3 | 556 | 704 | 112.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 6 | B:PACKT3 | 556 | 704 | 112.31
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 7 | B:PACKT3 | 556 | 704 | 112.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | S:PA_HNTL78 | 556 | 704 | 112.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | S:PA_HNTL78 | 556 | 704 | 112.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | S:PA_HNTL78 | 556 | 704 | 112.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | S:PA_HNTL78 | 556 | 704 | 112.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.22
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 112.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | S:PA_HNTL78 | 556 | 704 | 112.11
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | S:PA_HNTL78 | 556 | 704 | 112.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | S:PA_HNTL78 | 556 | 704 | 112.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL78 | 556 | 704 | 112.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | B:PACKT3 | 556 | 704 | 112.03
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CANDQUA - STNYRDG 68A 230 | 556 | 704 | 112
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:AVOCA | 556 | 704 | 112
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 111.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | B:PACKT3 | 556 | 704 | 111.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | B:PACKT3 | 556 | 704 | 111.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | B:PACKT3 | 556 | 704 | 111.96
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | S:PA_HNTL78 | 556 | 704 | 111.92
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | 5 MILE - STOLLE 37A 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 111.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:5M-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 111.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HOMERCTY - STOLLRD 37 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 111.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - BECK_TSA 345 | B:PACKT3 | 556 | 704 | 111.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - BECK_TSB 345 | B:PACKT3 | 556 | 704 | 111.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH 345/115 5TR | B:PACKT3 | 556 | 704 | 111.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH 345/115 5TR | S:PA_HNTL78 | 556 | 704 | 111.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | S:PA_HNTL78 | 556 | 704 | 111.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | S:PA_HNTL78 | 556 | 704 | 111.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:BLISS2 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 111.85
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | B:PACKT3 | 556 | 704 | 111.84
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | B:PACKT3 | 556 | 704 | 111.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LOCKPORT | B:PACKT3 | 556 | 704 | 111.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 111.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 111.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-1 345 | B:PACKT3 | 556 | 704 | 111.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 111.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 111.63
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ERIE E - 4 MILE 230 | 556 | 704 | 111.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH 345/115 5TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 111.59
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 111.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | B:PACKT3 | 556 | 704 | 111.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | B:PACKT3 | 556 | 704 | 111.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT2 | 556 | 704 | 111.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDL - FRASER 32 345 | 556 | 704 | 111.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FRASER - OAKDLE 32 345 | 556 | 704 | 111.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: RAVENSWOOD | 556 | 704 | 111.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:30 | 556 | 704 | 111.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | BWLN - WHAV -LDN 67 345 | 556 | 704 | 111.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BOWL PT1 | 556 | 704 | 111.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 2TR | 556 | 704 | 111.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | B:PACKT3 | 556 | 704 | 111.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | B:PACKT3 | 556 | 704 | 111.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | B:PACKT3 | 556 | 704 | 111.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M7TR | 556 | 704 | 110.93
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:9 MI PT2 | 556 | 704 | 110.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:NOEND | 556 | 704 | 110.85
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - WTRCR 31 345 | 556 | 704 | 110.85
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON2 | 556 | 704 | 110.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | RAMAPO - BRNCHBRG 5018 345 | 556 | 704 | 110.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M6TR | 556 | 704 | 110.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL 230/115 M8TR | 556 | 704 | 110.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS17-20 | 556 | 704 | 110.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:MOS21-24 | 556 | 704 | 110.72
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: ROSETON1 | 556 | 704 | 110.66
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/NWES | 556 | 704 | 110.58
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SRIPL - ERIE E 69 230 | 556 | 704 | 110.55
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | DUNKIRK - SRIPL 68 230 | 556 | 704 | 110.55
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: BESICORP | 556 | 704 | 110.53
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:EMPIRE | 556 | 704 | 110.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:EMPIRE | 556 | 704 | 110.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: IND PT 2 | 556 | 704 | 110.4
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | S:PA_HNTL78 | 556 | 704 | 110.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN GILBOA #3&4 | 556 | 704 | 110.37
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | S:PA_HNTL78 | 556 | 704 | 110.37
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 2TR | S:PA_HNTL78 | 556 | 704 | 110.36
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | B:PACKT3 | 556 | 704 | 110.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN GILBOA #1&2 | 556 | 704 | 110.32
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | BECK - PACKARD BP76 230 | 556 | 704 | 110.32
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | S:PA_HNTL78 | 556 | 704 | 110.3
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:NTHF3&4 | 556 | 704 | 110.29
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | S:PA_HNTL78 | 556 | 704 | 110.29
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | S:PA_HNTL78 | 556 | 704 | 110.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | S:PA_HNTL78 | 556 | 704 | 110.28
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | S:PA_HNTL78 | 556 | 704 | 110.27
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STONYCR - WTHRS 230 | 556 | 704 | 110.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | S:PA_HNTL78 | 556 | 704 | 110.25
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | B:PACKT3 | 556 | 704 | 110.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - FARMVLY | 556 | 704 | 110.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN: IND PT 3 | 556 | 704 | 110.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 110.14
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 2TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 110.12
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | S:PA_HNTL78 | 556 | 704 | 110.12
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | S:PA_HNTL78 | 556 | 704 | 110.12
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | B:PACKT3 | 556 | 704 | 110.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | S:PA_HNTL78 | 556 | 704 | 110.09
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | B:PACKT3 | 556 | 704 | 110.08
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | B:PACKT3 | 556 | 704 | 110.08
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HILLSIDE 230/115 4TR | 556 | 704 | 110.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:HILLSIDE | 556 | 704 | 110.07
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 110.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA 230/115 2TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 110.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | S:PA_HNTL78 | 556 | 704 | 110.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | S:PA_HNTL78 | 556 | 704 | 110.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | HUNTLEY - PACKARD 78 230 | 556 | 704 | 110.05
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | HUNTLEY - PACKARD 78 230 | 556 | 704 | 110.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | S:PA_HNTL78 | 556 | 704 | 110.04
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | S:PA_HNTL78 | 556 | 704 | 110.04
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | B:PACKT3 | 556 | 704 | 110.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - ELM 70 230 | 556 | 704 | 110.02
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 110.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M7TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | FARMVLY - FARMVLY | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:BETHSTM | 556 | 704 | 109.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:SITHE 1 | 556 | 704 | 109.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:SITHE 2 | 556 | 704 | 109.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | B:PACKT3 | 556 | 704 | 109.93
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | B:PACKT3 | 556 | 704 | 109.93
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | B:PACKT3 | 556 | 704 | 109.92
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | B:PACKT3 | 556 | 704 | 109.92
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HCWC/NWES | 556 | 704 | 109.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:MBWC/NWES | 556 | 704 | 109.89
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STNYRDG - HILLSIDE 68B 230 | 556 | 704 | 109.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:130 | 556 | 704 | 109.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:120_130 | 556 | 704 | 109.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | WTRCR - MAINSBRG 30A 345 | 556 | 704 | 109.85
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.84
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL78 | 556 | 704 | 109.83
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M6TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL 230/115 M8TR | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL78 | 556 | 704 | 109.81
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | B:PACKT3 | 556 | 704 | 109.81
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 7-9 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.8
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 10-12 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.8
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL78 | 556 | 704 | 109.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 1-3 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:LEW 4-6 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.79
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | B:PACKT3 | 556 | 704 | 109.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-WC_30&W-F_171 | 556 | 704 | 109.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | B:PACKT3 | 556 | 704 | 109.76
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | B:PACKT3 | 556 | 704 | 109.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL - DUNKIRK 73 230 | 556 | 704 | 109.64
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:DUNKG3 | 556 | 704 | 109.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GARDENVILL - DUNKIRK 74 230 | 556 | 704 | 109.62
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | B:PACKT3 | 556 | 704 | 109.61
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HCMB/NWES | 556 | 704 | 109.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MAINSBRG - HOMERCITY 30B 345 | 556 | 704 | 109.56
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:DUNKG4 | 556 | 704 | 109.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - PACKARD 62 230 | 556 | 704 | 109.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STNYRDG - HILLSIDE 68B 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.54
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | S:PA_HNTL78 | 556 | 704 | 109.54
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 73 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GARDENVILL - DUNKIRK 74 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | B:PACKT3 | 556 | 704 | 109.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - PACKARD 61 230 | 556 | 704 | 109.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:HC-MB_30&W-F_171 | 556 | 704 | 109.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | B:PACKT3 | 556 | 704 | 109.47
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | S:PA_HNTL78 | 556 | 704 | 109.44
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.31
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/WF/NWES | 556 | 704 | 109.18
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:DKSR/WRFL | 556 | 704 | 109.18
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - ELM 70 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 109.17
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/WRFL | 556 | 704 | 109.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | S:PA_HNTL78 | 556 | 704 | 108.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | S:PA_HNTL78 | 556 | 704 | 108.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | S:PA_HNTL78 | 556 | 704 | 108.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | S:PA_HNTL78 | 556 | 704 | 108.99
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | S:PA_HNTL78 | 556 | 704 | 108.92
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | S:PA_HNTL78 | 556 | 704 | 108.9
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | S:PA_HNTL78 | 556 | 704 | 108.84
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | S:PA_HNTL78 | 556 | 704 | 108.81
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:OSWEGO 5 | 556 | 704 | 108.8
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | B:PACKT3 | 556 | 704 | 108.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | S:PA_HNTL78 | 556 | 704 | 108.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.75
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | S:PA_HNTL78 | 556 | 704 | 108.75
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | B:Hunt68 | 556 | 704 | 108.73
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SIN:250 | 556 | 704 | 108.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:MILLST3 | 556 | 704 | 108.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:MLS3&OMS | 556 | 704 | 108.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | B:PACKT3 | 556 | 704 | 108.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | MEYER - CANDQUA 60 230 | 556 | 704 | 108.66
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - PACKARD 61 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.64
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | BECK - PACKARD BP76 230 | B:PACKT3 | 556 | 704 | 108.61
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 1 | B:PACKT3 | 556 | 704 | 108.57
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 2 | B:PACKT3 | 556 | 704 | 108.57
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 3 | B:PACKT3 | 556 | 704 | 108.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:KINTIGH | 556 | 704 | 108.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.56
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:FRGT/WRFL | 556 | 704 | 108.55
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MEYER - CANDQUA 60 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDLE - WTRCR 31 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:OSWEGO 6 | 556 | 704 | 108.49
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:9MIPT1 | 556 | 704 | 108.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | S:PA_HNTL78 | 556 | 704 | 108.41
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | S:PA_HNTL78 | 556 | 704 | 108.41
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | S:PA_HNTL78 | 556 | 704 | 108.41
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | S:PA_HNTL78 | 556 | 704 | 108.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | S:PA_HNTL78 | 556 | 704 | 108.4
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | S:PA_HNTL78 | 556 | 704 | 108.39
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:FITZPATR | 556 | 704 | 108.28
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | B:PACKT3 | 556 | 704 | 108.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | B:PACKT3 | 556 | 704 | 108.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | B:PACKT3 | 556 | 704 | 108.24
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SEABROOK | 556 | 704 | 108.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:SEAB&OMS | 556 | 704 | 108.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | B:PACKT3 | 556 | 704 | 108.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | B:PACKT3 | 556 | 704 | 108.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | B:PACKT3 | 556 | 704 | 108.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | S:PA_HNTL78 | 556 | 704 | 108.22
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | S:PA_HNTL78 | 556 | 704 | 108.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 11 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 12 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 13 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.17
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 8 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 9 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.16
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | B:PACKT3 | 556 | 704 | 108.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:NIAG. 10 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 108.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | B:PACKT3 | 556 | 704 | 108.12
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HQ-NY 765 | 556 | 704 | 108.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | G:GINNA | HUNTLEY - PACKARD 78 230 | 556 | 704 | 107.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | B:PACKT3 | 556 | 704 | 107.97
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | OAKDL - FRASER 32 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 107.95
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | S:PA_HNTL78 | 556 | 704 | 107.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SHLDON - STONYCR 230 | 556 | 704 | 107.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | B:PACKT3 | 556 | 704 | 107.63
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SANDY_DC | 556 | 704 | 107.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SANDY_DC&OMS | 556 | 704 | 107.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | S:PA_HNTL78 | 556 | 704 | 107.6
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ERIE E - 4 MILE 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 107.58
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | B:Hunt68 | 556 | 704 | 107.58
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | B:PACKT3 | 556 | 704 | 107.41
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SHLDON - STONYCR 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 107.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | B:PACKT3 | 556 | 704 | 107.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | B:PACKT3 | 556 | 704 | 107.23
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | S:PA_HNTL78 | 556 | 704 | 107.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | S:PA_HNTL78 | 556 | 704 | 107.11
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | B:PACKT3 | 556 | 704 | 107.11
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL78 | 556 | 704 | 107.08
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:GINNA | 556 | 704 | 107.07
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | DUNKIRK - SRIPL 68 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 106.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SRIPL - ERIE E 69 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 106.82
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 106.79
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:BRUCE5 | 556 | 704 | 106.61
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | CANDQUA - STNYRDG 68A 230 | 556 | 704 | 106.57
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:AVOCA | 556 | 704 | 106.57
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | S:PA_HNTL78 | 556 | 704 | 106.48
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | B:Hunt68 | 556 | 704 | 106.3
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | WTHRS - MEYER 230 | 556 | 704 | 106.19
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 106.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | ERIE E - 4 MILE 230 | 556 | 704 | 106.13
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:MEYER | 556 | 704 | 106.12
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:DARLIN1 | 556 | 704 | 105.69
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:9 MI PT2 | 556 | 704 | 105.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/NWES | 556 | 704 | 105.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | DUNKIRK - SRIPL 68 230 | 556 | 704 | 105.03
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | SRIPL - ERIE E 69 230 | 556 | 704 | 105.02
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | B:PACKT3 | 556 | 704 | 104.87
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | S:PA_HNTL78 | 556 | 704 | 104.86
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | S:PA_HNTL78 | 556 | 704 | 104.81
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | S:PA_HNTL78 | 556 | 704 | 104.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | B:PACKT3 | 556 | 704 | 104.78
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | S:PA_HNTL78 | 556 | 704 | 104.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | S:PA_HNTL78 | 556 | 704 | 104.76
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | STONYCR - WTHRS 230 | 556 | 704 | 104.74
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | S:PA_HNTL78 | 556 | 704 | 104.71
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | B:PACKT3 | 556 | 704 | 104.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | B:PACKT3 | 556 | 704 | 104.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | B:PACKT3 | 556 | 704 | 104.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-WC_30&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 104.61
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STONYCR - WTHRS 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 104.52
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTRCR - MAINSBRG 30A 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 104.51
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCWC/NWES | HUNTLEY - PACKARD 78 230 | 556 | 704 | 104.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:MBWC/NWES | HUNTLEY - PACKARD 78 230 | 556 | 704 | 104.48
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:DUNKG4 | 556 | 704 | 104.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | S:PA_HNTL78 | 556 | 704 | 104.06
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | HUNTLEY - PACKARD 78 230 | 556 | 704 | 103.82
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | B:PACKT3 | 556 | 704 | 103.74
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:DKSR/WRFL | 556 | 704 | 103.65
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/WF/NWES | 556 | 704 | 103.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | R:EESR/WRFL | 556 | 704 | 103.62
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | GEN:KINTIGH | B:PACKT3 | 556 | 704 | 103.59
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | B:PACKT3 | 556 | 704 | 103.59
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | S:PA_HNTL78 | 556 | 704 | 103.38
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | S:PA_HNTL78 | 556 | 704 | 103.33
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | B:PACKT3 | 556 | 704 | 103.27
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | B:PACKT3 | 556 | 704 | 103.26
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | S:PA_HNTL78 | 556 | 704 | 103.24
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAG - NEWROCH 1 345 | B:Hunt68 | 556 | 704 | 103.23
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:GARD72&79 | 556 | 704 | 103.15
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | B:PACKT3 | 556 | 704 | 103.13
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HCMB/NWES | HUNTLEY - PACKARD 78 230 | 556 | 704 | 103.11
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | R:HC-MB_30&W-F_171 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 103.05
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | GEN:KINTIGH | 556 | 704 | 103.01
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | NIAGARA - ROBINSON 64 230 | B:Hunt68 | 556 | 704 | 102.98
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | MAINSBRG - HOMERCITY 30B 345 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 102.96
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | STOLLRD - GARDENVILL 66 230 | B:Hunt68 | 556 | 704 | 102.64
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - GARDENVILL 80 230 | 556 | 704 | 102.5
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | S:HNT_GRD80 | 556 | 704 | 102.49
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 102.46
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - GARDENVILL 79 230 | 556 | 704 | 102.45
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 102.42
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 79 230 | S:PA_HNTL78 | 556 | 704 | 102.42
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | ROBINSON - STOLLRD 65 230 | B:Hunt68 | 556 | 704 | 101.51
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:Hunt68 | 556 | 704 | 101.47
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | SOMERSET - NEWROCH 1 345 | B:Hunt68 | 556 | 704 | 101.43
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | B:PACKT3 | 556 | 704 | 101.21
Dispatch 1 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:GARD73&80 | 556 | 704 | 101.21
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:BRUCE5 | 556 | 704 | 101.11
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | S:PA_HNTL78 | 556 | 704 | 101.1
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 78 230 | 556 | 704 | 100.77
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | WTHRS - MEYER 230 | 556 | 704 | 100.74
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | B:MEYER | 556 | 704 | 100.68
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - GARDENVILL 80 230 | S:PA_HNTL78 | 556 | 704 | 100.5
Dispatch 2 | 135303 SAWYER77 230 135415 PACKARD2 230 1 | HUNTLEY - PACKARD 78 230 | G:DARLIN1 | 556 | 704 | 100.19
| 135303 SAWYER77 230 135415 PACKARD2 230 1 Max |  |  |  |  | 139.28
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 118.44
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 230 | 566 | 755 | 118.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 566 | 755 | 117.71
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 566 | 755 | 116.81
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | B:PACKT4 | 566 | 755 | 116.75
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 116.06
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 566 | 755 | 115.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 115.28
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL77 | 566 | 755 | 114.94
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | B:PACKT4 | 566 | 755 | 114.41
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | B:PACKT4 | 566 | 755 | 113.44
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 113.14
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 566 | 755 | 112.57
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 566 | 755 | 112.04
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 111.79
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 566 | 755 | 111.78
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 230 | 566 | 755 | 111.71
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - NEWROCH 1 345 | 566 | 755 | 111.29
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 566 | 755 | 111.15
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | B:PACKT4 | 566 | 755 | 111.13
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 111.06
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 110.39
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SOMERSET - NEWROCH 1 345 | 566 | 755 | 110.04
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 566 | 755 | 109.98
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 109.76
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 566 | 755 | 109.65
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | B:PACKT4 | 566 | 755 | 109.36
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | B:PACKT4 | 566 | 755 | 109.12
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL77 | 566 | 755 | 108.28
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | B:PACKT4 | 566 | 755 | 108.13
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 107.74
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 566 | 755 | 107.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | B:PACKT4 | 566 | 755 | 107.3
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 566 | 755 | 106.94
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - HOMERCTY | 566 | 755 | 106.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-FV_37&W-F_171 | 566 | 755 | 106.4
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 106.26
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 566 | 755 | 106.25
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - NEWROCH 1 345 | 566 | 755 | 106.19
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 105.57
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 105.48
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA 230/115 1TR | 566 | 755 | 105.47
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | B:PACKT4 | 566 | 755 | 105.23
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | LFYTE - CLARKCRNS 36A 345 | 566 | 755 | 105.21
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 77 230 | 566 | 755 | 104.91
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SOMERSET - NEWROCH 1 345 | 566 | 755 | 104.82
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | PACKARD 230/115 3TR | 566 | 755 | 104.66
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - CLARKCRNS 36B 345 | 566 | 755 | 104.51
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE_B | 566 | 755 | 104.38
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 566 | 755 | 104.22
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | B:PACKT4 | 566 | 755 | 104.13
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 77 230 | 566 | 755 | 103.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - COOPERS 345 SC | 566 | 755 | 103.61
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT4 | 566 | 755 | 103.37
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - KINTIGH 345 | 566 | 755 | 103.29
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FRASER 345 SC | 566 | 755 | 103.08
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | B:PACKT4 | 566 | 755 | 103.06
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 103.04
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 77 230 | 566 | 755 | 103.01
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | B:PACKT4 | 566 | 755 | 103.01
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 102.81
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:170 | 566 | 755 | 102.75
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:180 | 566 | 755 | 102.75
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL77 | 566 | 755 | 102.72
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._99 | 566 | 755 | 102.7
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._77 | 566 | 755 | 102.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:160 | 566 | 755 | 102.62
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:150 | 566 | 755 | 102.62
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:PECHBTM2 | 566 | 755 | 102.58
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:90 | 566 | 755 | 102.53
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - N.SCOT99 I8 345 | 566 | 755 | 102.5
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 102.5
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE | 566 | 755 | 102.45
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:SUSQ1 | 566 | 755 | 102.41
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - N.SCOT77 I4 345 | 566 | 755 | 102.38
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - 5MILE 345 | 566 | 755 | 102.26
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-SR_37&W-F_171 | 566 | 755 | 102.25
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:FV-5M_37&W-F_171 | 566 | 755 | 102.25
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:SALEMG1 | 566 | 755 | 102.18
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:HOPECG1 | 566 | 755 | 102.17
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | G:LIMERCK2 | 566 | 755 | 102.16
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | HUNTLEY - PACKARD 77 230 | 566 | 755 | 102.12
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | HURLEY - ROCKT CMT/MTR-34 345 | 566 | 755 | 102.1
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CMT/MTR-34 345 | 566 | 755 | 102.1
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | B:PACKT4 | 566 | 755 | 102.09
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 566 | 755 | 102.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - DEW 13 345 | 566 | 755 | 101.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL77 | 566 | 755 | 101.95
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 566 | 755 | 101.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 566 | 755 | 101.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 1-16 345 | 566 | 755 | 101.92
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 566 | 755 | 101.91
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 566 | 755 | 101.91
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 566 | 755 | 101.88
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 566 | 755 | 101.88
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 566 | 755 | 101.86
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 566 | 755 | 101.86
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FITZ 345 | 566 | 755 | 101.84
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FITZ - EDIC FEI 345 | 566 | 755 | 101.84
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | VOLNEY - MARCY I9 345 | 566 | 755 | 101.8
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | VOL - MARCY 19 345 | 566 | 755 | 101.8
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:JAMESGN7 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 101.66
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - HOMERCTY | 566 | 755 | 101.52
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-FV_37&W-F_171 | 566 | 755 | 101.42
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 101.42
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | S:PA_HNTL77 | 566 | 755 | 101.4
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 101.27
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 101.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 101.2
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS2 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 101.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 101.04
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | B:PACKT4 | 566 | 755 | 101.02
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 101
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | B:PACKT4 | 566 | 755 | 100.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 100.97
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 100.97
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 100.87
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 100.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROCH - PANNELL RP-1 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 100.82
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | B:PACKT4 | 566 | 755 | 100.81
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 77 230 | 566 | 755 | 100.47
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | B:PACKT4 | 566 | 755 | 100.43
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | S:PA_HNTL77 | 566 | 755 | 100.41
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | FRASER - OAKDLE 32 345 | 566 | 755 | 100.4
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDL - FRASER 32 345 | 566 | 755 | 100.4
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT2 | 566 | 755 | 100.39
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: RAVENSWOOD | 566 | 755 | 100.37
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:30 | 566 | 755 | 100.36
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | BWLN - WHAV -LDN 67 345 | 566 | 755 | 100.36
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT1 | 566 | 755 | 100.36
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 2TR | 566 | 755 | 100.25
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - WTRCR 31 345 | 566 | 755 | 100.19
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | LFYTE - CLARKCRNS 36A 345 | 566 | 755 | 100.18
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:NOEND | 566 | 755 | 100.18
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M7TR | 566 | 755 | 100.13
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | RAMAPO - BRNCHBRG 5018 345 | 566 | 755 | 100.12
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON2 | 566 | 755 | 100.12
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 2TR | B:PACKT4 | 566 | 755 | 100.11
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS17-20 | 566 | 755 | 100.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS21-24 | 566 | 755 | 100.06
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | B:PACKT4 | 566 | 755 | 100.05
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 Max |  |  |  |  | 118.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL77 | 556 | 746 | 128.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 128.57
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 230 | 556 | 746 | 128.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 556 | 746 | 127.85
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 556 | 746 | 126.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | B:PACKT4 | 556 | 746 | 126.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 556 | 746 | 126.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 126.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 556 | 746 | 125.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 556 | 746 | 125.61
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 125.38
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | B:PACKT4 | 556 | 746 | 124.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 556 | 746 | 123.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | B:PACKT4 | 556 | 746 | 123.42
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 123.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | S:PA_HNTL77 | 556 | 746 | 122.11
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 556 | 746 | 122.11
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 121.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 230 | 556 | 746 | 121.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 556 | 746 | 121.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - NEWROCH 1 345 | 556 | 746 | 121.38
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 121.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 556 | 746 | 121.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | B:PACKT4 | 556 | 746 | 121.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 556 | 746 | 120.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 120.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SOMERSET - NEWROCH 1 345 | 556 | 746 | 120.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 556 | 746 | 120.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 556 | 746 | 120.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 119.79
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | B:PACKT4 | 556 | 746 | 119.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | B:PACKT4 | 556 | 746 | 119.16
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 556 | 746 | 118.15
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STOLLRD - GARDENVILL 66 230 | B:PACKT4 | 556 | 746 | 118.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 117.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROBINSON - STOLLRD 65 230 | B:PACKT4 | 556 | 746 | 117.21
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - HOMERCTY | 556 | 746 | 116.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL77 | 556 | 746 | 116.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-FV_37&W-F_171 | 556 | 746 | 116.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 116.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - NEWROCH 1 345 | 556 | 746 | 116.22
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 556 | 746 | 115.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL77 | 556 | 746 | 115.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 115.61
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 115.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA 230/115 1TR | 556 | 746 | 115.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - NEWROCH 1 345 | B:PACKT4 | 556 | 746 | 115.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | LFYTE - CLARKCRNS 36A 345 | 556 | 746 | 115.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | S:PA_HNTL77 | 556 | 746 | 115.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SOMERSET - NEWROCH 1 345 | 556 | 746 | 114.83
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 114.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | PACKARD 230/115 3TR | 556 | 746 | 114.54
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - CLARKCRNS 36B 345 | 556 | 746 | 114.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE_B | 556 | 746 | 114.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | S:PA_HNTL77 | 556 | 746 | 114.03
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | B:PACKT4 | 556 | 746 | 114
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 113.79
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - COOPERS 345 SC | 556 | 746 | 113.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | S:PA_HNTL77 | 556 | 746 | 113.21
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT4 | 556 | 746 | 113.21
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - KINTIGH 345 | 556 | 746 | 113.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | S:PA_HNTL77 | 556 | 746 | 113.15
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SOMERSET - NEWROCH 1 345 | B:PACKT4 | 556 | 746 | 113
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FRASER 345 SC | 556 | 746 | 112.96
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 112.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | S:PA_HNTL77 | 556 | 746 | 112.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 77 230 | 556 | 746 | 112.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | B:PACKT4 | 556 | 746 | 112.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 112.66
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:170 | 556 | 746 | 112.62
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:180 | 556 | 746 | 112.62
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:90 | 556 | 746 | 112.57
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | S:PA_HNTL77 | 556 | 746 | 112.57
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._99 | 556 | 746 | 112.56
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE | 556 | 746 | 112.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._77 | 556 | 746 | 112.51
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:160 | 556 | 746 | 112.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:150 | 556 | 746 | 112.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:PECHBTM2 | 556 | 746 | 112.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - N.SCOT99 I8 345 | 556 | 746 | 112.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 112.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SUSQ1 | 556 | 746 | 112.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - N.SCOT77 I4 345 | 556 | 746 | 112.23
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:FV-5M_37&W-F_171 | 556 | 746 | 112.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-SR_37&W-F_171 | 556 | 746 | 112.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | S:PA_HNTL77 | 556 | 746 | 112.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - 5MILE 345 | 556 | 746 | 112.17
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SALEMG1 | 556 | 746 | 112.02
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:HOPECG1 | 556 | 746 | 112.01
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:LIMERCK2 | 556 | 746 | 112.01
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CMT/MTR-34 345 | 556 | 746 | 111.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HURLEY - ROCKT CMT/MTR-34 345 | 556 | 746 | 111.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | HUNTLEY - PACKARD 77 230 | 556 | 746 | 111.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | B:PACKT4 | 556 | 746 | 111.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - DEW 13 345 | 556 | 746 | 111.82
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 746 | 111.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 746 | 111.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 1-16 345 | 556 | 746 | 111.76
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 556 | 746 | 111.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 556 | 746 | 111.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | S:PA_HNTL77 | 556 | 746 | 111.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 556 | 746 | 111.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 556 | 746 | 111.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 556 | 746 | 111.7
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 556 | 746 | 111.7
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FITZ 345 | 556 | 746 | 111.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FITZ - EDIC FEI 345 | 556 | 746 | 111.68
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | VOL - MARCY 19 345 | 556 | 746 | 111.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | VOLNEY - MARCY I9 345 | 556 | 746 | 111.64
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL77 | 556 | 746 | 111.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 111.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | S:PA_HNTL77 | 556 | 746 | 111.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - HOMERCTY | 556 | 746 | 111.44
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | S:PA_HNTL77 | 556 | 746 | 111.42
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | S:PA_HNTL77 | 556 | 746 | 111.42
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-FV_37&W-F_171 | 556 | 746 | 111.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 111.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | S:PA_HNTL77 | 556 | 746 | 111.19
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 111.18
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | S:PA_HNTL77 | 556 | 746 | 111.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 111.11
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 111.11
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | S:PA_HNTL77 | 556 | 746 | 111.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | S:PA_HNTL77 | 556 | 746 | 111.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL77 | 556 | 746 | 111.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | S:PA_HNTL77 | 556 | 746 | 110.93
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 110.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | S:PA_HNTL77 | 556 | 746 | 110.91
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | S:PA_HNTL77 | 556 | 746 | 110.91
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | S:PA_HNTL77 | 556 | 746 | 110.91
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | S:PA_HNTL77 | 556 | 746 | 110.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 110.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-1 345 | S:PA_HNTL77 | 556 | 746 | 110.87
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | B:PACKT4 | 556 | 746 | 110.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 110.81
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 110.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 110.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | B:PACKT4 | 556 | 746 | 110.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 110.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL77 | 556 | 746 | 110.67
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 110.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-1 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 110.63
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | B:PACKT4 | 556 | 746 | 110.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 110.35
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDL - FRASER 32 345 | 556 | 746 | 110.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FRASER - OAKDLE 32 345 | 556 | 746 | 110.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT2 | 556 | 746 | 110.18
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: RAVENSWOOD | 556 | 746 | 110.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:30 | 556 | 746 | 110.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | BWLN - WHAV -LDN 67 345 | 556 | 746 | 110.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT1 | 556 | 746 | 110.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | B:PACKT4 | 556 | 746 | 110.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 2TR | 556 | 746 | 110.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | LFYTE - CLARKCRNS 36A 345 | 556 | 746 | 110.06
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - WTRCR 31 345 | 556 | 746 | 109.98
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:NOEND | 556 | 746 | 109.97
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M7TR | 556 | 746 | 109.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | RAMAPO - BRNCHBRG 5018 345 | 556 | 746 | 109.9
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON2 | 556 | 746 | 109.9
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS17-20 | 556 | 746 | 109.87
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS21-24 | 556 | 746 | 109.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 2TR | B:PACKT4 | 556 | 746 | 109.83
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON1 | 556 | 746 | 109.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | B:PACKT4 | 556 | 746 | 109.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M6TR | 556 | 746 | 109.73
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M8TR | 556 | 746 | 109.73
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BESICORP | 556 | 746 | 109.66
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:EMPIRE | 556 | 746 | 109.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | S:EMPIRE | 556 | 746 | 109.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: IND PT 2 | 556 | 746 | 109.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN GILBOA #3&4 | 556 | 746 | 109.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN GILBOA #1&2 | 556 | 746 | 109.46
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:NTHF3&4 | 556 | 746 | 109.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | S:PA_HNTL77 | 556 | 746 | 109.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - FARMVLY | 556 | 746 | 109.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | S:PA_HNTL77 | 556 | 746 | 109.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | BECK - PACKARD BP76 230 | 556 | 746 | 109.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: IND PT 3 | 556 | 746 | 109.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | B:PACKT4 | 556 | 746 | 109.33
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - CLARKCRNS 36B 345 | 556 | 746 | 109.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | S:PA_HNTL77 | 556 | 746 | 109.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE_B | 556 | 746 | 109.29
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HILLSIDE 230/115 4TR | 556 | 746 | 109.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:HILLSIDE | 556 | 746 | 109.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | S:PA_HNTL77 | 556 | 746 | 109.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | S:PA_HNTL77 | 556 | 746 | 109.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | S:PA_HNTL77 | 556 | 746 | 109.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | S:PA_HNTL77 | 556 | 746 | 109.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | S:PA_HNTL77 | 556 | 746 | 109.18
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 109.18
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | HUNTLEY - PACKARD 77 230 | 556 | 746 | 109.15
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:SITHE 2 | 556 | 746 | 109.14
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:SITHE 1 | 556 | 746 | 109.14
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:BETHSTM | 556 | 746 | 109.13
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | S:PA_HNTL77 | 556 | 746 | 109.11
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | S:PA_HNTL77 | 556 | 746 | 109.11
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HUNTLEY - ELM 70 230 | 556 | 746 | 109.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HCWC/NWES | 556 | 746 | 109.08
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:MBWC/NWES | 556 | 746 | 109.08
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | B:PACKT4 | 556 | 746 | 109.08
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | B:PACKT4 | 556 | 746 | 109.07
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | B:PACKT4 | 556 | 746 | 109.07
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 109.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | WTRCR - MAINSBRG 30A 345 | 556 | 746 | 109.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:130 | 556 | 746 | 109.02
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:120_130 | 556 | 746 | 109.02
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STNYRDG - HILLSIDE 68B 230 | 556 | 746 | 108.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-WC_30&W-F_171 | 556 | 746 | 108.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL77 | 556 | 746 | 108.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL77 | 556 | 746 | 108.89
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL77 | 556 | 746 | 108.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | B:PACKT4 | 556 | 746 | 108.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HCMB/NWES | 556 | 746 | 108.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL - DUNKIRK 73 230 | 556 | 746 | 108.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:DUNKG3 | 556 | 746 | 108.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL - DUNKIRK 74 230 | 556 | 746 | 108.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MAINSBRG - HOMERCITY 30B 345 | 556 | 746 | 108.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | B:PACKT4 | 556 | 746 | 108.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | S:PA_HNTL77 | 556 | 746 | 108.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | S:PA_HNTL77 | 556 | 746 | 108.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | S:PA_HNTL77 | 556 | 746 | 108.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:PACKT4 | 556 | 746 | 108.69
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-MB_30&W-F_171 | 556 | 746 | 108.66
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.66
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | B:PACKT4 | 556 | 746 | 108.66
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | B:PACKT4 | 556 | 746 | 108.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | B:PACKT4 | 556 | 746 | 108.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.64
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.63
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK_TSA 345 | B:PACKT4 | 556 | 746 | 108.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK_TSB 345 | B:PACKT4 | 556 | 746 | 108.55
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | B:PACKT4 | 556 | 746 | 108.54
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | B:PACKT4 | 556 | 746 | 108.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | B:PACKT4 | 556 | 746 | 108.52
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | B:PACKT4 | 556 | 746 | 108.51
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | S:PA_HNTL77 | 556 | 746 | 108.5
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-1 345 | B:PACKT4 | 556 | 746 | 108.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | B:PACKT4 | 556 | 746 | 108.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.47
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.47
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.47
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | LFYTE - CLARKCRNS 36A 345 | B:PACKT4 | 556 | 746 | 108.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - COOPERS 345 SC | 556 | 746 | 108.4
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 108.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - PACKARD 62 230 | 556 | 746 | 108.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | S:PA_HNTL77 | 556 | 746 | 108.19
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | PACKARD 230/115 3TR | 556 | 746 | 108.17
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - PACKARD 61 230 | 556 | 746 | 108.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | S:PA_HNTL77 | 556 | 746 | 108.06
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:OSWEGO 5 | 556 | 746 | 108.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | S:PA_HNTL77 | 556 | 746 | 108.02
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | S:PA_HNTL77 | 556 | 746 | 107.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:MLS3&OMS | 556 | 746 | 107.91
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:250 | 556 | 746 | 107.91
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:MILLST3 | 556 | 746 | 107.91
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA 230/115 1TR | 556 | 746 | 107.9
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MEYER - CANDQUA 60 230 | 556 | 746 | 107.9
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - KINTIGH 345 | 556 | 746 | 107.87
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 107.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FRASER 345 SC | 556 | 746 | 107.85
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:FRGT/WRFL | 556 | 746 | 107.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 77 230 | 556 | 746 | 107.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 107.78
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:OSWEGO 6 | 556 | 746 | 107.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:9MIPT1 | 556 | 746 | 107.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 107.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | S:PA_HNTL77 | 556 | 746 | 107.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | S:PA_HNTL77 | 556 | 746 | 107.64
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:90 | 556 | 746 | 107.64
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SB:5MILE | 556 | 746 | 107.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | S:PA_HNTL77 | 556 | 746 | 107.62
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 61 230 | S:PA_HNTL77 | 556 | 746 | 107.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT4 | 556 | 746 | 107.59
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:FITZPATR | 556 | 746 | 107.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:170 | 556 | 746 | 107.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:180 | 556 | 746 | 107.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SEAB&OMS | 556 | 746 | 107.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SEABROOK | 556 | 746 | 107.49
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | S:PA_HNTL77 | 556 | 746 | 107.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | S:PA_HNTL77 | 556 | 746 | 107.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | S:PA_HNTL77 | 556 | 746 | 107.46
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 107.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._99 | 556 | 746 | 107.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | S:PA_HNTL77 | 556 | 746 | 107.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:N.S._77 | 556 | 746 | 107.38
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 61 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 107.38
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 107.37
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:160 | 556 | 746 | 107.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:150 | 556 | 746 | 107.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 107.36
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HQ-NY 765 | 556 | 746 | 107.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:PECHBTM2 | 556 | 746 | 107.31
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | HUNTLEY - PACKARD 77 230 | 556 | 746 | 107.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 107.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MARCY - N.SCOT99 I8 345 | 556 | 746 | 107.23
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 107.21
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SHLDON - STONYCR 230 | 556 | 746 | 107.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SUSQ1 | 556 | 746 | 107.15
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 107.13
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - N.SCOT77 I4 345 | 556 | 746 | 107.1
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | S:PA_HNTL77 | 556 | 746 | 107.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | B:PACKT4 | 556 | 746 | 107.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | S:PA_HNTL77 | 556 | 746 | 107.07
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-SR_37&W-F_171 | 556 | 746 | 107.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:FV-5M_37&W-F_171 | 556 | 746 | 107.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - 5MILE 345 | 556 | 746 | 107.03
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | B:PACKT4 | 556 | 746 | 107.02
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | B:PACKT4 | 556 | 746 | 106.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | S:PA_HNTL77 | 556 | 746 | 106.92
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SANDY_DC&OMS | 556 | 746 | 106.91
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SANDY_DC | 556 | 746 | 106.91
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SALEMG1 | 556 | 746 | 106.9
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:HOPECG1 | 556 | 746 | 106.89
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:LIMERCK2 | 556 | 746 | 106.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | B:PACKT4 | 556 | 746 | 106.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | B:PACKT4 | 556 | 746 | 106.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | B:PACKT4 | 556 | 746 | 106.84
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | B:PACKT4 | 556 | 746 | 106.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.82
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HURLEY - ROCKT CMT/MTR-34 345 | 556 | 746 | 106.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CMT/MTR-34 345 | 556 | 746 | 106.8
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | B:PACKT4 | 556 | 746 | 106.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | B:PACKT4 | 556 | 746 | 106.77
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - DEW 13 345 | 556 | 746 | 106.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | S:PA_HNTL77 | 556 | 746 | 106.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 746 | 106.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | COOPERC - ROCKT CCRT-42 345 | 556 | 746 | 106.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 1-16 345 | 556 | 746 | 106.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 556 | 746 | 106.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CLAY - EDIC 2-15 345 | 556 | 746 | 106.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HOMERCTY - STOLLRD 37 345 | 556 | 746 | 106.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE345 | 556 | 746 | 106.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | 5 MILE - STOLLE 37A 345 | 556 | 746 | 106.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 556 | 746 | 106.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | LEEDS - PV 92 345 | 556 | 746 | 106.57
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | B:PACKT4 | 556 | 746 | 106.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 556 | 746 | 106.56
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ATHENS - PV 91 345 | 556 | 746 | 106.56
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | B:PACKT4 | 556 | 746 | 106.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FITZ - EDIC FEI 345 | 556 | 746 | 106.54
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | EDIC - FITZ 345 | 556 | 746 | 106.54
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | B:PACKT4 | 556 | 746 | 106.54
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | S:PA_HNTL77 | 556 | 746 | 106.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | S:PA_HNTL77 | 556 | 746 | 106.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | S:PA_HNTL77 | 556 | 746 | 106.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | S:PA_HNTL77 | 556 | 746 | 106.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | S:PA_HNTL77 | 556 | 746 | 106.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | S:PA_HNTL77 | 556 | 746 | 106.52
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | S:STOLLE345 | 556 | 746 | 106.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | VOLNEY - MARCY I9 345 | 556 | 746 | 106.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | VOL - MARCY 19 345 | 556 | 746 | 106.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:5M-SR_37&W-F_171 | 556 | 746 | 106.45
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | S:PA_HNTL77 | 556 | 746 | 106.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | S:PA_HNTL77 | 556 | 746 | 106.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ROCH 345/115 5TR | 556 | 746 | 106.43
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | S:PA_HNTL77 | 556 | 746 | 106.42
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.41
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | S:PA_HNTL77 | 556 | 746 | 106.41
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | S:PA_HNTL77 | 556 | 746 | 106.39
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:GINNA | 556 | 746 | 106.38
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL77 | 556 | 746 | 106.32
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.29
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.29
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | B:PACKT4 | 556 | 746 | 106.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | S:PA_HNTL77 | 556 | 746 | 106.17
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | S:PA_HNTL77 | 556 | 746 | 106.15
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | S:PA_HNTL77 | 556 | 746 | 106.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | S:PA_HNTL77 | 556 | 746 | 106.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.09
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.09
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 106.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | S:PA_HNTL77 | 556 | 746 | 106
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | S:PA_HNTL77 | 556 | 746 | 105.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | S:PA_HNTL77 | 556 | 746 | 105.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL77 | 556 | 746 | 105.95
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CANDQUA - STNYRDG 68A 230 | 556 | 746 | 105.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | S:AVOCA | 556 | 746 | 105.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 105.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | S:PA_HNTL77 | 556 | 746 | 105.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 105.79
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 105.79
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 105.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH 345/115 5TR | S:PA_HNTL77 | 556 | 746 | 105.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-1 345 | S:PA_HNTL77 | 556 | 746 | 105.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | S:PA_HNTL77 | 556 | 746 | 105.77
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 105.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 105.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 105.69
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | B:PACKT4 | 556 | 746 | 105.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 105.67
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | B:PACKT4 | 556 | 746 | 105.66
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 105.54
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ERIE E - 4 MILE 230 | 556 | 746 | 105.53
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH 345/115 5TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 105.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH - PANNELL RP-2 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 105.48
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | B:PACKT4 | 556 | 746 | 105.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-FV_37&W-F_171 | B:PACKT4 | 556 | 746 | 105.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | B:PACKT4 | 556 | 746 | 105.16
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | B:PACKT4 | 556 | 746 | 105.14
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - HOMERCTY | B:PACKT4 | 556 | 746 | 105.11
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT2 | 556 | 746 | 105.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDL - FRASER 32 345 | 556 | 746 | 105.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FRASER - OAKDLE 32 345 | 556 | 746 | 105.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: RAVENSWOOD | 556 | 746 | 105
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:30 | 556 | 746 | 105
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | BWLN - WHAV -LDN 67 345 | 556 | 746 | 105
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BOWL PT1 | 556 | 746 | 105
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 2TR | 556 | 746 | 104.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M7TR | 556 | 746 | 104.87
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | B:PACKT4 | 556 | 746 | 104.86
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:9 MI PT2 | 556 | 746 | 104.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:NOEND | 556 | 746 | 104.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | OAKDLE - WTRCR 31 345 | 556 | 746 | 104.79
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON2 | 556 | 746 | 104.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | RAMAPO - BRNCHBRG 5018 345 | 556 | 746 | 104.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS17-20 | 556 | 746 | 104.7
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M8TR | 556 | 746 | 104.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL 230/115 M6TR | 556 | 746 | 104.69
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAG - KINTIGH 345 | B:PACKT4 | 556 | 746 | 104.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:MOS21-24 | 556 | 746 | 104.67
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | B:PACKT4 | 556 | 746 | 104.67
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: ROSETON1 | 556 | 746 | 104.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | PACKARD 230/115 3TR | B:PACKT4 | 556 | 746 | 104.6
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/NWES | 556 | 746 | 104.53
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SRIPL - ERIE E 69 230 | 556 | 746 | 104.51
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | DUNKIRK - SRIPL 68 230 | 556 | 746 | 104.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: BESICORP | 556 | 746 | 104.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:EMPIRE | 556 | 746 | 104.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 1TR | B:PACKT4 | 556 | 746 | 104.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS1 | B:PACKT4 | 556 | 746 | 104.46
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | S:EMPIRE | 556 | 746 | 104.43
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: IND PT 2 | 556 | 746 | 104.37
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | S:PA_HNTL77 | 556 | 746 | 104.37
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | S:PA_HNTL77 | 556 | 746 | 104.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 2TR | S:PA_HNTL77 | 556 | 746 | 104.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN GILBOA #3&4 | 556 | 746 | 104.34
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN GILBOA #1&2 | 556 | 746 | 104.3
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | S:PA_HNTL77 | 556 | 746 | 104.3
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | BECK - PACKARD BP76 230 | 556 | 746 | 104.29
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | S:PA_HNTL77 | 556 | 746 | 104.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | S:PA_HNTL77 | 556 | 746 | 104.28
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | S:PA_HNTL77 | 556 | 746 | 104.28
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:NTHF3&4 | 556 | 746 | 104.26
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | S:PA_HNTL77 | 556 | 746 | 104.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | S:PA_HNTL77 | 556 | 746 | 104.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | B:PACKT4 | 556 | 746 | 104.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | B:PACKT4 | 556 | 746 | 104.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | B:PACKT4 | 556 | 746 | 104.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | B:PACKT4 | 556 | 746 | 104.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | B:PACKT4 | 556 | 746 | 104.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STONYCR - WTHRS 230 | 556 | 746 | 104.24
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | B:PACKT4 | 556 | 746 | 104.24
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | FARMVLY - FARMVLY | 556 | 746 | 104.21
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | B:PACKT4 | 556 | 746 | 104.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN: IND PT 3 | 556 | 746 | 104.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | B:PACKT4 | 556 | 746 | 104.2
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 104.13
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | S:PA_HNTL77 | 556 | 746 | 104.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | S:PA_HNTL77 | 556 | 746 | 104.12
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 2TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 104.11
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | S:PA_HNTL77 | 556 | 746 | 104.09
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:INDEK-OL | B:PACKT4 | 556 | 746 | 104.08
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HILLSIDE 230/115 4TR | 556 | 746 | 104.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:HILLSIDE | 556 | 746 | 104.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | S:PA_HNTL77 | 556 | 746 | 104.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | S:PA_HNTL77 | 556 | 746 | 104.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | S:PA_HNTL77 | 556 | 746 | 104.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 2TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 104.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | S:PA_HNTL77 | 556 | 746 | 104.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | HUNTLEY - PACKARD 77 230 | 556 | 746 | 104.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | HUNTLEY - PACKARD 77 230 | 556 | 746 | 104.05
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 104.03
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | B:PACKT4 | 556 | 746 | 104.03
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 104.01
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HUNTLEY - ELM 70 230 | 556 | 746 | 104
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.99
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.99
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:BETHSTM | 556 | 746 | 103.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:SITHE 2 | 556 | 746 | 103.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:SITHE 1 | 556 | 746 | 103.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:MBWC/NWES | 556 | 746 | 103.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HCWC/NWES | 556 | 746 | 103.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | STNYRDG - HILLSIDE 68B 230 | 556 | 746 | 103.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:130 | 556 | 746 | 103.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:120_130 | 556 | 746 | 103.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | BECK - PACKARD BP76 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.85
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | WTRCR - MAINSBRG 30A 345 | 556 | 746 | 103.85
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | S:PA_HNTL77 | 556 | 746 | 103.85
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | S:PA_HNTL77 | 556 | 746 | 103.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | S:PA_HNTL77 | 556 | 746 | 103.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.81
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-WC_30&W-F_171 | 556 | 746 | 103.76
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:JAMESGN7 | B:PACKT4 | 556 | 746 | 103.68
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL - DUNKIRK 73 230 | 556 | 746 | 103.65
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:DUNKG3 | 556 | 746 | 103.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GARDENVILL - DUNKIRK 74 230 | 556 | 746 | 103.63
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HCMB/NWES | 556 | 746 | 103.61
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.58
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | S:PA_HNTL77 | 556 | 746 | 103.58
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MAINSBRG - HOMERCITY 30B 345 | 556 | 746 | 103.57
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:DUNKG4 | 556 | 746 | 103.57
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - PACKARD 62 230 | 556 | 746 | 103.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.53
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-SR_37&W-F_171 | B:PACKT4 | 556 | 746 | 103.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:FV-5M_37&W-F_171 | B:PACKT4 | 556 | 746 | 103.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - PACKARD 61 230 | 556 | 746 | 103.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:HC-MB_30&W-F_171 | 556 | 746 | 103.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | S:PA_HNTL77 | 556 | 746 | 103.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - DEW 13 345 | B:PACKT4 | 556 | 746 | 103.37
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:5M-SR_37&W-F_171 | B:PACKT4 | 556 | 746 | 103.23
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - 5MILE 345 | B:PACKT4 | 556 | 746 | 103.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 103.21
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/WF/NWES | 556 | 746 | 103.21
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:DKSR/WRFL | 556 | 746 | 103.21
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:EESR/WRFL | 556 | 746 | 103.21
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | 5 MILE - STOLLE 37A 345 | B:PACKT4 | 556 | 746 | 103.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HOMERCTY - STOLLRD 37 345 | B:PACKT4 | 556 | 746 | 103.2
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | S:PA_HNTL77 | 556 | 746 | 103.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | S:PA_HNTL77 | 556 | 746 | 103.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | S:PA_HNTL77 | 556 | 746 | 103.06
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | S:PA_HNTL77 | 556 | 746 | 103.05
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:BLISS2 | B:PACKT4 | 556 | 746 | 103.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 61 230 | S:PA_HNTL77 | 556 | 746 | 102.99
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | S:PA_HNTL77 | 556 | 746 | 102.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:PACKT4 | 556 | 746 | 102.96
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - WATERCURE 69 230 | B:PACKT4 | 556 | 746 | 102.94
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HILLSIDE - ETWANDA 70 230 | B:PACKT4 | 556 | 746 | 102.94
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DEWITT3 - LAFAYTTE 345 | B:PACKT4 | 556 | 746 | 102.94
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | S:PA_HNTL77 | 556 | 746 | 102.92
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | S:PA_HNTL77 | 556 | 746 | 102.88
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:OSWEGO 5 | 556 | 746 | 102.86
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | S:PA_HNTL77 | 556 | 746 | 102.84
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK_TSA 345 | B:PACKT4 | 556 | 746 | 102.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - BECK_TSB 345 | B:PACKT4 | 556 | 746 | 102.83
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | S:PA_HNTL77 | 556 | 746 | 102.83
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CLAY - EDIC 2-15 345 | B:PACKT4 | 556 | 746 | 102.82
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.82
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.82
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.82
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ROCH 345/115 5TR | B:PACKT4 | 556 | 746 | 102.8
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 62 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:MILLST3 | 556 | 746 | 102.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:MLS3&OMS | 556 | 746 | 102.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SIN:250 | 556 | 746 | 102.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | MEYER - CANDQUA 60 230 | 556 | 746 | 102.73
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - PACKARD 61 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.72
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.7
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.65
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:KINTIGH | 556 | 746 | 102.64
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | R:FRGT/WRFL | 556 | 746 | 102.62
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MEYER - CANDQUA 60 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.6
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDLE - WTRCR 31 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.59
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | GEN:OSWEGO 6 | 556 | 746 | 102.56
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.56
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:9MIPT1 | 556 | 746 | 102.55
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | S:PA_HNTL77 | 556 | 746 | 102.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | S:PA_HNTL77 | 556 | 746 | 102.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | S:PA_HNTL77 | 556 | 746 | 102.51
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | S:PA_HNTL77 | 556 | 746 | 102.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | S:PA_HNTL77 | 556 | 746 | 102.5
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | S:PA_HNTL77 | 556 | 746 | 102.49
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:FITZPATR | 556 | 746 | 102.37
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | S:PA_HNTL77 | 556 | 746 | 102.33
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SEAB&OMS | 556 | 746 | 102.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:SEABROOK | 556 | 746 | 102.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | S:PA_HNTL77 | 556 | 746 | 102.32
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 11 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.27
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 12 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.27
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 13 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.27
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 10 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 8 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 9 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.26
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | HQ-NY 765 | 556 | 746 | 102.19
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-WC_30&W-F_171 | B:PACKT4 | 556 | 746 | 102.11
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:GINNA | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.09
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | OAKDL - FRASER 32 345 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 102.07
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTRCR - MAINSBRG 30A 345 | B:PACKT4 | 556 | 746 | 102.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STONYCR - WTHRS 230 | B:PACKT4 | 556 | 746 | 102.04
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCWC/NWES | B:PACKT4 | 556 | 746 | 102.02
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:MBWC/NWES | B:PACKT4 | 556 | 746 | 102.02
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | S:PA_HNTL77 | 556 | 746 | 101.98
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SHLDON - STONYCR 230 | 556 | 746 | 101.94
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SANDY_DC | 556 | 746 | 101.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | SANDY_DC&OMS | 556 | 746 | 101.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | S:PA_HNTL77 | 556 | 746 | 101.74
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | ERIE E - 4 MILE 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 101.71
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SHLDON - STONYCR 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 101.48
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M7TR | B:PACKT4 | 556 | 746 | 101.33
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | S:PA_HNTL77 | 556 | 746 | 101.31
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | S:PA_HNTL77 | 556 | 746 | 101.27
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | FARMVLY - FARMVLY | B:PACKT4 | 556 | 746 | 101.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | S:PA_HNTL77 | 556 | 746 | 101.25
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GEN:KINTIGH | B:PACKT4 | 556 | 746 | 101.25
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:GINNA | 556 | 746 | 101.22
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M6TR | B:PACKT4 | 556 | 746 | 101.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL 230/115 M8TR | B:PACKT4 | 556 | 746 | 101.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 3 | B:PACKT4 | 556 | 746 | 101.18
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 1 | B:PACKT4 | 556 | 746 | 101.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:NIAG. 2 | B:PACKT4 | 556 | 746 | 101.17
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 1-3 | B:PACKT4 | 556 | 746 | 101.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 4-6 | B:PACKT4 | 556 | 746 | 101.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 7-9 | B:PACKT4 | 556 | 746 | 101.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | G:LEW 10-12 | B:PACKT4 | 556 | 746 | 101.1
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA - ROBINSON 64 230 | B:Hunt67 | 556 | 746 | 101.1
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | DUNKIRK - SRIPL 68 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 101.03
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | SRIPL - ERIE E 69 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 100.99
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | CANDQUA - STNYRDG 68A 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 100.97
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | STNYRDG - HILLSIDE 68B 230 | B:PACKT4 | 556 | 746 | 100.91
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 73 230 | B:PACKT4 | 556 | 746 | 100.89
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | GARDENVILL - DUNKIRK 74 230 | B:PACKT4 | 556 | 746 | 100.88
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | G:BRUCE5 | 556 | 746 | 100.78
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | S:AVOCA | 556 | 746 | 100.75
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | CANDQUA - STNYRDG 68A 230 | 556 | 746 | 100.75
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HCMB/NWES | B:PACKT4 | 556 | 746 | 100.74
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | R:HC-MB_30&W-F_171 | B:PACKT4 | 556 | 746 | 100.69
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | S:PA_HNTL77 | 556 | 746 | 100.67
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | MAINSBRG - HOMERCITY 30B 345 | B:PACKT4 | 556 | 746 | 100.6
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - ELM 70 230 | B:PACKT4 | 556 | 746 | 100.58
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | WTHRS - MEYER 230 | 556 | 746 | 100.38
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 77 230 | 556 | 746 | 100.36
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | NIAGARA 230/115 2TR | B:PACKT4 | 556 | 746 | 100.35
Dispatch 2 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | ERIE E - 4 MILE 230 | 556 | 746 | 100.33
Dispatch 1 | 135304 SAWYER78 230 135415 PACKARD2 230 2 | HUNTLEY - PACKARD 77 230 | B:MEYER | 556 | 746 | 100.33
| 135304 SAWYER78 230 135415 PACKARD2 230 2 Max |  |  |  |  | 128.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 62 230 | 620 | 841 | 119.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | BECK - PACKARD BP76 230 | 620 | 841 | 119.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | NIAGARA - PACKARD 62 230 | 620 | 841 | 112.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - ROBINSON 64 230 | 620 | 841 | 112.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | B:PACKT4 | 620 | 841 | 106.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAGARA - PACKARD 62 230 | 620 | 841 | 106.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | B:STOLE230 | 620 | 841 | 106
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | NIAGARA - PACKARD 62 230 | 620 | 841 | 105.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | ROBINSON - STOLLRD 65 230 | 620 | 841 | 105.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAG - NEWROCH 1 345 | 620 | 841 | 105.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | NIAGARA - PACKARD 62 230 | 620 | 841 | 104.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | STOLLRD - GARDENVILL 66 230 | 620 | 841 | 104.72
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 62 230 | 620 | 841 | 103.74
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | BECK - PACKARD BP76 230 | 620 | 841 | 103.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SOMERSET - NEWROCH 1 345 | 620 | 841 | 103.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAGARA - PACKARD 62 230 | 620 | 841 | 103.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | NIAGARA - PACKARD 62 230 | 620 | 841 | 102.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA 230/115 1TR | 620 | 841 | 102.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT4 | 620 | 841 | 100.53
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 Max |  |  |  |  | 119.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 61 230 | 620 | 841 | 119.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | BECK - PACKARD BP76 230 | 620 | 841 | 119
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 230 | NIAGARA - PACKARD 61 230 | 620 | 841 | 112.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA - ROBINSON 64 230 | 620 | 841 | 111.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | NIAGARA - PACKARD 61 230 | 620 | 841 | 105.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | B:STOLE230 | 620 | 841 | 105.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | NIAGARA - PACKARD 61 230 | 620 | 841 | 105.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | ROBINSON - STOLLRD 65 230 | 620 | 841 | 104.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAG - NEWROCH 1 345 | 620 | 841 | 104.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | NIAGARA - PACKARD 61 230 | 620 | 841 | 104.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | STOLLRD - GARDENVILL 66 230 | 620 | 841 | 104.34
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 61 230 | 620 | 841 | 103.51
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | BECK - PACKARD BP76 230 | 620 | 841 | 103.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SOMERSET - NEWROCH 1 345 | 620 | 841 | 102.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | NIAGARA - PACKARD 61 230 | 620 | 841 | 102.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 1TR | NIAGARA - PACKARD 61 230 | 620 | 841 | 102.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA 230/115 1TR | 620 | 841 | 102.38
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 Max |  |  |  |  | 119.36
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | NIAGARA - PACKARD 62 230 | 500 | 587 | 115
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - PACKARD 61 230 | 500 | 587 | 115
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | B:PACKT4 | 500 | 587 | 111.8
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | B:PACKT3 | 500 | 587 | 103.01
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | B:PACKT4 | 500 | 587 | 102.08
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | NIAGARA - PACKARD 62 230 | 500 | 587 | 101.65
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - PACKARD 61 230 | 500 | 587 | 101.64
| 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 Max |  |  |  |  | 115
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | B:PACKT4 | 168 | 206 | 100.64
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 Max |  |  |  |  | 100.64
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | B:PACKT4 | 168 | 206 | 102.92
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 168 | 206 | 102.61
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 168 | 206 | 100.3
| 135451 HUNTLEY1 115 135562 S214-133 115 1 Max |  |  |  |  | 102.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 160 | 206 | 106.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 160 | 206 | 106.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 160 | 206 | 106.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 160 | 206 | 106.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 160 | 206 | 106.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 160 | 206 | 102.84
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 160 | 206 | 102.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 160 | 206 | 102.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 160 | 206 | 102.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 160 | 206 | 102.1
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 Max |  |  |  |  | 106.99
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 168 | 206 | 105.69
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | B:PACKT4 | 168 | 206 | 105.5
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 168 | 206 | 103.34
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | NIAGARA 230/115 2TR | 168 | 206 | 102.05
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | PACKARD 230/115 4TR | 168 | 206 | 102.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 168 | 206 | 100.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 168 | 206 | 100.56
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 168 | 206 | 100.5
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 168 | 206 | 100.49
| 135497 ZRMN-133 115 135562 S214-133 115 1 Max |  |  |  |  | 105.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 192 | 288 | 137.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 230 | B:PACKT3 | 192 | 288 | 113.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 192 | 288 | 108.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT4 | 192 | 288 | 106.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 192 | 288 | 103.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 192 | 288 | 103.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 192 | 288 | 103.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 192 | 288 | 103.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 192 | 288 | 102.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | B:PACKT3 | 192 | 288 | 101.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | B:PACKT3 | 192 | 288 | 101.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | B:PACKT3 | 192 | 288 | 101.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | B:PACKT3 | 192 | 288 | 101.05
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 Max |  |  |  |  | 137.97
| Grand Max |  |  |  |  | 139.28

## Ratings_Minimum_Criteria
N-1 (Emergency Transfer Criteria) - 1000 MW Ontario Import
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
135303 | SAWYER77 | 230 | 135415 | PACKARD2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | B - Clearance
135304 | SAWYER78 | 230 | 135415 | PACKARD2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135303 | SAWYER77 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | A - Conductor
135304 | SAWYER78 | 230 | 135414 | HUNTLEY2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
N-1 Thermal Normal - 0 MW Ontario Import
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
135458 | NI.B-181 | 115 | 135460 | PACK(N)E | 115 | 1 | LN | 181 | A - Conductor | A - Conductor | A - Conductor
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
135304 | SAWYER78 | 230 | 135415 | PACKARD2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135303 | SAWYER77 | 230 | 135415 | PACKARD2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | B - Clearance
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 2 | LN | 62 | A - Conductor | G - CT | A - Conductor
130847 | ROLL | 115 | 130857 | STOLE115 | 115 | 1 | Not Available
135461 | PACK (S)W | 115 | 147851 | NIAG115W | 115 | 3 | LN | 195 | A - Conductor | A - Conductor | A - Conductor
135450 | GRDNVL1 | 115 | 135453 | LONG-180 | 115 | 1 | Not Available
130795 | DEPEW115 | 115 | 130799 | ERIE 115 | 115 | 1 | LN | 921 | I - Relay | I - Relay | I - Relay
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 1 | LN | 61 | A - Conductor | G - CT | A - Conductor
135460 | PACK(N)E | 115 | 147850 | NIAG115E | 115 | 2 | LN | 192 | A - Conductor | A - Conductor | A - Conductor
135460 | PACK(N)E | 115 | 147850 | NIAG115E | 115 | 1 | LN | 194 | A - Conductor | A - Conductor | A - Conductor
135460 | PACK(N)E | 115 | 135538 | LONG-182 | 115 | 1 | Not Available
135449 | GR.I-182 | 115 | 135459 | NI.B-182 | 115 | 1 | Not Available
N-1-0 Thermal Overloads (Normal Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
135304 | SAWYER78 | 230 | 135415 | PACKARD2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135303 | SAWYER77 | 230 | 135415 | PACKARD2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | B - Clearance
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 2 | LN | 62 | A - Conductor | G - CT | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 1 | LN | 61 | A - Conductor | G - CT | A - Conductor
N-1-1 (Normal Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
135303 | SAWYER77 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | A - Conductor
135303 | SAWYER77 | 230 | 135415 | PACKARD2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | B - Clearance
135304 | SAWYER78 | 230 | 135414 | HUNTLEY2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135304 | SAWYER78 | 230 | 135415 | PACKARD2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 1 | LN | 61 | A - Conductor | G - CT | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 2 | LN | 62 | A - Conductor | G - CT | A - Conductor
135497 | ZRMN-133 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
147850 | NIAG115E | 115 | 147842 | NIAGAR2W | 230 | 1 | TR | BK T1 | F - Transformer | F - Transformer | F - Transformer
N-1-0 Thermal Overloads (Emergency Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
135304 | SAWYER78 | 230 | 135415 | PACKARD2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135303 | SAWYER77 | 230 | 135415 | PACKARD2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | B - Clearance
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 1 | LN | 61 | A - Conductor | G - CT | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 2 | LN | 62 | A - Conductor | G - CT | A - Conductor
N-1-1 (Emergency) - Ontario Allowed to Move Between 1000 MW and 0 MW
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
135303 | SAWYER77 | 230 | 135415 | PACKARD2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | B - Clearance

## Ratings_Beyond_Criteria
N-1 (NTC) - 1000 MW Ontario Import
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
135303 | SAWYER77 | 230 | 135415 | PACKARD2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | B - Clearance
135304 | SAWYER78 | 230 | 135415 | PACKARD2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135458 | NI.B-181 | 115 | 135460 | PACK(N)E | 115 | 1 | LN | 181-1 | A - Conductor | A - Conductor | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 1 | LN | 61 | A - Conductor | G - CT | A - Conductor
135303 | SAWYER77 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | A - Conductor
135304 | SAWYER78 | 230 | 135414 | HUNTLEY2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
135450 | GRDNVL1 | 115 | 135453 | LONG-180 | 115 | 1 | Not Available
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 2 | LN | 62 | A - Conductor | G - CT | A - Conductor
130795 | DEPEW115 | 115 | 130799 | ERIE 115 | 115 | 1 | LN | 921 | I - Relay | I - Relay | I - Relay
135460 | PACK(N)E | 115 | 135538 | LONG-182 | 115 | 1 | Not Available
135461 | PACK (S)W | 115 | 147851 | NIAG115W | 115 | 3 | LN | 195 | A - Conductor | A - Conductor | A - Conductor
135449 | GR.I-182 | 115 | 135459 | NI.B-182 | 115 | 1 | Not Available
135442 | ECWA-181 | 115 | 135458 | NI.B-181 | 115 | 1 | Not Available
135497 | ZRMN-133 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135442 | ECWA-181 | 115 | 135495 | YNG-181 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135449 | GR.I-182 | 115 | 135538 | LONG-182 | 115 | 1 | Not Available
135437 | CLSP-181 | 115 | 135495 | YNG-181 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135498 | ZRMN-130 | 115 | 1 | Not Available
147850 | NIAG115E | 115 | 147842 | NIAGAR2W | 230 | 1 | TR | BK T1 | F - Transformer | F - Transformer | F - Transformer
130834 | N.BRW115 | 115 | 135437 | CLSP-181 | 115 | 1 | Not Available
130847 | ROLL | 115 | 130857 | STOLE115 | 115 | 1 | Not Available
135443 | ECWA-182 | 115 | 135459 | NI.B-182 | 115 | 1 | Not Available
135443 | ECWA-182 | 115 | 135496 | YNG-182 | 115 | 1 | Not Available
130766 | ROBIN230 | 230 | 147841 | NIAGAR2E | 230 | 1 | LN | 64 | L - Bus Work | L - Bus Work | L - Bus Work
135460 | PACK(N)E | 115 | 147850 | NIAG115E | 115 | 2 | LN | 192 | A - Conductor | A - Conductor | A - Conductor
135433 | AMHST-38 | 115 | 135472 | S129-38 | 115 | 1 | Not Available
135434 | AMHST-39 | 115 | 135473 | S129-39 | 115 | 1 | Not Available
135434 | AMHST-39 | 115 | 135478 | S140-39 | 115 | 1 | Not Available
135441 | FMC-39 | 115 | 135473 | S129-39 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135472 | S129-38 | 115 | 1 | LN | 39-1 | D - Disconnect | A - Conductor | A - Conductor
135452 | LOCKPORT | 115 | 135510 | SHAW-102 | 115 | 1 | Not Available
135453 | LONG-180 | 115 | 147850 | NIAG115E | 115 | 1 | Not Available
135460 | PACK(N)E | 115 | 147850 | NIAG115E | 115 | 1 | LN | 194 | A - Conductor | A - Conductor | A - Conductor
N-2 Normal - Locked Dispatch - 1000 MW Ontario Import
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
147850 | NIAG115E | 115 | 147842 | NIAGAR2W | 230 | 1 | TR | BK T1 | F - Transformer | F - Transformer | F - Transformer
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 1 | LN | 61 | A - Conductor | G - CT | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 2 | LN | 62 | A - Conductor | G - CT | A - Conductor
135303 | SAWYER77 | 230 | 135415 | PACKARD2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | B - Clearance
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
135304 | SAWYER78 | 230 | 135415 | PACKARD2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135303 | SAWYER77 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | A - Conductor
135458 | NI.B-181 | 115 | 135460 | PACK(N)E | 115 | 1 | LN | 181-1 | A - Conductor | A - Conductor | A - Conductor
135304 | SAWYER78 | 230 | 135414 | HUNTLEY2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135415 | PACKARD2 | 230 | 157062 | BECK_#2_BP76 | 230 | 1 | LN | BP76 | M - Voltage Regulator | A - Conductor | A - Conductor
135415 | PACKARD2 | 230 | 135460 | PACK(N)E | 115 | 1 | TR | BK 3 | F - Transformer | F - Transformer | F - Transformer
135450 | GRDNVL1 | 115 | 135453 | LONG-180 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135472 | S129-38 | 115 | 1 | LN | 39-1 | D - Disconnect | A - Conductor | A - Conductor
135441 | FMC-39 | 115 | 135473 | S129-39 | 115 | 1 | Not Available
135433 | AMHST-38 | 115 | 135472 | S129-38 | 115 | 1 | Not Available
135449 | GR.I-182 | 115 | 135459 | NI.B-182 | 115 | 1 | Not Available
135434 | AMHST-39 | 115 | 135473 | S129-39 | 115 | 1 | Not Available
135434 | AMHST-39 | 115 | 135478 | S140-39 | 115 | 1 | Not Available
135497 | ZRMN-133 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135460 | PACK(N)E | 115 | 135538 | LONG-182 | 115 | 1 | Not Available
130766 | ROBIN230 | 230 | 147841 | NIAGAR2E | 230 | 1 | LN | 64 | L - Bus Work | L - Bus Work | L - Bus Work
130834 | N.BRW115 | 115 | 135437 | CLSP-181 | 115 | 1 | Not Available
135437 | CLSP-181 | 115 | 135495 | YNG-181 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135449 | GR.I-182 | 115 | 135538 | LONG-182 | 115 | 1 | Not Available
130764 | MEYER230 | 230 | 131343 | MEYER M4 | 34.5 | 1 | TR | BK4P | F - Transformer | F - Transformer | F - Transformer
135451 | HUNTLEY1 | 115 | 135498 | ZRMN-130 | 115 | 1 | LN | 130-1 | A - Conductor | L - Bus Work | A - Conductor
135443 | ECWA-182 | 115 | 135496 | YNG-182 | 115 | 1 | Not Available
135443 | ECWA-182 | 115 | 135459 | NI.B-182 | 115 | 1 | Not Available
135442 | ECWA-181 | 115 | 135458 | NI.B-181 | 115 | 1 | Not Available
135442 | ECWA-181 | 115 | 135495 | YNG-181 | 115 | 1 | Not Available
135441 | FMC-39 | 115 | 135451 | HUNTLEY1 | 115 | 1 | Not Available
135383 | S219-182 | 115 | 135505 | WALDENTP | 115 | 1 | Not Available
135305 | SAWYER80 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 80 | A - Conductor | A - Conductor | A - Conductor
135452 | LOCKPORT | 115 | 135876 | TELRDTP1 | 115 | 1 | LN | 114-1 | A - Conductor | A - Conductor | A - Conductor
135460 | PACK(N)E | 115 | 147850 | NIAG115E | 115 | 2 | LN | 192 | A - Conductor | A - Conductor | A - Conductor
130815 | HINMN115 | 115 | 131611 | HARIS115 | 115 | 1 | LN | 908 | L - Bus Work | A - Conductor | G - CT
135452 | LOCKPORT | 115 | 135851 | SHEL-113 | 115 | 1 | Not Available
135453 | LONG-180 | 115 | 147850 | NIAG115E | 115 | 1 | Not Available
130764 | MEYER230 | 230 | 131122 | WTHRS230 | 230 | 1 | LN | 85 | A - Conductor | A - Conductor | L - Bus Work
130815 | HINMN115 | 115 | 135452 | LOCKPORT | 115 | 1 | LN | 100 | A - Conductor | A - Conductor | A - Conductor
130799 | ERIE 115 | 115 | 130834 | N.BRW115 | 115 | 1 | LN | 922 | G - CT | G - CT | G - CT
135306 | SAWYER79 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 79 | A - Conductor | A - Conductor | A - Conductor
135306 | SAWYER79 | 230 | 135418 | SUNY-79 | 230 | 1 | LN | 79 | A - Conductor | A - Conductor | B - Clearance
135305 | SAWYER80 | 230 | 135419 | SUNY-80 | 230 | 1 | LN | 80 | A - Conductor | A - Conductor | A - Conductor
135861 | MORTIMER | 115 | 149011 | S82-1115 | 115 | 1 | LN | 7X8272 | D - Disconnect | G - CT | G - CT
135383 | S219-182 | 115 | 135496 | YNG-182 | 115 | 1 | Not Available
135445 | FORD-142 | 115 | 135484 | S55-142 | 115 | 1 | Not Available
135269 | CLVB-142 | 115 | 135445 | FORD-142 | 115 | 1 | Not Available
135432 | AM.S-182 | 115 | 135505 | WALDENTP | 115 | 1 | Not Available
135433 | AMHST-38 | 115 | 135477 | S140-38 | 115 | 1 | Not Available
135415 | PACKARD2 | 230 | 135461 | PACK(S)W | 115 | 2 | TR | BK 4 | F - Transformer | F - Transformer | F - Transformer
135413 | GRDNVL2 | 230 | 135418 | SUNY-79 | 230 | 1 | LN | 79-1 | A - Conductor | A - Conductor | B - Clearance
135450 | GRDNVL1 | 115 | 135475 | S139-141 | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135475 | S139-141 | 115 | 135483 | S55-141 | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135268 | CLVB-141 | 115 | 135483 | S55-141 | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135413 | GRDNVL2 | 230 | 135419 | SUNY-80 | 230 | 1 | LN | 80-1 | A - Conductor | A - Conductor | B - Clearance
135452 | LOCKPORT | 115 | 135872 | SOUR-111 | 115 | 1 | LN | 111 | G - CT | G - CT | G - CT
135435 | SUMIT PK | 115 | 135454 | MLPN-129 | 115 | 1 | Not Available
135454 | MLPN-129 | 115 | 135461 | PACK(S)W | 115 | 1 | Not Available
135455 | MLPN-130 | 115 | 135461 | PACK(S)W | 115 | 1 | Not Available
135497 | ZRMN-133 | 115 | 135552 | OXBOWNUG | 115 | 1 | Not Available
N-2 Emergency - Locked Dispatch - 1000 MW Ontario Import
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
135303 | SAWYER77 | 230 | 135415 | PACKARD2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | B - Clearance
147850 | NIAG115E | 115 | 147842 | NIAGAR2W | 230 | 1 | TR | BK T1 | F - Transformer | F - Transformer | F - Transformer
135304 | SAWYER78 | 230 | 135415 | PACKARD2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
135303 | SAWYER77 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 1 | LN | 61 | A - Conductor | G - CT | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 2 | LN | 62 | A - Conductor | G - CT | A - Conductor
135304 | SAWYER78 | 230 | 135414 | HUNTLEY2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135415 | PACKARD2 | 230 | 157062 | BECK_#2_BP76 | 230 | 1 | LN | BP76 | M - Voltage Regulator | A - Conductor | A - Conductor
135497 | ZRMN-133 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135458 | NI.B-181 | 115 | 135460 | PACK(N)E | 115 | 1 | LN | 181-1 | A - Conductor | A - Conductor | A - Conductor
130815 | HINMN115 | 115 | 131611 | HARIS115 | 115 | 1 | LN | 908 | L - Bus Work | A - Conductor | G - CT
130764 | MEYER230 | 230 | 131343 | MEYER M4 | 34.5 | 1 | TR | BK4P | F - Transformer | F - Transformer | F - Transformer
130815 | HINMN115 | 115 | 135452 | LOCKPORT | 115 | 1 | LN | 100 | A - Conductor | A - Conductor | A - Conductor
135451 | HUNTLEY1 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135498 | ZRMN-130 | 115 | 1 | LN | 130-1 | A - Conductor | L - Bus Work | A - Conductor