## Legend
SERIES REACTORS ON 77 & 78 LINES IN-SERVICE
| Base Case Dispatch Distribution of | Niagara 115 kV units | Niagara 230 kV units | Lewiston
| Niagara Generation 115 kV vs. 230 kV units | MW Output | MW Output | MW Output
| Dispatch 1 | 1140 | 1320 | 240
| Dispatch 2 | 1540 | 920 | 240
Minimum Criteria:
Baseline results according to the minimum sufficiency criteria
Additional Information Beyond Minimum Criteria:
Transmission security results (N-1 and N-2) to provide additional information to developers showing potential overloads under conditions when importing the full 1000 MW from Ontario
Note for N-1-0 Analysis:
The term "base case" is used to describe violations where the system could not be adjusted following the first contingency to adequately secure the system to an element's continuous rating (Rate A)
| Sheet Name | Transmission Security Analysis | Transfer Criteria (Normal or Emergency) | OH -> NY Interchange (MW) | Ontario Re-Dispatch Adjustment (if applicable) | Public Policy Transmission Need Criteria
| Minimum_Criteria | Summary of the thermal and voltage violations under N-1, N-1-0, and N-1-1 conditions of the Public Policy Transmission Need
| Additional_Info_Beyond_Criteria | Summary of the informative thermal violations under N-1 and N-2 conditions beyond the mandatory criteria
| N-1_ETC_OH_1000 | N-1 | Emergency | 1000 | NA | Minimum Criteria
| N-1_NTC_OH_0 | N-1 | Normal | 0 | NA | Minimum Criteria
| N-1-1_NTC_OH_1000_Adjust | N-1-0 and N-1-1 | Normal | 1000 | Ontario Allowed to Adjust to an OH->NY Interchange of 0 MW | Minimum Criteria
| N-1-1_ETC_OH_1000_Adjust | N-1-0 and N-1-1 | Emergency | 1000 | Ontario Allowed to Adjust to an OH->NY Interchange of 0 MW | Minimum Criteria
| N-1_NTC_OH_1000 | N-1 | Normal | 1000 | NA | Additional Info Beyond Criteria
| N-2_NTC_OH_1000_Fixed | N-2 | Normal | 1000 | Ontario Dispatch Fixed | Additional Info Beyond Criteria
| N-2_ETC_OH_1000_Fixed | N-2 | Emergency | 1000 | Ontario Dispatch Fixed | Additional Info Beyond Criteria
| Ratings_Minimum_Criteria | Contains information on limiting equipment which the ratings are based for elements identified in the "Minimum_Criteria" tab
| Ratings_Beyond_Criteria | Contains information on limiting equipment which the ratings are based for elements identified in the "Additional_Infp_Beyond_Criteria" tab

## Minimum_Criteria
SERIES REACTORS ON 77 & 78 LINES IN-SERVICE
N-1 Thermal Overloads (Emergency Transfer Criteria) - 1000 MW Ontario Import
| Monitored Facility | Applicable | Dispatch 1 - Niagara 230 kV Max |  | Dispatch 2 - Niagara 115 kV Max
|  | Rating [MVA] | Contingency | AC % Loading | Contingency | AC % Loading
None
N-1 Thermal Overloads (Normal Transfer Criteria) - 0 MW Ontario Import
| Monitored Facility | Applicable | Dispatch 1 - Niagara 230 kV Max |  | Dispatch 2 - Niagara 115 kV Max
|  | Rating [MVA] | Contingency | AC % Loading | Contingency | AC % Loading
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 166 | DCT:115:180+182N | 112.23 | DCT:115:180+182N | 121.98
| 130762 GARDV230 230 130767 STOLE230 230 1 | 478 | DCT:230:77+78+THR | 112.2 | DCT:230:77+78+THR | 107.01
| 130847 ROLL 115 115 130857 STOLE115 115 1 | 90 | SB:181:ER | 103.19 | SB:181:ER | 103.11
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 (See footnote) | 351 | DCT:115:193+194 | 103.03 | DCT:115:193+194 | 122.53
| 135449 GR.I-182 115 135459 NI.B-182 115 1 | 181 | - | - | DCT:230:77+78 | 101.15
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 181 | - | - | NF:115:133 HT | 102.26
| 135451 HUNTLEY1 115 135562 S214-133 115 1 | 181 | - | - | SB:130:PK | 100.19
| 135460 PACK(N)E 115 135538 LONG-182 115 1 | 208 | - | - | DCT:115:180+181/922 | 106.27
| 135460 PACK(N)E 115 147850 NIAG115E 115 2 (See footnote) | 328 | - | - | DCT:115:101+191 | 111.63
| 135497 ZRMN-133 115 135562 S214-133 115 1 | 185 | - | - | SB:130:PK | 100.91
Footnote - Uses NYSRC Reliability Rule Exception #13. Developer must ensure that sufficient generation can be reduced at Niagara to return the flows to less than their STE ratings within 5 minutes and to less than their LTE ratings within 10 minutes from the initial overload.
N-1-0 Thermal Overloads (Normal Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
|  |  | Dispatch 1 |  |  | Dispatch 2
| Monitored Facility | Applicable Rating [MVA] | First Contingency | Second Contingency | AC %Loading | First Contingency | Second Contingency | AC %Loading
| 135327 AM.S-54 115 135450 GRDNVL1 115 1 | 129 | LN:115:181/922 | Base Case | 107.32 | LN:115:181/922 | Base Case | 107.79
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | - | - | - | LN:115:182S | Base Case | 101.97
| 135454 MLPN-129 115 135461 PACK(S)W 115 1 | 239 | - | - | - | LN:115:130 | Base Case | 100.02
N-1-1 Thermal Overloads (Normal Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
|  |  | Dispatch 1 |  |  | Dispatch 2
| Monitored Facility | Applicable Rating [MVA] | First Contingency | Second Contingency | AC %Loading | First Contingency | Second Contingency | AC %Loading
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 (See footnote) | 239 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 123.2 | PACKARD 230/115 3TR | T:77&78 | 100.13
| 130762 GARDV230 230 130767 STOLE230 230 1 | 478 | LN:115:180 | T:77&78 | 121.33 | WTHRS - MEYER 230 | T:77&78 | 118.08
| 130795 DEPEW115 115 130799 ERIE 115 115 1 | 119 | First:Lancaster_926B | LN:115:181/922 | 118.34 | First:Lancaster_926B | LN:115:181/922 | 118.07
| 135461 PACK(S)W 115 147851 NIAG115W 115 1 (See footnote) | 351 | LN:115:195 | LN:115:194 | 108.6 | LN:115:195 | LN:115:194 | 134.63
| 135461 PACK(S)W 115 147851 NIAG115W 115 2 (See footnote) | 351 | LN:115:195 | LN:115:193 | 108.6 | LN:115:193 | LN:115:195 | 134.63
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 (See footnote) | 351 | LN:115:193 | LN:115:194 | 101.5 | LN:115:193 | LN:115:194 | 125.23
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 (See footnote) | 841 | NIAGARA 230/115 1TR | T:61&64 | 100.61
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | 654 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 100.1 | - | - | -
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 (See footnote) | 841 | LN:115:192 | T:62&BP76 | 100.08 | - | - | -
| 135455 MLPN-130 115 135461 PACK(S)W 115 1 | 298 | - | - | - | NIAGARA 230/115 2TR | LN:115:129 | 101.21
| 135497 ZRMN-133 115 135562 S214-133 115 1 | 206 | - | - | - | HUNTLEY - PACKARD 78 230 | LN:115:130 | 100.35
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 206 | - | - | - | NIAGARA 230/115 2TR | LN:115:133 | 100.34
| 135454 MLPN-129 115 135461 PACK(S)W 115 1 | 298 | - | - | - | NIAGARA 230/115 2TR | LN:115:130 | 100
Footnote - Uses NYSRC Reliability Rule Exception #13. Developer must ensure that sufficient generation can be reduced at Niagara to return the flows to less than their STE ratings within 5 minutes and to less than their LTE ratings within 10 minutes from the initial overload.
N-1-0 Thermal Overloads (Emergency Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
|  |  | Dispatch 1 |  |  | Dispatch 2
| Monitored Facility | Applicable Rating [MVA] | First Contingency | Second Contingency | AC %Loading | First Contingency | Second Contingency | AC %Loading
| 135327 AM.S-54 115 135450 GRDNVL1 115 1 | 236 | LN:115:181/922 | Base Case | 107.03 | LN:115:181/922 | Base Case | 106.83
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | LN:115:182S | Base Case | 104.07 | LN:115:182S | Base Case | 111.55
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 288 | HUNTLEY - GARDENVILL 79 230 | Base Case | 100.04 | - | - | -
N-1-1 Thermal Overloads (Emergency Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
|  |  | Dispatch 1 - Niagara 230 kV Max |  |  | Dispatch 2 - Niagara 115 kV Max
| Monitored Facility | Applicable Rating [MVA] | First Contingency | Second Contingency | AC %Loading | First Contingency | Second Contingency | AC %Loading
| 130795 DEPEW115 115 130799 ERIE 115 115 1 | 119 | LN:115:705 NY | LN:115:181/922 | 122.06 | LN:115:705 NY | LN:115:181/922 | 122.14
| 135461 PACK(S)W 115 147851 NIAG115W 115 1 (See footnote) | 351 | LN:115:194 | LN:115:195 | 117.4 | LN:115:194 | LN:115:195 | 136.75
| 135461 PACK(S)W 115 147851 NIAG115W 115 2 (See footnote) | 351 | LN:115:193 | LN:115:195 | 117.4 | LN:115:193 | LN:115:195 | 136.75
| 130762 GARDV230 230 130767 STOLE230 230 1 | 478 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 110.64 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 106.5
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 | 351 | LN:115:193 | LN:115:194 | 107.35 | LN:115:193 | LN:115:194 | 126.93
| 130815 HINMN115 115 131611 HARIS115 115 1 | 306 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 100.01 | - | - | -
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 288 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 100.01 | - | - | -
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 206 | - | - | - | NIAGARA 230/115 2TR | LN:115:133 | 100.28
| 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | 180 | - | - | - | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 100.03
| 135455 MLPN-130 115 135461 PACK(S)W 115 1 | 298 | - | - | - | NIAGARA 230/115 2TR | LN:115:129 | 101.25
| 135467 SHAW-103 115 135470 SWAN-103 115 1 | 206 | - | - | - | LN:115:101 | LN:115:102 | 101.32
| 135497 ZRMN-133 115 135562 S214-133 115 1 | 206 | - | - | - | First:Lockport_104 | LN:115:130 | 100.05
Footnote - Uses NYSRC Reliability Rule Exception #13. Developer must ensure that sufficient generation can be reduced at Niagara to return the flows to less than their STE ratings within 5 minutes and to less than their LTE ratings within 10 minutes from the initial overload.
| Voltage Violations |  | Key Contingency |  |  | Monitored Facility
| Multiple instances of low-voltage and non-convergence violations under both N-1 and N-1-1 conditions for all cases; load was modified (PQBRK = 0.7) to solve cases. |  | Any combination resulting in the loss of two out of three Sawyer transformers under N-1 (Towers 77&80, 79&80) or N-1-1 (any combination of the 77, 79, 80 lines) |  |  | HUNTLEY 230 kV and GARDENVILLE 230 kV

## Additional_Info_Beyond_Criteria
SERIES REACTORS ON 77 & 78 LINES IN-SERVICE
N-1 Thermal Overloads (NTC) - 1000 MW Ontario Import
| Monitored Facility | Applicable | Dispatch 1 - Niagara 230 kV Max |  | Dispatch 2 - Niagara 115 kV Max
|  | Rating [MVA] | Contingency | AC % Loading | Contingency | AC % Loading
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 (See footnote) | 239 | DCT:230:77+78+THR | 125.6 | - | -
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 166 | DCT:230:77+78 | 124.28 | DCT:115:180+182N | 130.06
| 130762 GARDV230 230 130767 STOLE230 230 1 | 478 | DCT:230:77+78+THR | 114.4 | DCT:230:77+78+THR | 109.61
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 (See footnote) | 351 | DCT:115:193+194 | 109.93 | DCT:115:193+194 | 129.47
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 (See footnote) | 841 | T:62&BP76 | 108.97 | - | -
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 181 | NF:115:133 HT | 108.74 | NF:115:133 HT | 117.5
| 135460 PACK(N)E 115 135538 LONG-182 115 1 | 208 | DCT:230:77+78 | 108.62 | DCT:230:77+78 | 113.06
| 130795 DEPEW115 115 130799 ERIE 115 115 1 | 119 | SB:PK115 30+40 | 108.35 | SB:PK115 30+40 | 108.78
| 135449 GR.I-182 115 135459 NI.B-182 115 1 | 181 | DCT:230:77+78+THR | 107.8 | DCT:230:77+78+THR | 112.96
| 135497 ZRMN-133 115 135562 S214-133 115 1 | 185 | DCT:230:77+78+THR | 107.43 | SB:130:PK | 114.24
| 135451 HUNTLEY1 115 135562 S214-133 115 1 | 181 | DCT:230:77+78+THR | 106.59 | SB:130:PK | 113.82
| 135442 ECWA-181 115 135458 NI.B-181 115 1 | 181 | DCT:230:77+78 | 105.52 | DCT:230:77+78 | 110.06
| 135442 ECWA-181 115 135495 YNG-181 115 1 | 181 | DCT:230:77+78 | 104.92 | DCT:230:77+78 | 109.42
| 135449 GR.I-182 115 135538 LONG-182 115 1 | 208 | DCT:230:77+78 | 104.37 | DCT:230:77+78 | 108.92
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 (See footnote) | 841 | DCT:230:61+64 | 103.23 | - | -
| 135437 CLSP-181 115 135495 YNG-181 115 1 | 163 | DCT:230:77+78 | 101.86 | DCT:230:77+78 | 106.6
| 130847 ROLL 115 115 130857 STOLE115 115 1 | 90 | SB:181:ER | 101.77 | SB:181:ER | 101.74
| 135443 ECWA-182 115 135496 YNG-182 115 1 | 181 | DCT:230:77+78+THR | 101.61 | DCT:230:77+78+THR | 106.85
| 135443 ECWA-182 115 135459 NI.B-182 115 1 | 181 | DCT:230:77+78+THR | 101.51 | DCT:230:77+78+THR | 106.71
| 130834 N.BRW115 115 135437 CLSP-181 115 1 | 163 | DCT:230:77+78 | 101.01 | DCT:230:77+78 | 105.75
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | 654 | LN:230:77 | 100.9 | - | -
| 135433 AMHST-38 115 135472 S129-38 115 1 | 151 | - | - | DCT:230:77+78 | 100.05
| 135441 FMC-39 115 135473 S129-39 115 1 | 151 | - | - | DCT:230:77+78 | 101.64
| 135451 HUNTLEY1 115 135472 S129-38 115 1 | 151 | - | - | DCT:230:77+78 | 102.57
| 135452 LOCKPORT 115 135510 SHAW-102 115 1 | 253 | - | - | SB:37:LP | 103.52
| 135455 MLPN-130 115 135461 PACK(S)W 115 1 | 298 | - | - | SB:WAL:129+133 | 100.36
| 135460 PACK(N)E 115 147850 NIAG115E 115 2 (See footnote) | 328 | - | - | DCT:115:101+191 | 109.36
Footnote - Uses NYSRC Reliability Rule Exception #13. Developer must ensure that sufficient generation can be reduced at Niagara to return the flows to less than their STE ratings within 5 minutes and to less than their LTE ratings within 10 minutes from the initial overload.
N-2 Normal Transfer Criteria - Locked Dispatch - OH Import 1000
| Monitored Facility | Niagara Dispatch | First Contingency | Second contingency | Base Case Rating (MVA) | Contingency Rating (MVA) | Final AC %Loading
| 130754 SOMERSET345 345 149690 NEWROCH345 345 1 | Dispatch 1 | STOLLRD - SHLDON 67 230 | HILLSIDE 230/115 4TR | 1301 | 1501 | NConv
| 130762 GARDV230 230 130767 STOLE230 230 1 | Dispatch 1 | MEYER - CANDQUA 60 230 | T:72&69 | 474 | 478 | NConv
| 130766 ROBIN230 230 130767 STOLE230 230 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 550 | 637 | NConv
| 130766 ROBIN230 230 147841 NIAGAR2E 230 1 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 496 | 657 | NConv
| 130775 BIGTR115 115 131467 LANGN115 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 163 | NConv
| 130795 DEPEW115 115 130799 ERIE 115 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 119 | 119 | NConv
| 130799 ERIE 115 115 130834 N.BRW115 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 124 | 139 | NConv
| 130806 GARDV115 115 131467 LANGN115 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 163 | NConv
| 130815 HINMN115 115 131611 HARIS115 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 238 | 287 | NConv
| 130815 HINMN115 115 135452 LOCKPORT 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 220 | 252 | NConv
| 130834 N.BRW115 115 135437 CLSP-181 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 163 | NConv
| 130846 ROBIN115 115 130853 A.LUD TP 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 215 | 247 | NConv
| 130853 A.LUD TP 115 131611 HARIS115 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 215 | 247 | NConv
| 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 444 | 444 | NConv
| 135253 S224-36 115 135256 S214-36 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
| 135254 S224-37 115 135451 HUNTLEY1 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 148 | 148 | NConv
| 135256 S214-36 115 135451 HUNTLEY1 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 176 | NConv
| 135268 CLVB-141 115 135292 SHALTNTP 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
| 135268 CLVB-141 115 135483 S55-141 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
| 135269 CLVB-142 115 135445 FORD-142 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
| 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
| 135270 DELMTR-1 115 135287 NANG-141 115 1 | Dispatch 2 | LN:115:142 | T:73&74 | 88 | 101 | 101.77
| 135270 DELMTR-1 115 135579 LAKEV141 115 1 | Dispatch 2 | LN:115:142 | T:73&74 | 88 | 101 | 101.88
| 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
| 135277 FALCONER 115 200579 26WARREN 115 1 | Dispatch 2 | SRIPL - ERIE E 69 230 | SIN:90 | 116 | 116 | 113.56
| 135284 MCHS-151 115 135401 GERNATT 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 129 | 148 | NConv
| 135292 SHALTNTP 115 135579 LAKEV141 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
| 135305 SAWYER80 230 135309 SAWYERB3 230 1 | Dispatch 1 | HUNTLEY - GARDENVILL 79 230 | T:77&78 | 220 | 252 | 105.37
| 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
| 135305 SAWYER80 230 135419 SUNY-80 230 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
| 135306 SAWYER79 230 135308 SAWYERB2 230 1 | Dispatch 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&80 | 220 | 252 | 109.28
| 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
| 135306 SAWYER79 230 135418 SUNY-79 230 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
| 135327 AM.S-54 115 135450 GRDNVL1 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 129 | 182 | NConv
| 135327 AM.S-54 115 135493 LUDWIG 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 187 | 215 | NConv
| 135383 S219-182 115 135496 YNG-182 115 1 | Dispatch 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
| 135383 S219-182 115 135505 WALDENTP 115 1 | Dispatch 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 181 | NConv
| 135401 GERNATT 115 147875 ARCADE 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 129 | 148 | NConv
| 135413 GRDNVL2 230 135418 SUNY-79 230 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
| 135413 GRDNVL2 230 135419 SUNY-80 230 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
| 135415 PACKARD2 230 135460 PACK(N)E 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 189 | 250 | NConv
| 135415 PACKARD2 230 135461 PACK(S)W 115 2 | Dispatch 2 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 190 | 250 | 117.59
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 620 | 841 | NConv
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 620 | 841 | NConv
| 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 500 | 587 | NConv
| 135432 AM.S-182 115 135450 GRDNVL1 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 129 | 182 | 126.52
| 135432 AM.S-182 115 135505 WALDENTP 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 185 | 125.09
| 135433 AMHST-38 115 135472 S129-38 115 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
| 135433 AMHST-38 115 135477 S140-38 115 1 | Dispatch 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 132.92
| 135434 AMHST-39 115 135473 S129-39 115 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
| 135434 AMHST-39 115 135478 S140-39 115 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
| 135435 SUMIT PK 115 135454 MLPN-129 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 283 | NConv
| 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
| 135437 CLSP-181 115 135495 YNG-181 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 163 | NConv
| 135438 CLSP-54 115 135439 TUNGSTEN 115 1 | Dispatch 2 | LN:115:181/922 | Base Case | 129 | 182 | 100.68
| 135441 FMC-39 115 135451 HUNTLEY1 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 181 | 134.83
| 135441 FMC-39 115 135473 S129-39 115 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
| 135442 ECWA-181 115 135458 NI.B-181 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
| 135442 ECWA-181 115 135495 YNG-181 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
| 135443 ECWA-182 115 135459 NI.B-182 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
| 135443 ECWA-182 115 135496 YNG-182 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
| 135445 FORD-142 115 135484 S55-142 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
| 135449 GR.I-182 115 135459 NI.B-182 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
| 135449 GR.I-182 115 135538 LONG-182 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 200 | 208 | NConv
| 135450 GRDNVL1 115 135453 LONG-180 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 160 | 206 | NConv
| 135450 GRDNVL1 115 135475 S139-141 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
| 135450 GRDNVL1 115 135503 DALE-38 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 129 | 181 | 105.59
| 135450 GRDNVL1 115 135504 DALE-39 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 129 | 181 | 109.2
| 135451 HUNTLEY1 115 135472 S129-38 115 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 181 | NConv
| 135451 HUNTLEY1 115 135562 S214-133 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 181 | NConv
| 135452 LOCKPORT 115 135464 SANBORNT 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 233 | 253 | NConv
| 135452 LOCKPORT 115 135467 SHAW-103 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
| 135452 LOCKPORT 115 135510 SHAW-102 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 233 | 253 | NConv
| 135452 LOCKPORT 115 135851 SHEL-113 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 165 | NConv
| 135452 LOCKPORT 115 135865 NAKR-108 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 130 | 136 | NConv
| 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 131 | 144 | NConv
| 135452 LOCKPORT 115 135872 SOUR-111 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 199 | 199 | NConv
| 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 220 | 252 | NConv
| 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 165 | NConv
| 135453 LONG-180 115 147850 NIAG115E 115 1 (See footnote) | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 265 | 114.22
| 135454 MLPN-129 115 135461 PACK(S)W 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
| 135455 MLPN-130 115 135461 PACK(S)W 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
| 135455 MLPN-130 115 135469 SUMIT PK 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
| 135456 MTNS-120 115 135470 SWAN-103 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 176 | 211 | NConv
| 135456 MTNS-120 115 147850 NIAG115E 115 1 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 176 | 258 | NConv
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 160 | 166 | NConv
| 135460 PACK(N)E 115 135538 LONG-182 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 200 | 208 | NConv
| 135460 PACK(N)E 115 147850 NIAG115E 115 2 (See footnote) | Dispatch 2 | NIAGARA - PACKARD 62 230 | T:61&191 | 247 | 328 | 125.19
| 135461 PACK(S)W 115 147851 NIAG115W 115 1 (See footnote) | Dispatch 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
| 135461 PACK(S)W 115 147851 NIAG115W 115 2 (See footnote) | Dispatch 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
| 135464 SANBORNT 115 147850 NIAG115E 115 1 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 247 | 275 | NConv
| 135467 SHAW-103 115 135470 SWAN-103 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 181 | NConv
| 135468 SNBRN102 115 135510 SHAW-102 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 275 | 303 | NConv
| 135468 SNBRN102 115 147850 NIAG115E 115 1 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 247 | 275 | NConv
| 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
| 135475 S139-141 115 135483 S55-141 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
| 135477 S140-38 115 135481 S54-38 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 121.21
| 135478 S140-39 115 135482 S54-39 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 120.35
| 135479 S154-38 115 135485 S61-38 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 114.18
| 135479 S154-38 115 135492 WALDENTP 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 113.26
| 135480 S154-39 115 135486 S61-39 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 113.12
| 135480 S154-39 115 135504 DALE-39 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 112.15
| 135482 S54-39 115 135486 S61-39 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 116.58
| 135492 WALDENTP 115 135503 DALE-38 115 1 | Dispatch 2 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 105.59
| 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
| 135497 ZRMN-133 115 135562 S214-133 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 185 | NConv
| 147841 NIAGAR2E 230 147834 NIAG 345 345 1 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 384 | 479 | NConv
| 147841 NIAGAR2E 230 147834 NIAG 345 345 2 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 384 | 479 | NConv
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 192 | 239 | NConv
Footnote - Uses NYSRC Reliability Rule Exception #13. Developer must ensure that sufficient generation can be reduced at Niagara to return the flows to less than their STE ratings within 5 minutes and to less than their LTE ratings within 10 minutes from the initial overload.
N-2 Emergency Transfer Criteria - Locked Dispatch - OH Import 1000
| Monitored Facility | Niagara Dispatch | First Contingency | Second contingency | Base Case Rating (MVA) | Contingency Rating (MVA) | Final AC %Loading
| 130762 GARDV230 230 130767 STOLE230 230 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 474 | 478 | NConv
| 130766 ROBIN230 230 130767 STOLE230 230 1 | Dispatch 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 550 | 717 | NConv
| 130766 ROBIN230 230 147841 NIAGAR2E 230 1 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 496 | 657 | NConv
| 130775 BIGTR115 115 131467 LANGN115 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 183 | NConv
| 130795 DEPEW115 115 130799 ERIE 115 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 119 | 119 | NConv
| 130799 ERIE 115 115 130834 N.BRW115 115 1 | Dispatch 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 124 | 159 | NConv
| 130806 GARDV115 115 131467 LANGN115 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 183 | NConv
| 130815 HINMN115 115 131611 HARIS115 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 238 | 306 | NConv
| 130815 HINMN115 115 135452 LOCKPORT 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 220 | 280 | NConv
| 130834 N.BRW115 115 135437 CLSP-181 115 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 139 | 181 | NConv
| 130846 ROBIN115 115 130853 A.LUD TP 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 215 | 275 | NConv
| 130853 A.LUD TP 115 131611 HARIS115 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 215 | 275 | NConv
| 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | Dispatch 1 | HILLSIDE 230/115 4TR | B:MEYER | 444 | 444 | NConv
| 135254 S224-37 115 135451 HUNTLEY1 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 148 | 148 | NConv
| 135256 S214-36 115 135451 HUNTLEY1 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 176 | NConv
| 135268 CLVB-141 115 135292 SHALTNTP 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
| 135268 CLVB-141 115 135483 S55-141 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
| 135269 CLVB-142 115 135445 FORD-142 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
| 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
| 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
| 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
| 135305 SAWYER80 230 135419 SUNY-80 230 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
| 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
| 135306 SAWYER79 230 135418 SUNY-79 230 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 710 | NConv
| 135327 AM.S-54 115 135450 GRDNVL1 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 129 | 236 | NConv
| 135327 AM.S-54 115 135493 LUDWIG 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 187 | 236 | NConv
| 135413 GRDNVL2 230 135418 SUNY-79 230 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 699 | NConv
| 135413 GRDNVL2 230 135419 SUNY-80 230 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 722 | NConv
| 135415 PACKARD2 230 135460 PACK(N)E 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 189 | 250 | NConv
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 (See footnote) | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 620 | 841 | NConv
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 (See footnote) | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 620 | 841 | NConv
| 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | Dispatch 1 | NIAGARA - PACKARD 61 230 | B:PACKT4 | 500 | 587 | 113.93
| 135435 SUMIT PK 115 135454 MLPN-129 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 283 | NConv
| 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
| 135437 CLSP-181 115 135495 YNG-181 115 1 | Dispatch 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 139 | 183 | NConv
| 135438 CLSP-54 115 135439 TUNGSTEN 115 1 | Dispatch 2 | LN:115:181/922 | Base Case | 129 | 239 | 100.68
| 135442 ECWA-181 115 135458 NI.B-181 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
| 135442 ECWA-181 115 135495 YNG-181 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
| 135443 ECWA-182 115 135459 NI.B-182 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
| 135443 ECWA-182 115 135496 YNG-182 115 1 | Dispatch 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
| 135445 FORD-142 115 135484 S55-142 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
| 135449 GR.I-182 115 135459 NI.B-182 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
| 135449 GR.I-182 115 135538 LONG-182 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 200 | 265 | NConv
| 135450 GRDNVL1 115 135453 LONG-180 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 160 | 206 | NConv
| 135450 GRDNVL1 115 135475 S139-141 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 206 | NConv
| 135451 HUNTLEY1 115 135562 S214-133 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 206 | NConv
| 135452 LOCKPORT 115 135464 SANBORNT 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 233 | 318 | NConv
| 135452 LOCKPORT 115 135467 SHAW-103 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 199 | NConv
| 135452 LOCKPORT 115 135510 SHAW-102 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 233 | 318 | NConv
| 135452 LOCKPORT 115 135851 SHEL-113 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 180 | NConv
| 135452 LOCKPORT 115 135865 NAKR-108 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 130 | 165 | NConv
| 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 131 | 158 | NConv
| 135452 LOCKPORT 115 135872 SOUR-111 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 199 | 199 | NConv
| 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | Dispatch 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 220 | 280 | NConv
| 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 180 | NConv
| 135454 MLPN-129 115 135461 PACK(S)W 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
| 135455 MLPN-130 115 135461 PACK(S)W 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
| 135455 MLPN-130 115 135469 SUMIT PK 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
| 135456 MTNS-120 115 135470 SWAN-103 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 176 | 240 | NConv
| 135456 MTNS-120 115 147850 NIAG115E 115 1 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 176 | 258 | NConv
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 160 | 206 | NConv
| 135460 PACK(N)E 115 135538 LONG-182 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 200 | 265 | NConv
| 135461 PACK(S)W 115 147851 NIAG115W 115 1 (See footnote) | Dispatch 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
| 135461 PACK(S)W 115 147851 NIAG115W 115 2 (See footnote) | Dispatch 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
| 135464 SANBORNT 115 147850 NIAG115E 115 1 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 247 | 328 | NConv
| 135467 SHAW-103 115 135470 SWAN-103 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 206 | NConv
| 135468 SNBRN102 115 135510 SHAW-102 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 275 | 354 | NConv
| 135468 SNBRN102 115 147850 NIAG115E 115 1 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 247 | 328 | NConv
| 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
| 135475 S139-141 115 135483 S55-141 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
| 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
| 135497 ZRMN-133 115 135562 S214-133 115 1 | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 206 | NConv
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 (See footnote) | Dispatch 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 192 | 288 | NConv
Footnote - Uses NYSRC Reliability Rule Exception #13. Developer must ensure that sufficient generation can be reduced at Niagara to return the flows to less than their STE ratings within 5 minutes and to less than their LTE ratings within 10 minutes from the initial overload.

## N-1_ETC_OH_1000
SERIES REACTORS ON 77 & 78 LINES IN-SERVICE
Niagara Dispatch | Monitored Facility | Contingency | Rate Base (MVA) | Rate Cont (MVA) | Final AC %Loading

## N-1_NTC_OH_0
SERIES REACTORS ON 77 & 78 LINES IN-SERVICE
Scenario | Monitored Facility | Areas | Rate Base (MVA) | Rate Cont (MVA) | Cont Name | Final AC %Loading
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 1 | 474 | 478 | DCT:230:77+78+THR | 112.2
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 1 | 474 | 478 | DCT:230:77+78 | 112.12
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 1 | 474 | 478 | T:77&78 | 112.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 1 | 474 | 478 | DCT:230:77+78+THR | 107.01
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 1 | 474 | 478 | DCT:230:77+78 | 106.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 1 | 474 | 478 | T:77&78 | 106.97
| 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  |  |  | 112.2
Dispatch 1 | 130847 ROLL 115 115 130857 STOLE115 115 1 | 1 | 90 | 90 | SB:181:ER | 103.19
Dispatch 2 | 130847 ROLL 115 115 130857 STOLE115 115 1 | 1 | 90 | 90 | SB:181:ER | 103.11
| 130847 ROLL 115 115 130857 STOLE115 115 1 Max |  |  |  |  | 103.19
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | 1 | 220 | 252 | DCT:230:77+80 | 103.9
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | 1 | 220 | 252 | T:77&80 | 103.9
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | 1 | 220 | 252 | DCT:230:77+80 | 102.55
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | 1 | 220 | 252 | T:77&80 | 102.55
| 135306 SAWYER79 230 135308 SAWYERB2 230 1 Max |  |  |  |  | 103.9
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 1 | 174 | 181 | DCT:230:77+78 | 101.15
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 1 | 174 | 181 | T:77&78 | 101.15
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 1 | 174 | 181 | DCT:230:77+78+THR | 101.14
| 135449 GR.I-182 115 135459 NI.B-182 115 1 Max |  |  |  |  | 101.15
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 1 | 168 | 181 | NF:115:133 HT | 102.26
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 Max |  |  |  |  | 102.26
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 1 | 168 | 181 | SB:130:PK | 100.19
| 135451 HUNTLEY1 115 135562 S214-133 115 1 Max |  |  |  |  | 100.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:115:180+182N | 121.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:115:180+182S | 119.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:77+78 | 116.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | T:77&78 | 116.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:77+78+THR | 116.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:115:54+182S | 115.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:115:180+182N | 112.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:77+78 | 112.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | T:77&78 | 112.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:77+78+THR | 112.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:115:180+182S | 110.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | SB:GI115 | 109.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:115:54+182S | 109.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | SB:182N:PK | 109.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:79+80+THR+ELM3-4 | 108.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:79+80+ELM3-4 | 108.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | BUS:115:PK-30 | 108.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | LN:115:182S | 107.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | LN:115:182S | 107.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | LN:115:182N | 107.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | LN:115:182N | 107.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | NF:115:182 GI-N | 107.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | NF:115:182 PK | 106.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:79+80 | 104.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | T:79&80 | 104.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:79+80+THR | 104.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:79+80+THR+ELM3-4 | 104.12
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:79+80+ELM3-4 | 104.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:79+80+THR+ELM1-2 | 103.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | NF:115:182 GI-S | 103.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:79+80+ELM1-2 | 103.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | DCT:230:79+80+ELM1-2 | 103.94
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | SB:GI115 | 102.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | LN:115:182S | 100.87
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 1 | 160 | 166 | LN:115:182S | 100.87
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 Max |  |  |  |  | 121.98
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 1 | 200 | 208 | DCT:115:180+181/922 | 106.27
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 1 | 200 | 208 | DCT:230:77+78 | 102.61
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 1 | 200 | 208 | T:77&78 | 102.61
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 1 | 200 | 208 | DCT:230:77+78+THR | 102.54
| 135460 PACK(N)E 115 135538 LONG-182 115 1 Max |  |  |  |  | 106.27
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | 1 | 247 | 328 | DCT:115:101+191 | 111.63
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | 1 | 247 | 328 | DCT:230:61+191 | 107.09
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | 1 | 247 | 328 | T:61&191 | 107.09
| 135460 PACK(N)E 115 147850 NIAG115E 115 2 Max |  |  |  |  | 111.63
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | 1 | 273 | 351 | DCT:115:193+194 | 122.53
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | 1 | 273 | 351 | DCT:115:193+194 | 103.03
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | 1 | 273 | 351 | SB:129:PK | 102.39
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | 1 | 273 | 351 | BUS:115:PK-60 | 100.86
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 Max |  |  |  |  | 122.53
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 1 | 168 | 185 | SB:130:PK | 100.91
| 135497 ZRMN-133 115 135562 S214-133 115 1 Max |  |  |  |  | 100.91
| Grand Max |  |  |  |  | 122.53

## N-1-1_NTC_OH_1000_Adjust
SERIES REACTORS ON 77 & 78 LINES IN-SERVICE
Niagara Dispatch | Monitored Facility | First Level Scenario | Cont Name | Rate Base (MVA) | Rate Cont (MVA) | SCD AC %Loading
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:180 | T:77&78 | 474 | 478 | 121.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:182N | T:77&78 | 474 | 478 | 120.6
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:345:37S-FM-FV-HC | T:77&78 | 474 | 478 | 119.93
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 474 | 478 | 119.64
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:182S | T:77&78 | 474 | 478 | 119.36
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 474 | 478 | 119.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 474 | 478 | 119.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:77&78 | 474 | 478 | 119.05
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - HOMERCTY | T:77&78 | 474 | 478 | 118.75
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 474 | 478 | 118.26
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | T:77&78 | 474 | 478 | 118.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:77&78 | 474 | 478 | 118.08
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:345:37S-FM-FV-HC | T:77&78 | 474 | 478 | 117.96
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | T:77&78 | 474 | 478 | 117.95
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:180 | T:77&78 | 474 | 478 | 117.51
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:345:37S-FM-FV | T:77&78 | 474 | 478 | 117.08
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 474 | 478 | 116.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 474 | 478 | 116.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 474 | 478 | 116.79
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | T:77&78 | 474 | 478 | 116.62
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:38 | T:77&78 | 474 | 478 | 116.52
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 474 | 478 | 116.42
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 474 | 478 | 116.41
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:181/922 | T:77&78 | 474 | 478 | 116.18
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:39 | T:77&78 | 474 | 478 | 116.17
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - HOMERCTY | T:77&78 | 474 | 478 | 115.84
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:345:37S-FM-FV | T:77&78 | 474 | 478 | 115.71
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | T:77&78 | 474 | 478 | 115.05
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | T:77&78 | 474 | 478 | 114.82
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:38 | T:77&78 | 474 | 478 | 114.69
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS1 | T:77&78 | 474 | 478 | 114.2
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:ROB | T:77&78 | 474 | 478 | 114.15
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:182N | T:77&78 | 474 | 478 | 114.14
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:39 | T:77&78 | 474 | 478 | 114.11
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:INDEK-OL | T:77&78 | 474 | 478 | 114.09
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_922 | T:77&78 | 474 | 478 | 113.58
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 474 | 478 | 113.48
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:NI1 | T:77&78 | 474 | 478 | 113.47
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 1TR | T:77&78 | 474 | 478 | 113.47
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | T:77&78 | 474 | 478 | 113.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:133 | T:77&78 | 474 | 478 | 113.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:129 | T:77&78 | 474 | 478 | 112.95
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_907 | T:77&78 | 474 | 478 | 112.93
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 474 | 478 | 112.85
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:907 NY | T:77&78 | 474 | 478 | 112.74
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 474 | 478 | 112.65
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 474 | 478 | 112.65
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 474 | 478 | 112.65
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:130 | T:77&78 | 474 | 478 | 112.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN7 | T:77&78 | 474 | 478 | 112.56
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:182S | T:77&78 | 474 | 478 | 112.44
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - INDEPNC 26 345 | T:77&78 | 474 | 478 | 112.1
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 1 | T:77&78 | 474 | 478 | 111.94
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 2 | T:77&78 | 474 | 478 | 111.94
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 3 | T:77&78 | 474 | 478 | 111.94
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:181/922 | T:77&78 | 474 | 478 | 111.91
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:966 NY | T:77&78 | 474 | 478 | 111.5
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 4 MILE - ERIE SE 230 | T:77&78 | 474 | 478 | 111.46
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS2 | T:77&78 | 474 | 478 | 111.45
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:DUPONT46 | T:77&78 | 474 | 478 | 111.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 10 | T:77&78 | 474 | 478 | 111.16
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 8 | T:77&78 | 474 | 478 | 111.16
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 9 | T:77&78 | 474 | 478 | 111.16
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 11 | T:77&78 | 474 | 478 | 111.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 12 | T:77&78 | 474 | 478 | 111.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 13 | T:77&78 | 474 | 478 | 111.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/1:FMR | T:77&78 | 474 | 478 | 111.12
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE 345/115 1TR | T:77&78 | 474 | 478 | 111.12
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:9 MI PT2 | T:77&78 | 474 | 478 | 111.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS1 | T:77&78 | 474 | 478 | 111.01
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:968 NY | T:77&78 | 474 | 478 | 110.94
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 474 | 478 | 110.92
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:OXBOWNUG | T:77&78 | 474 | 478 | 110.88
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:INDEK-OL | T:77&78 | 474 | 478 | 110.88
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 474 | 478 | 110.84
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | T:77&78 | 474 | 478 | 110.82
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:HUN | T:77&78 | 474 | 478 | 110.79
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:ROB | T:77&78 | 474 | 478 | 110.79
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:345:SOMERSET | T:77&78 | 474 | 478 | 110.71
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:KINTIGH | T:77&78 | 474 | 478 | 110.71
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:PK3 | T:77&78 | 474 | 478 | 110.67
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 474 | 478 | 110.65
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:37 | T:77&78 | 474 | 478 | 110.62
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:46 | T:77&78 | 474 | 478 | 110.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 4 | T:77&78 | 474 | 478 | 110.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 5 | T:77&78 | 474 | 478 | 110.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 6 | T:77&78 | 474 | 478 | 110.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 7 | T:77&78 | 474 | 478 | 110.6
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:SITHE 1 | T:77&78 | 474 | 478 | 110.59
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:SITHE 2 | T:77&78 | 474 | 478 | 110.59
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 110.58
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | T:77&78 | 474 | 478 | 110.58
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 110.58
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:UDG-184 | T:77&78 | 474 | 478 | 110.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:36 | T:77&78 | 474 | 478 | 110.54
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:171 | T:77&78 | 474 | 478 | 110.54
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - VOL 21 345 | T:77&78 | 474 | 478 | 110.47
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 3TR | T:77&78 | 474 | 478 | 110.47
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:OSWEGO 6 | T:77&78 | 474 | 478 | 110.43
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - 9MI1 8 345 | T:77&78 | 474 | 478 | 110.4
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:PK4 | T:77&78 | 474 | 478 | 110.39
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 4TR | T:77&78 | 474 | 478 | 110.39
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:9MIPT1 | T:77&78 | 474 | 478 | 110.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:NI2 | T:77&78 | 474 | 478 | 110.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 2TR | T:77&78 | 474 | 478 | 110.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 1-3 | T:77&78 | 474 | 478 | 110.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 4-6 | T:77&78 | 474 | 478 | 110.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 7-9 | T:77&78 | 474 | 478 | 110.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 10-12 | T:77&78 | 474 | 478 | 110.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:953 NY | T:77&78 | 474 | 478 | 110.26
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | MAINSBRG 345/115 1TR | T:77&78 | 474 | 478 | 110.25
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:AMERT | T:77&78 | 474 | 478 | 110.21
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:FITZPATR | T:77&78 | 474 | 478 | 110.2
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:OSWEGO 5 | T:77&78 | 474 | 478 | 110.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:SENECA | T:77&78 | 474 | 478 | 110.15
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:110 | T:77&78 | 474 | 478 | 110.12
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_103 | T:77&78 | 474 | 478 | 110.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 474 | 478 | 110.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 474 | 478 | 110.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 474 | 478 | 110.11
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:ESYR | T:77&78 | 474 | 478 | 110.08
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - VOLNEY 6 345 | T:77&78 | 474 | 478 | 110.06
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:133 | T:77&78 | 474 | 478 | 110.03
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_104 | T:77&78 | 474 | 478 | 110
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | T:77&78 | 474 | 478 | 109.99
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:HOORKN86 | T:77&78 | 474 | 478 | 109.99
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:HOORKN85 | T:77&78 | 474 | 478 | 109.97
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:151 | T:77&78 | 474 | 478 | 109.92
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:STL1_G1 | T:77&78 | 474 | 478 | 109.89
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:STL1_G2 | T:77&78 | 474 | 478 | 109.89
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - EDIC 2-15 345 | T:77&78 | 474 | 478 | 109.88
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | T:77&78 | 474 | 478 | 109.83
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:MODERNLF | T:77&78 | 474 | 478 | 109.82
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:Q234_CLIB_G10 | T:77&78 | 474 | 478 | 109.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:Q234_CLIB_G20 | T:77&78 | 474 | 478 | 109.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAG - KINTIGH 345 | T:77&78 | 474 | 478 | 109.76
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/2:NI3 | T:77&78 | 474 | 478 | 109.72
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 345/230 4TR | T:77&78 | 474 | 478 | 109.72
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:932 NY | T:77&78 | 474 | 478 | 109.69
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 3 115 | T:77&78 | 474 | 478 | 109.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:119 | T:77&78 | 474 | 478 | 109.63
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:927 NY | T:77&78 | 474 | 478 | 109.6
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:113 | T:77&78 | 474 | 478 | 109.59
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ERIE E - 4 MILE 230 | T:77&78 | 474 | 478 | 109.59
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROBRD 230/115/34.5 1TR | T:77&78 | 474 | 478 | 109.59
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY 345/115 1TR | T:77&78 | 474 | 478 | 109.59
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY 345/115 2TR | T:77&78 | 474 | 478 | 109.59
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:114 | T:77&78 | 474 | 478 | 109.57
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | T:77&78 | 474 | 478 | 109.56
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:OSWEGO 6 | T:77&78 | 474 | 478 | 109.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:ELLICTVL | T:77&78 | 474 | 478 | 109.54
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:GENMLS61 | T:77&78 | 474 | 478 | 109.54
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 3 | T:77&78 | 474 | 478 | 109.51
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:926 NY | T:77&78 | 474 | 478 | 109.5
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 2TR | T:77&78 | 474 | 478 | 109.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 1 | T:77&78 | 474 | 478 | 109.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 2 | T:77&78 | 474 | 478 | 109.5
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:922 | T:77&78 | 474 | 478 | 109.49
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:WOLEAN55 | T:77&78 | 474 | 478 | 109.48
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_926B | T:77&78 | 474 | 478 | 109.47
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_926A | T:77&78 | 474 | 478 | 109.46
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 474 | 478 | 109.46
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | T:77&78 | 474 | 478 | 109.45
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:HH | T:77&78 | 474 | 478 | 109.43
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OS - EL - LFYTE 17 345 | T:77&78 | 474 | 478 | 109.43
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:152 | T:77&78 | 474 | 478 | 109.42
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:169 | T:77&78 | 474 | 478 | 109.41
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:170 | T:77&78 | 474 | 478 | 109.41
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - ELM 70 230 | T:77&78 | 474 | 478 | 109.41
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:149 | T:77&78 | 474 | 478 | 109.39
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:903 | T:77&78 | 474 | 478 | 109.39
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - BECK PA27 230 | T:77&78 | 474 | 478 | 109.39
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:SW | T:77&78 | 474 | 478 | 109.38
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:47 | T:77&78 | 474 | 478 | 109.38
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/2:PA27 | T:77&78 | 474 | 478 | 109.38
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 345/115 3TR | T:77&78 | 474 | 478 | 109.38
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 345/115 4TR | T:77&78 | 474 | 478 | 109.38
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:NI1 | T:77&78 | 474 | 478 | 109.38
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 1TR | T:77&78 | 474 | 478 | 109.38
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:117 | T:77&78 | 474 | 478 | 109.37
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:706 NY | T:77&78 | 474 | 478 | 109.37
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_706 | T:77&78 | 474 | 478 | 109.37
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 345/115 2TR | T:77&78 | 474 | 478 | 109.37
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:VANDALIA | T:77&78 | 474 | 478 | 109.37
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:104 | T:77&78 | 474 | 478 | 109.36
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:HYDLRACE | T:77&78 | 474 | 478 | 109.36
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:SRANDOLP | T:77&78 | 474 | 478 | 109.36
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:OSWEGO 5 | T:77&78 | 474 | 478 | 109.36
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:111 | T:77&78 | 474 | 478 | 109.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:150 | T:77&78 | 474 | 478 | 109.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:6 | T:77&78 | 474 | 478 | 109.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:ELB-GL3 | T:77&78 | 474 | 478 | 109.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - IND 25 345 | T:77&78 | 474 | 478 | 109.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA 345/115 1TR | T:77&78 | 474 | 478 | 109.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA 345/115 2TR | T:77&78 | 474 | 478 | 109.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BURT | T:77&78 | 474 | 478 | 109.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN8 | T:77&78 | 474 | 478 | 109.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN9 | T:77&78 | 474 | 478 | 109.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:1/.6:109 | T:77&78 | 474 | 478 | 109.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:81 | T:77&78 | 474 | 478 | 109.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:914 | T:77&78 | 474 | 478 | 109.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - 9MI1 9 345 | T:77&78 | 474 | 478 | 109.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | VOL - MARCY 19 345 | T:77&78 | 474 | 478 | 109.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:FAL | T:77&78 | 474 | 478 | 109.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:120 | T:77&78 | 474 | 478 | 109.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:44 | T:77&78 | 474 | 478 | 109.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:45 | T:77&78 | 474 | 478 | 109.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:929 | T:77&78 | 474 | 478 | 109.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:ELB-GL19 | T:77&78 | 474 | 478 | 109.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OSW - VOL 12 345 | T:77&78 | 474 | 478 | 109.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - FITZ 10 345 | T:77&78 | 474 | 478 | 109.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:AND | T:77&78 | 474 | 478 | 109.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/2:NI1 | T:77&78 | 474 | 478 | 109.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/2:NI2 | T:77&78 | 474 | 478 | 109.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:5 | T:77&78 | 474 | 478 | 109.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:912 | T:77&78 | 474 | 478 | 109.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 345/230 3TR | T:77&78 | 474 | 478 | 109.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 345/230 5TR | T:77&78 | 474 | 478 | 109.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OSW - VOL 11 345 | T:77&78 | 474 | 478 | 109.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:122 | T:77&78 | 474 | 478 | 109.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:23 | T:77&78 | 474 | 478 | 109.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:916 | T:77&78 | 474 | 478 | 109.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:107 | T:77&78 | 474 | 478 | 109.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:108 | T:77&78 | 474 | 478 | 109.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:121 | T:77&78 | 474 | 478 | 109.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:ELB-GL18 | T:77&78 | 474 | 478 | 109.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - NEWROCH 1 345 | T:77&78 | 474 | 478 | 109.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - NEWROCH 2 345 | T:77&78 | 474 | 478 | 109.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - NEWROCH 3 345 | T:77&78 | 474 | 478 | 109.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL - CLAY PC-1 345 | T:77&78 | 474 | 478 | 109.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL - CLAY PC-2 345 | T:77&78 | 474 | 478 | 109.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDL - FRASER 32 345 | T:77&78 | 474 | 478 | 109.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:3 | T:77&78 | 474 | 478 | 109.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:ELB-WOOD4 | T:77&78 | 474 | 478 | 109.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - PANNELL RP-1 345 | T:77&78 | 474 | 478 | 109.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - PANNELL RP-2 345 | T:77&78 | 474 | 478 | 109.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FUL - CLAY 4 115 | T:77&78 | 474 | 478 | 109.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:103 | T:77&78 | 474 | 478 | 109.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:24 | T:77&78 | 474 | 478 | 109.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WATERCURE - OAKDALE 71 230 | T:77&78 | 474 | 478 | 109.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - TEAL 11 115 | T:77&78 | 474 | 478 | 109.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DEWITT3 - LAFAYTTE 345 | T:77&78 | 474 | 478 | 109.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - VOL 20 345 | T:77&78 | 474 | 478 | 109.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:112 | T:77&78 | 474 | 478 | 109.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:904 NY | T:77&78 | 474 | 478 | 109.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/3:PA301 | T:77&78 | 474 | 478 | 109.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/3:PA302 | T:77&78 | 474 | 478 | 109.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 | T:77&78 | 474 | 478 | 109.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_904 | T:77&78 | 474 | 478 | 109.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - BECK_TSA 345 | T:77&78 | 474 | 478 | 109.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - BECK_TSB 345 | T:77&78 | 474 | 478 | 109.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 5 115 | T:77&78 | 474 | 478 | 109.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 230/115 1TR | T:77&78 | 474 | 478 | 109.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:116 | T:77&78 | 474 | 478 | 109.26
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:1 | T:77&78 | 474 | 478 | 109.26
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:7 | T:77&78 | 474 | 478 | 109.25
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:2 | T:77&78 | 474 | 478 | 109.25
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:9 MI PT2 | T:77&78 | 474 | 478 | 109.25
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:INDECK SS | T:77&78 | 474 | 478 | 109.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CBL:230:72 | T:77&78 | 474 | 478 | 109.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:82 | T:77&78 | 474 | 478 | 109.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:976 | T:77&78 | 474 | 478 | 109.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NEWROCH 345/115 1TR | T:77&78 | 474 | 478 | 109.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - ELM 71 230 | T:77&78 | 474 | 478 | 109.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - TEAL 10 115 | T:77&78 | 474 | 478 | 109.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - WOOD 17 115 | T:77&78 | 474 | 478 | 109.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 474 | 478 | 109.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:DUN31 | T:77&78 | 474 | 478 | 109.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:DUN41 | T:77&78 | 474 | 478 | 109.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:909 | T:77&78 | 474 | 478 | 109.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NEWROCH 345/115 2TR | T:77&78 | 474 | 478 | 109.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK 230/115 31TR | T:77&78 | 474 | 478 | 109.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK 230/115 41TR | T:77&78 | 474 | 478 | 109.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 5TR | T:77&78 | 474 | 478 | 109.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:DK | T:77&78 | 474 | 478 | 109.22
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:146 | T:77&78 | 474 | 478 | 109.22
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:926 | T:77&78 | 474 | 478 | 109.22
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - LM 14 115 | T:77&78 | 474 | 478 | 109.22
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OSW 345/115 1TR | T:77&78 | 474 | 478 | 109.21
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:9MIPT1 | T:77&78 | 474 | 478 | 109.21
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:924 NY | T:77&78 | 474 | 478 | 109.2
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:GV3 | T:77&78 | 474 | 478 | 109.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:GV4 | T:77&78 | 474 | 478 | 109.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:102 | T:77&78 | 474 | 478 | 109.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 3TR | T:77&78 | 474 | 478 | 109.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 4TR | T:77&78 | 474 | 478 | 109.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 1TR | T:77&78 | 474 | 478 | 109.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 2TR | T:77&78 | 474 | 478 | 109.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 3TR | T:77&78 | 474 | 478 | 109.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LHH - CLAY 7 115 | T:77&78 | 474 | 478 | 109.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | EDIC - MRCY ue 1-7 345 | T:77&78 | 474 | 478 | 109.18
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:25 | T:77&78 | 474 | 478 | 109.17
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:13 | T:77&78 | 474 | 478 | 109.17
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:FITZPATR | T:77&78 | 474 | 478 | 109.17
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:KAMINE | T:77&78 | 474 | 478 | 109.14
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:15 | T:77&78 | 474 | 478 | 109.14
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | EDIC - FITZ 345 | T:77&78 | 474 | 478 | 109.14
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:SITHE 1 | T:77&78 | 474 | 478 | 109.14
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:SITHE 2 | T:77&78 | 474 | 478 | 109.14
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN7 | T:77&78 | 474 | 478 | 109.14
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:GV6 | T:77&78 | 474 | 478 | 109.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:GV8 | T:77&78 | 474 | 478 | 109.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:101 | T:77&78 | 474 | 478 | 109.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:153 | T:77&78 | 474 | 478 | 109.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:705 NY | T:77&78 | 474 | 478 | 109.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:930 | T:77&78 | 474 | 478 | 109.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_705 | T:77&78 | 474 | 478 | 109.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 M6TR | T:77&78 | 474 | 478 | 109.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 M8TR | T:77&78 | 474 | 478 | 109.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 1TR | T:77&78 | 474 | 478 | 109.12
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DEWITT 345/115 2TR | T:77&78 | 474 | 478 | 109.12
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:GV2 | T:77&78 | 474 | 478 | 109.1
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 2TR | T:77&78 | 474 | 478 | 109.1
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 3TR | T:77&78 | 474 | 478 | 109.1
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_922 | T:77&78 | 474 | 478 | 109.09
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 4MILE 230/115 1TR | T:77&78 | 474 | 478 | 109.05
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:GINNA | T:77&78 | 474 | 478 | 109.03
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:192 | T:77&78 | 474 | 478 | 109.02
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:GINNA | T:77&78 | 474 | 478 | 109.01
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:907 NY | T:77&78 | 474 | 478 | 109.01
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:191 | T:77&78 | 474 | 478 | 108.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | T:77&78 | 474 | 478 | 108.99
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:GV7 | T:77&78 | 474 | 478 | 108.98
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_GRDN_250MVA_XFMR | T:77&78 | 474 | 478 | 108.98
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 M7TR | T:77&78 | 474 | 478 | 108.98
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_907 | T:77&78 | 474 | 478 | 108.96
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WATERCURE 345/230 1TR | T:77&78 | 474 | 478 | 108.94
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WATERCURE 345/230 2TR | T:77&78 | 474 | 478 | 108.94
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 13 345 | T:77&78 | 474 | 478 | 108.94
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:154 | T:77&78 | 474 | 478 | 108.92
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:162 | T:77&78 | 474 | 478 | 108.91
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:157 | T:77&78 | 474 | 478 | 108.86
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:155 | T:77&78 | 474 | 478 | 108.84
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:167 | T:77&78 | 474 | 478 | 108.82
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/1:ELB | T:77&78 | 474 | 478 | 108.77
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ELBRIDGE 345/115 1TR | T:77&78 | 474 | 478 | 108.77
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:8 | T:77&78 | 474 | 478 | 108.74
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:969 | T:77&78 | 474 | 478 | 108.66
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:345:SOMERSET | T:77&78 | 474 | 478 | 108.66
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:KINTIGH | T:77&78 | 474 | 478 | 108.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:156 | T:77&78 | 474 | 478 | 108.6
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:141 | T:77&78 | 474 | 478 | 108.54
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:145 | T:77&78 | 474 | 478 | 108.44
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:906 NY | T:77&78 | 474 | 478 | 108.4
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:4 | T:77&78 | 474 | 478 | 108.4
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LOCKPORT | T:77&78 | 474 | 478 | 108.34
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 474 | 478 | 108.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:142 | T:77&78 | 474 | 478 | 108.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:193 | T:77&78 | 474 | 478 | 108.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:194 | T:77&78 | 474 | 478 | 108.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 3TR | T:77&78 | 474 | 478 | 108.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SRIPL - ERIE E 69 230 | T:77&78 | 474 | 478 | 108.27
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | T:77&78 | 474 | 478 | 108.21
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK - SRIPL 68 230 | T:77&78 | 474 | 478 | 108.2
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - DUNKIRK 73 230 | T:77&78 | 474 | 478 | 108.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - DUNKIRK 74 230 | T:77&78 | 474 | 478 | 108.19
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - 9MI1 8 345 | T:77&78 | 474 | 478 | 108.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:161 | T:77&78 | 474 | 478 | 108.17
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:AMERT | T:77&78 | 474 | 478 | 108.16
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - INDEPNC 26 345 | T:77&78 | 474 | 478 | 108.11
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:GINNA | T:77&78 | 474 | 478 | 108.06
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:GINNA | T:77&78 | 474 | 478 | 108.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:DUPONT46 | T:77&78 | 474 | 478 | 108
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:934 NY | T:77&78 | 474 | 478 | 107.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS2 | T:77&78 | 474 | 478 | 107.95
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | BECK - PACKARD BP76 230 | T:77&78 | 474 | 478 | 107.93
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:903 NY | T:77&78 | 474 | 478 | 107.82
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 107.79
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | T:77&78 | 474 | 478 | 107.79
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 107.79
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:54/921 | T:77&78 | 474 | 478 | 107.78
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 474 | 478 | 107.71
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | T:77&78 | 474 | 478 | 107.68
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - VOLNEY 6 345 | T:77&78 | 474 | 478 | 107.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/2:FV | T:77&78 | 474 | 478 | 107.6
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - FARMVLY | T:77&78 | 474 | 478 | 107.6
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LOCKPORT | T:77&78 | 474 | 478 | 107.57
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE - WATERCURE 69 230 | T:77&78 | 474 | 478 | 107.53
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE - ETWANDA 70 230 | T:77&78 | 474 | 478 | 107.53
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 3TR | T:77&78 | 474 | 478 | 107.52
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:966 NY | T:77&78 | 474 | 478 | 107.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 4 MILE - ERIE SE 230 | T:77&78 | 474 | 478 | 107.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:OXBOWNUG | T:77&78 | 474 | 478 | 107.37
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 7 | T:77&78 | 474 | 478 | 107.36
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:HUN | T:77&78 | 474 | 478 | 107.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 4 | T:77&78 | 474 | 478 | 107.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 5 | T:77&78 | 474 | 478 | 107.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 6 | T:77&78 | 474 | 478 | 107.28
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/1:FMR | T:77&78 | 474 | 478 | 107.22
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE 345/115 1TR | T:77&78 | 474 | 478 | 107.22
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:46 | T:77&78 | 474 | 478 | 107.16
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAG - NEWROCH 1 345 | T:77&78 | 474 | 478 | 107.13
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 474 | 478 | 107.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 10 | T:77&78 | 474 | 478 | 107.07
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 8 | T:77&78 | 474 | 478 | 107.06
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 9 | T:77&78 | 474 | 478 | 107.06
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 11 | T:77&78 | 474 | 478 | 107.05
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 12 | T:77&78 | 474 | 478 | 107.05
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 13 | T:77&78 | 474 | 478 | 107.05
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:160 | T:77&78 | 474 | 478 | 107.03
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 474 | 478 | 107.03
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:195 | T:77&78 | 474 | 478 | 106.98
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:PK4 | T:77&78 | 474 | 478 | 106.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 4TR | T:77&78 | 474 | 478 | 106.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:968 NY | T:77&78 | 474 | 478 | 106.95
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | MAINSBRG 345/115 1TR | T:77&78 | 474 | 478 | 106.8
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | T:77&78 | 474 | 478 | 106.77
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:STL1_G1 | T:77&78 | 474 | 478 | 106.76
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:STL1_G2 | T:77&78 | 474 | 478 | 106.76
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:953 NY | T:77&78 | 474 | 478 | 106.75
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_104 | T:77&78 | 474 | 478 | 106.73
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_103 | T:77&78 | 474 | 478 | 106.72
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | T:77&78 | 474 | 478 | 106.71
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:110 | T:77&78 | 474 | 478 | 106.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:193 | T:77&78 | 474 | 478 | 106.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:194 | T:77&78 | 474 | 478 | 106.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:HOORKN86 | T:77&78 | 474 | 478 | 106.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:UDG-184 | T:77&78 | 474 | 478 | 106.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:171 | T:77&78 | 474 | 478 | 106.68
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:HOORKN85 | T:77&78 | 474 | 478 | 106.63
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:SENECA | T:77&78 | 474 | 478 | 106.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:ESYR | T:77&78 | 474 | 478 | 106.6
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:Q234_CLIB_G10 | T:77&78 | 474 | 478 | 106.6
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:Q234_CLIB_G20 | T:77&78 | 474 | 478 | 106.6
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:151 | T:77&78 | 474 | 478 | 106.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 1-3 | T:77&78 | 474 | 478 | 106.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 4-6 | T:77&78 | 474 | 478 | 106.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 7-9 | T:77&78 | 474 | 478 | 106.45
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:LEW 10-12 | T:77&78 | 474 | 478 | 106.45
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - VOL 21 345 | T:77&78 | 474 | 478 | 106.35
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | T:77&78 | 474 | 478 | 106.32
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 13 345 | T:77&78 | 474 | 478 | 106.31
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:37 | T:77&78 | 474 | 478 | 106.3
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:36 | T:77&78 | 474 | 478 | 106.29
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROBRD 230/115/34.5 1TR | T:77&78 | 474 | 478 | 106.27
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:706 NY | T:77&78 | 474 | 478 | 106.25
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_706 | T:77&78 | 474 | 478 | 106.25
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:ELLICTVL | T:77&78 | 474 | 478 | 106.25
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:GENMLS61 | T:77&78 | 474 | 478 | 106.25
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | T:77&78 | 474 | 478 | 106.24
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - BECK PA27 230 | T:77&78 | 474 | 478 | 106.22
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/2:PA27 | T:77&78 | 474 | 478 | 106.21
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:MODERNLF | T:77&78 | 474 | 478 | 106.21
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:927 NY | T:77&78 | 474 | 478 | 106.2
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/2:NI3 | T:77&78 | 474 | 478 | 106.17
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 345/230 4TR | T:77&78 | 474 | 478 | 106.17
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY 345/115 1TR | T:77&78 | 474 | 478 | 106.17
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY 345/115 2TR | T:77&78 | 474 | 478 | 106.17
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:WOLEAN55 | T:77&78 | 474 | 478 | 106.17
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:FAL | T:77&78 | 474 | 478 | 106.16
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:SW | T:77&78 | 474 | 478 | 106.16
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:117 | T:77&78 | 474 | 478 | 106.16
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:HH | T:77&78 | 474 | 478 | 106.13
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:45 | T:77&78 | 474 | 478 | 106.13
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:NI2 | T:77&78 | 474 | 478 | 106.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:926 NY | T:77&78 | 474 | 478 | 106.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - BECK_TSA 345 | T:77&78 | 474 | 478 | 106.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - BECK_TSB 345 | T:77&78 | 474 | 478 | 106.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 2TR | T:77&78 | 474 | 478 | 106.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DEWITT3 - LAFAYTTE 345 | T:77&78 | 474 | 478 | 106.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/3:PA301 | T:77&78 | 474 | 478 | 106.11
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/3:PA302 | T:77&78 | 474 | 478 | 106.11
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_926A | T:77&78 | 474 | 478 | 106.11
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_926B | T:77&78 | 474 | 478 | 106.11
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 345/115 2TR | T:77&78 | 474 | 478 | 106.11
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - ELM 70 230 | T:77&78 | 474 | 478 | 106.1
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 345/115 3TR | T:77&78 | 474 | 478 | 106.1
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 345/115 4TR | T:77&78 | 474 | 478 | 106.1
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:44 | T:77&78 | 474 | 478 | 106.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAG - KINTIGH 345 | T:77&78 | 474 | 478 | 106.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/2:NI1 | T:77&78 | 474 | 478 | 106.06
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/2:NI2 | T:77&78 | 474 | 478 | 106.06
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 345/230 3TR | T:77&78 | 474 | 478 | 106.06
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 345/230 5TR | T:77&78 | 474 | 478 | 106.06
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:169 | T:77&78 | 474 | 478 | 106.05
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:170 | T:77&78 | 474 | 478 | 106.05
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:HYDLRACE | T:77&78 | 474 | 478 | 106.04
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:904 NY | T:77&78 | 474 | 478 | 106.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_904 | T:77&78 | 474 | 478 | 106.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:ELB-GL3 | T:77&78 | 474 | 478 | 106.02
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:DK | T:77&78 | 474 | 478 | 106.01
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - NEWROCH 1 345 | T:77&78 | 474 | 478 | 106.01
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - NEWROCH 2 345 | T:77&78 | 474 | 478 | 106.01
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - NEWROCH 3 345 | T:77&78 | 474 | 478 | 106.01
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - PANNELL RP-1 345 | T:77&78 | 474 | 478 | 106.01
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH - PANNELL RP-2 345 | T:77&78 | 474 | 478 | 106.01
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:VANDALIA | T:77&78 | 474 | 478 | 106.01
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:AND | T:77&78 | 474 | 478 | 106
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:47 | T:77&78 | 474 | 478 | 106
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:ELB-GL19 | T:77&78 | 474 | 478 | 106
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:104 | T:77&78 | 474 | 478 | 105.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:1/.6:109 | T:77&78 | 474 | 478 | 105.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:152 | T:77&78 | 474 | 478 | 105.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:81 | T:77&78 | 474 | 478 | 105.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:149 | T:77&78 | 474 | 478 | 105.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:150 | T:77&78 | 474 | 478 | 105.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - FITZ 10 345 | T:77&78 | 474 | 478 | 105.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN8 | T:77&78 | 474 | 478 | 105.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN9 | T:77&78 | 474 | 478 | 105.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:SRANDOLP | T:77&78 | 474 | 478 | 105.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:909 | T:77&78 | 474 | 478 | 105.98
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BURT | T:77&78 | 474 | 478 | 105.98
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:121 | T:77&78 | 474 | 478 | 105.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:122 | T:77&78 | 474 | 478 | 105.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:932 NY | T:77&78 | 474 | 478 | 105.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:6 | T:77&78 | 474 | 478 | 105.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 3TR | T:77&78 | 474 | 478 | 105.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - 9MI1 9 345 | T:77&78 | 474 | 478 | 105.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - IND 25 345 | T:77&78 | 474 | 478 | 105.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA 345/115 1TR | T:77&78 | 474 | 478 | 105.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA 345/115 2TR | T:77&78 | 474 | 478 | 105.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CBL:230:72 | T:77&78 | 474 | 478 | 105.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:5 | T:77&78 | 474 | 478 | 105.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:912 | T:77&78 | 474 | 478 | 105.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NEWROCH 345/115 1TR | T:77&78 | 474 | 478 | 105.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NEWROCH 345/115 2TR | T:77&78 | 474 | 478 | 105.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - ELM 71 230 | T:77&78 | 474 | 478 | 105.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OSW - VOL 11 345 | T:77&78 | 474 | 478 | 105.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:23 | T:77&78 | 474 | 478 | 105.95
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:929 | T:77&78 | 474 | 478 | 105.95
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:976 | T:77&78 | 474 | 478 | 105.95
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OSW - VOL 12 345 | T:77&78 | 474 | 478 | 105.94
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 1TR | T:77&78 | 474 | 478 | 105.93
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL 345/115 2TR | T:77&78 | 474 | 478 | 105.93
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:2 | T:77&78 | 474 | 478 | 105.92
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:914 | T:77&78 | 474 | 478 | 105.92
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 1TR | T:77&78 | 474 | 478 | 105.92
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 3TR | T:77&78 | 474 | 478 | 105.92
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:903 | T:77&78 | 474 | 478 | 105.91
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - EDIC 2-15 345 | T:77&78 | 474 | 478 | 105.91
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SCRIBA - VOL 20 345 | T:77&78 | 474 | 478 | 105.91
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:24 | T:77&78 | 474 | 478 | 105.9
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 | T:77&78 | 474 | 478 | 105.9
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OKDLE 230/115 1TR | T:77&78 | 474 | 478 | 105.9
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:DUN31 | T:77&78 | 474 | 478 | 105.89
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:DUN41 | T:77&78 | 474 | 478 | 105.89
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:916 | T:77&78 | 474 | 478 | 105.89
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:ELB-GL18 | T:77&78 | 474 | 478 | 105.89
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK 230/115 31TR | T:77&78 | 474 | 478 | 105.89
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK 230/115 41TR | T:77&78 | 474 | 478 | 105.89
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | EDIC - MRCY ue 1-7 345 | T:77&78 | 474 | 478 | 105.89
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:GV3 | T:77&78 | 474 | 478 | 105.88
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:GV4 | T:77&78 | 474 | 478 | 105.88
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:926 | T:77&78 | 474 | 478 | 105.88
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 3TR | T:77&78 | 474 | 478 | 105.88
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 4TR | T:77&78 | 474 | 478 | 105.88
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:103 | T:77&78 | 474 | 478 | 105.87
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:1 | T:77&78 | 474 | 478 | 105.87
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - TEAL 11 115 | T:77&78 | 474 | 478 | 105.87
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:GV6 | T:77&78 | 474 | 478 | 105.86
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:GV8 | T:77&78 | 474 | 478 | 105.86
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:924 NY | T:77&78 | 474 | 478 | 105.86
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:922 | T:77&78 | 474 | 478 | 105.86
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 M6TR | T:77&78 | 474 | 478 | 105.86
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 M8TR | T:77&78 | 474 | 478 | 105.86
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WATERCURE - OAKDALE 71 230 | T:77&78 | 474 | 478 | 105.86
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 2TR | T:77&78 | 474 | 478 | 105.86
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:ELB-WOOD4 | T:77&78 | 474 | 478 | 105.85
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LHH - CLAY 7 115 | T:77&78 | 474 | 478 | 105.85
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:114 | T:77&78 | 474 | 478 | 105.84
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:82 | T:77&78 | 474 | 478 | 105.84
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:25 | T:77&78 | 474 | 478 | 105.84
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:13 | T:77&78 | 474 | 478 | 105.84
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OSW 345/115 1TR | T:77&78 | 474 | 478 | 105.83
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:112 | T:77&78 | 474 | 478 | 105.82
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:7 | T:77&78 | 474 | 478 | 105.82
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - WOOD 17 115 | T:77&78 | 474 | 478 | 105.81
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:GV2 | T:77&78 | 474 | 478 | 105.8
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:146 | T:77&78 | 474 | 478 | 105.8
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:15 | T:77&78 | 474 | 478 | 105.8
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:3 | T:77&78 | 474 | 478 | 105.8
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 2TR | T:77&78 | 474 | 478 | 105.8
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FUL - CLAY 4 115 | T:77&78 | 474 | 478 | 105.8
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:930 | T:77&78 | 474 | 478 | 105.79
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 5 115 | T:77&78 | 474 | 478 | 105.79
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL - CLAY PC-1 345 | T:77&78 | 474 | 478 | 105.78
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PANL - CLAY PC-2 345 | T:77&78 | 474 | 478 | 105.78
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ROCH 345/115 5TR | T:77&78 | 474 | 478 | 105.76
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:GV7 | T:77&78 | 474 | 478 | 105.75
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_GRDN_250MVA_XFMR | T:77&78 | 474 | 478 | 105.75
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL 230/115 M7TR | T:77&78 | 474 | 478 | 105.75
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DEWITT 345/115 2TR | T:77&78 | 474 | 478 | 105.74
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAG - NEWROCH 1 345 | T:77&78 | 474 | 478 | 105.73
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - LM 14 115 | T:77&78 | 474 | 478 | 105.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - TEAL 10 115 | T:77&78 | 474 | 478 | 105.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:108 | T:77&78 | 474 | 478 | 105.68
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:705 NY | T:77&78 | 474 | 478 | 105.68
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_705 | T:77&78 | 474 | 478 | 105.68
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:107 | T:77&78 | 474 | 478 | 105.65
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:153 | T:77&78 | 474 | 478 | 105.65
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 4MILE 230/115 1TR | T:77&78 | 474 | 478 | 105.65
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CLAY - DEW 3 115 | T:77&78 | 474 | 478 | 105.64
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WATERCURE 345/230 1TR | T:77&78 | 474 | 478 | 105.63
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:111 | T:77&78 | 474 | 478 | 105.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WATERCURE 345/230 2TR | T:77&78 | 474 | 478 | 105.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:116 | T:77&78 | 474 | 478 | 105.61
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:113 | T:77&78 | 474 | 478 | 105.6
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:INDECK SS | T:77&78 | 474 | 478 | 105.59
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 62 230 | T:77&78 | 474 | 478 | 105.59
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:120 | T:77&78 | 474 | 478 | 105.54
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | BECK - PACKARD BP76 230 | T:77&78 | 474 | 478 | 105.54
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:KAMINE | T:77&78 | 474 | 478 | 105.49
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:119 | T:77&78 | 474 | 478 | 105.45
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:154 | T:77&78 | 474 | 478 | 105.45
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ERIE E - 4 MILE 230 | T:77&78 | 474 | 478 | 105.45
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:162 | T:77&78 | 474 | 478 | 105.44
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | EDIC - FITZ 345 | T:77&78 | 474 | 478 | 105.41
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:155 | T:77&78 | 474 | 478 | 105.37
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 474 | 478 | 105.37
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:8 | T:77&78 | 474 | 478 | 105.35
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 474 | 478 | 105.35
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/1:ELB | T:77&78 | 474 | 478 | 105.33
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ELBRIDGE 345/115 1TR | T:77&78 | 474 | 478 | 105.33
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:167 | T:77&78 | 474 | 478 | 105.31
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OS - EL - LFYTE 17 345 | T:77&78 | 474 | 478 | 105.31
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:157 | T:77&78 | 474 | 478 | 105.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 62 230 | T:77&78 | 474 | 478 | 105.25
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:PK3 | T:77&78 | 474 | 478 | 105.23
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:156 | T:77&78 | 474 | 478 | 105.07
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 61 230 | T:77&78 | 474 | 478 | 105.06
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:906 NY | T:77&78 | 474 | 478 | 105.05
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - DUNKIRK 73 230 | T:77&78 | 474 | 478 | 105.04
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:4 | T:77&78 | 474 | 478 | 105.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - DUNKIRK 74 230 | T:77&78 | 474 | 478 | 105.02
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | VOL - MARCY 19 345 | T:77&78 | 474 | 478 | 104.92
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:145 | T:77&78 | 474 | 478 | 104.91
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:969 | T:77&78 | 474 | 478 | 104.9
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 474 | 478 | 104.74
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 474 | 478 | 104.69
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDL - FRASER 32 345 | T:77&78 | 474 | 478 | 104.66
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 104.53
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | T:77&78 | 474 | 478 | 104.53
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 104.53
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:161 | T:77&78 | 474 | 478 | 104.52
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | T:77&78 | 474 | 478 | 104.52
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 104.52
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 104.52
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 61 230 | T:77&78 | 474 | 478 | 104.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:934 NY | T:77&78 | 474 | 478 | 104.48
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:102 | T:77&78 | 474 | 478 | 104.44
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:142 | T:77&78 | 474 | 478 | 104.44
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:54/921 | T:77&78 | 474 | 478 | 104.42
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 3TR | T:77&78 | 474 | 478 | 104.41
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE - WATERCURE 69 230 | T:77&78 | 474 | 478 | 104.39
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE - ETWANDA 70 230 | T:77&78 | 474 | 478 | 104.39
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:129 | T:77&78 | 474 | 478 | 104.36
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:101 | T:77&78 | 474 | 478 | 104.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:GV1 | T:77&78 | 474 | 478 | 104.12
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:GV2 | T:77&78 | 474 | 478 | 104.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:141 | T:77&78 | 474 | 478 | 104.06
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK - SRIPL 68 230 | T:77&78 | 474 | 478 | 104.02
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:191 | T:77&78 | 474 | 478 | 103.98
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:192 | T:77&78 | 474 | 478 | 103.94
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:130 | T:77&78 | 474 | 478 | 103.88
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SRIPL - ERIE E 69 230 | T:77&78 | 474 | 478 | 103.88
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:903 NY | T:77&78 | 474 | 478 | 103.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/2:FV | T:77&78 | 474 | 478 | 103.66
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - FARMVLY | T:77&78 | 474 | 478 | 103.66
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:160 | T:77&78 | 474 | 478 | 102.7
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:195 | T:77&78 | 474 | 478 | 101.93
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | WTHRS - MEYER 230 | 474 | 478 | 101.59
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SHLDON - STONYCR 230 | T:77&78 | 474 | 478 | 101.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | TB:2/1:MEYER | 474 | 478 | 101.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:MEYER | 474 | 478 | 101.51
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | TB:2/1:MEYER | 474 | 478 | 101.2
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:79&80 | 474 | 478 | 100.88
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | S:AVOCA | 474 | 478 | 100.65
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | CANDQUA - STNYRDG 68A 230 | 474 | 478 | 100.65
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | SB:STONYRIDGE | 474 | 478 | 100.58
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 474 | 478 | 100.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | S:AVOCA | 474 | 478 | 100.45
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | CANDQUA - STNYRDG 68A 230 | 474 | 478 | 100.45
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | SB:STONYRIDGE | 474 | 478 | 100.38
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 474 | 478 | 100.37
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 474 | 478 | 100.28
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:GV1 | T:77&78 | 474 | 478 | 100.1
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:GV2 | T:77&78 | 474 | 478 | 100.1
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SHLDON - STONYCR 230 | T:77&78 | 474 | 478 | 100.07
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:79&80 | 474 | 478 | 100.01
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-WC_30&W-F_171 | T:77&78 | 474 | 478 | 100
| 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  |  |  | 121.23
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_926B | LN:115:181/922 | 119 | 119 | 118.34
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_926B | LN:115:181/922 | 119 | 119 | 118.07
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV-HC | 119 | 119 | 117.14
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:5M-SR_37&W-F_171 | 119 | 119 | 116.89
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_STOL_HOMER_345 | 119 | 119 | 116.75
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | 5 MILE - STOLLE 37A 345 | 119 | 119 | 116.75
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | HOMERCTY - STOLLRD 37 345 | 119 | 119 | 116.75
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:STOLE345 | 119 | 119 | 116.75
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV-HC | 119 | 119 | 116.71
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:5M-SR_37&W-F_171 | 119 | 119 | 116.61
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV | 119 | 119 | 116.55
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | 5 MILE - STOLLE 37A 345 | 119 | 119 | 116.34
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_STOL_HOMER_345 | 119 | 119 | 116.34
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:STOLE345 | 119 | 119 | 116.34
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | HOMERCTY - STOLLRD 37 345 | 119 | 119 | 116.34
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV | 119 | 119 | 116.3
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | S:STOLLE345 | 119 | 119 | 116.2
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | S:STOLLE345 | 119 | 119 | 116.1
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_926B | 119 | 119 | 114.96
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_926B | 119 | 119 | 114.72
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV | LN:115:181/922 | 119 | 119 | 114.33
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV-HC | LN:115:181/922 | 119 | 119 | 114.27
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:5M-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 114.11
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_STOL_HOMER_345 | LN:115:181/922 | 119 | 119 | 113.98
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | 5 MILE - STOLLE 37A 345 | LN:115:181/922 | 119 | 119 | 113.98
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | HOMERCTY - STOLLRD 37 345 | LN:115:181/922 | 119 | 119 | 113.98
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV | LN:115:181/922 | 119 | 119 | 113.42
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV-HC | LN:115:181/922 | 119 | 119 | 113
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:5M-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 112.97
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_STOL_HOMER_345 | LN:115:181/922 | 119 | 119 | 112.95
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | 5 MILE - STOLLE 37A 345 | LN:115:181/922 | 119 | 119 | 112.95
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | HOMERCTY - STOLLRD 37 345 | LN:115:181/922 | 119 | 119 | 112.95
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | LN:115:181/922 | 119 | 119 | 112.9
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | LN:115:181/922 | 119 | 119 | 112.9
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:926 NY | LN:115:181/922 | 119 | 119 | 112.46
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:926 NY | LN:115:181/922 | 119 | 119 | 112.12
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-FV_37&W-F_171 | LN:115:181/922 | 119 | 119 | 111.15
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - HOMERCTY | LN:115:181/922 | 119 | 119 | 111.13
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:926 NY | 119 | 119 | 109.44
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | LN:115:181/922 | 119 | 119 | 109.26
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | LN:115:181/922 | 119 | 119 | 109.26
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:926 NY | 119 | 119 | 109.03
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-FV_37&W-F_171 | 119 | 119 | 108.58
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - HOMERCTY | 119 | 119 | 108.5
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-FV_37&W-F_171 | 119 | 119 | 107.94
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - HOMERCTY | 119 | 119 | 107.88
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - HOMERCTY | LN:115:181/922 | 119 | 119 | 107.56
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-FV_37&W-F_171 | LN:115:181/922 | 119 | 119 | 107.3
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:903 NY | LN:115:181/922 | 119 | 119 | 104.75
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-SR_37&W-F_171 | 119 | 119 | 104.4
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:FV-5M_37&W-F_171 | 119 | 119 | 104.4
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:FV-5M_37&W-F_171 | 119 | 119 | 104.07
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-SR_37&W-F_171 | 119 | 119 | 104.07
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 104.01
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:FV-5M_37&W-F_171 | LN:115:181/922 | 119 | 119 | 104.01
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 103.29
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:FV-5M_37&W-F_171 | LN:115:181/922 | 119 | 119 | 103.29
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:903 NY | LN:115:181/922 | 119 | 119 | 103.28
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | R:5M-SR_37&W-F_171 | 119 | 119 | 102.8
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | R:5M-SR_37&W-F_171 | 119 | 119 | 102.8
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | 5 MILE - STOLLE 37A 345 | 119 | 119 | 102.79
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | First:Lancaster_STOL_HOMER_345 | 119 | 119 | 102.79
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | B:STOLE345 | 119 | 119 | 102.79
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | HOMERCTY - STOLLRD 37 345 | 119 | 119 | 102.79
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | 5 MILE - STOLLE 37A 345 | 119 | 119 | 102.79
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | First:Lancaster_STOL_HOMER_345 | 119 | 119 | 102.79
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | B:STOLE345 | 119 | 119 | 102.79
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | HOMERCTY - STOLLRD 37 345 | 119 | 119 | 102.79
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | S:STOLLE345 | 119 | 119 | 102.78
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | S:STOLLE345 | 119 | 119 | 102.78
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - 5MILE 345 | LN:115:181/922 | 119 | 119 | 102.64
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | LN:345:37S-FM-FV | 119 | 119 | 102.29
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | LN:345:37S-FM-FV | 119 | 119 | 102.29
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - 5MILE 345 | 119 | 119 | 101.84
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | LN:345:37S-FM-FV-HC | 119 | 119 | 101.67
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | LN:345:37S-FM-FV-HC | 119 | 119 | 101.67
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - 5MILE 345 | LN:115:181/922 | 119 | 119 | 101.63
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - 5MILE 345 | 119 | 119 | 101.55
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | DUNKIRK - SRIPL 68 230 | LN:115:181/922 | 119 | 119 | 100.12
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:706 NY | LN:115:181/922 | 119 | 119 | 100.08
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_706 | LN:115:181/922 | 119 | 119 | 100.08
| 130795 DEPEW115 115 130799 ERIE 115 115 1 Max |  |  |  |  | 118.34
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 566 | 654 | 100.1
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 100.1
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | Base Case | 129 | 236 | 107.79
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | Base Case | 129 | 236 | 107.32
| 135327 AM.S-54 115 135450 GRDNVL1 115 1 Max |  |  |  |  | 107.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:192 | T:62&BP76 | 620 | 841 | 100.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:180 | T:62&BP76 | 620 | 841 | 100
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 Max |  |  |  |  | 100.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:2/1:NI1 | T:61&64 | 620 | 841 | 100.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 1TR | T:61&64 | 620 | 841 | 100.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | T:61&64 | 620 | 841 | 100.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:180 | T:61&64 | 620 | 841 | 100
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 Max |  |  |  |  | 100.61
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | LN:115:133 | 168 | 206 | 100.34
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | LN:115:133 | 168 | 206 | 100.34
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 Max |  |  |  |  | 100.34
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | Base Case | 239 | 298 | 100.02
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | TB:2/1:NI2 | LN:115:130 | 239 | 298 | 100
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAGARA 230/115 2TR | LN:115:130 | 239 | 298 | 100
| 135454 MLPN-129 115 135461 PACK(S)W 115 1 Max |  |  |  |  | 100.02
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | TB:2/1:NI2 | LN:115:129 | 239 | 298 | 101.21
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAGARA 230/115 2TR | LN:115:129 | 239 | 298 | 101.21
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | TB:2/1:PK4 | LN:115:129 | 239 | 298 | 100.06
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | Base Case | 239 | 298 | 100.06
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | PACKARD 230/115 4TR | LN:115:129 | 239 | 298 | 100.06
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:120 | LN:115:129 | 239 | 298 | 100.03
| 135455 MLPN-130 115 135461 PACK(S)W 115 1 Max |  |  |  |  | 101.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | Base Case | 160 | 206 | 101.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | Base Case | 160 | 206 | 101.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | Base Case | 160 | 206 | 100.18
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 Max |  |  |  |  | 101.97
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:194 | LN:115:195 | 273 | 351 | 134.63
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:195 | LN:115:194 | 273 | 351 | 127.92
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:195 | LN:115:194 | 273 | 351 | 108.6
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:194 | LN:115:195 | 273 | 351 | 108.56
| 135461 PACK(S)W 115 147851 NIAG115W 115 1 Max |  |  |  |  | 134.63
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:193 | LN:115:195 | 273 | 351 | 134.63
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:195 | LN:115:193 | 273 | 351 | 127.92
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:195 | LN:115:193 | 273 | 351 | 108.6
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:193 | LN:115:195 | 273 | 351 | 108.56
| 135461 PACK(S)W 115 147851 NIAG115W 115 2 Max |  |  |  |  | 134.63
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:193 | LN:115:194 | 273 | 351 | 125.23
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:194 | LN:115:193 | 273 | 351 | 125.23
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:193 | LN:115:194 | 273 | 351 | 101.5
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:194 | LN:115:193 | 273 | 351 | 101.5
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 Max |  |  |  |  | 125.23
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:130 | 168 | 206 | 100.35
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:130 | 168 | 206 | 100.32
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:46 | LN:115:130 | 168 | 206 | 100.19
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:DUPONT46 | LN:115:130 | 168 | 206 | 100.07
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:908 NY | LN:115:130 | 168 | 206 | 100.02
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | LN:115:130 | 168 | 206 | 100
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:LOCKPORT | LN:115:130 | 168 | 206 | 100
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | LN:115:130 | 168 | 206 | 100
| 135497 ZRMN-133 115 135562 S214-133 115 1 Max |  |  |  |  | 100.35
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 192 | 239 | 123.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 192 | 239 | 120.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:9 MI PT2 | T:77&78 | 192 | 239 | 109.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | T:62&BP76 | 192 | 239 | 108.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CLAY - INDEPNC 26 345 | T:77&78 | 192 | 239 | 108.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CLAY - 9MI1 8 345 | T:77&78 | 192 | 239 | 106.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 192 | 239 | 106.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SCRIBA - VOL 21 345 | T:77&78 | 192 | 239 | 105.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:61&64 | 192 | 239 | 105.31
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OS - EL - LFYTE 17 345 | T:77&78 | 192 | 239 | 104.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | VOL - MARCY 19 345 | T:77&78 | 192 | 239 | 104.44
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CLAY - VOLNEY 6 345 | T:77&78 | 192 | 239 | 104.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:77&78 | 192 | 239 | 103.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 192 | 239 | 101.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:GINNA | T:77&78 | 192 | 239 | 101.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 192 | 239 | 101.59
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:GINNA | T:77&78 | 192 | 239 | 101.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | T:77&78 | 192 | 239 | 100.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:FITZPATR | T:77&78 | 192 | 239 | 100.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:OSWEGO 6 | T:77&78 | 192 | 239 | 100.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | T:77&78 | 192 | 239 | 100.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:182S | T:77&78 | 192 | 239 | 100.16
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:77&78 | 192 | 239 | 100.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:SITHE 1 | T:77&78 | 192 | 239 | 100.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:SITHE 2 | T:77&78 | 192 | 239 | 100.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:3/2:NI3 | T:77&78 | 192 | 239 | 100.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 345/230 4TR | T:77&78 | 192 | 239 | 100.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STNYRDG - HILLSIDE 68B 230 | T:77&78 | 192 | 239 | 100.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 192 | 239 | 100.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 192 | 239 | 100.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 192 | 239 | 100.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:PK4 | T:77&78 | 192 | 239 | 100.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:NI2 | T:77&78 | 192 | 239 | 100.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:110 | T:77&78 | 192 | 239 | 100.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:922 | T:77&78 | 192 | 239 | 100.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | T:77&78 | 192 | 239 | 100.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 192 | 239 | 100.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | T:77&78 | 192 | 239 | 100.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | T:77&78 | 192 | 239 | 100.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 2TR | T:77&78 | 192 | 239 | 100.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:HOORKN85 | T:77&78 | 192 | 239 | 100.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:141 | T:77&78 | 192 | 239 | 100.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | T:77&78 | 192 | 239 | 100.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | MEYER - CANDQUA 60 230 | T:77&78 | 192 | 239 | 100.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | EDIC - FITZ 345 | T:77&78 | 192 | 239 | 100.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | T:77&78 | 192 | 239 | 100.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV | T:77&78 | 192 | 239 | 100.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CLAY 345/115 1TR | T:77&78 | 192 | 239 | 100.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CLAY 345/115 2TR | T:77&78 | 192 | 239 | 100.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:HOORKN86 | T:77&78 | 192 | 239 | 100.02
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 192 | 239 | 100.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:3/1:FMR | T:77&78 | 192 | 239 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:38 | T:77&78 | 192 | 239 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:39 | T:77&78 | 192 | 239 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | T:77&78 | 192 | 239 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:171 | T:77&78 | 192 | 239 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:969 | T:77&78 | 192 | 239 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 5 MILE 345/115 1TR | T:77&78 | 192 | 239 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 4 MILE - ERIE SE 230 | T:77&78 | 192 | 239 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 192 | 239 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | T:77&78 | 192 | 239 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:BLISS1 | T:77&78 | 192 | 239 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:INDEK-OL | T:77&78 | 192 | 239 | 100.01
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:77&78 | 192 | 239 | 100.01
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:77&78 | 192 | 239 | 100.01
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:77&78 | 192 | 239 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:AMERT | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:INDECK SS | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:KAMINE | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:36 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:37 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:119 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:160 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:903 NY | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:953 NY | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:968 NY | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lancaster_922 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_103 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCWC/NWES | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCMB/NWES | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:MBWC/NWES | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ERIE E - 4 MILE 230 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | DUNKIRK - SRIPL 68 230 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SRIPL - ERIE E 69 230 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HILLSIDE 230/115 4TR | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CLAY - EDIC 2-15 345 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CLAY - DEW 3 115 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 1-3 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 4-6 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 7-9 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 10-12 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:MODERNLF | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 1 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 10 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 11 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 12 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 13 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 2 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 3 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 8 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 9 | T:77&78 | 192 | 239 | 100
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:UDG-184 | T:77&78 | 192 | 239 | 100
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:77&78 | 192 | 239 | 100
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 Max |  |  |  |  | 123.2
| Grand Max |  |  |  |  | 134.63

## N-1-1_ETC_OH_1000_Adjust
SERIES REACTORS ON 77 & 78 LINES IN-SERVICE
Niagara Dispatch | Monitored Facility | First Contingency | Second Contingency | Rate Base (MVA) | Rate Cont (MVA) | SCD AC %Loading
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 110.64
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 110.64
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 110.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 110.3
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 106.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 106.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 106.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 106.46
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | TB:2/1:MEYER | 474 | 478 | 105.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | TB:2/1:MEYER | 474 | 478 | 103.71
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | S:AVOCA | 474 | 478 | 102.99
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | CANDQUA - STNYRDG 68A 230 | 474 | 478 | 102.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt68 | 474 | 478 | 102.78
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt68 | 474 | 478 | 101.78
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | CANDQUA - STNYRDG 68A 230 | 474 | 478 | 100.52
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | S:AVOCA | 474 | 478 | 100.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | WTHRS - MEYER 230 | 474 | 478 | 100.1
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | WTHRS - MEYER 230 | 474 | 478 | 100.1
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_907 | WTHRS - MEYER 230 | 474 | 478 | 100.04
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | B:MEYER | 474 | 478 | 100.03
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | B:MEYER | 474 | 478 | 100.03
| 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  |  |  | 110.64
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | LN:115:181/922 | 119 | 119 | 122.14
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | LN:115:181/922 | 119 | 119 | 122.14
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | LN:115:181/922 | 119 | 119 | 122.06
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | LN:115:181/922 | 119 | 119 | 122.06
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_926B | LN:115:181/922 | 119 | 119 | 119.85
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_926B | LN:115:181/922 | 119 | 119 | 119.85
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-FV_37&W-F_171 | LN:115:181/922 | 119 | 119 | 116.13
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - HOMERCTY | LN:115:181/922 | 119 | 119 | 115.99
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-FV_37&W-F_171 | LN:115:181/922 | 119 | 119 | 115.77
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - HOMERCTY | LN:115:181/922 | 119 | 119 | 115.64
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV-HC | LN:115:181/922 | 119 | 119 | 115.33
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_STOL_HOMER_345 | LN:115:181/922 | 119 | 119 | 115.15
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | 5 MILE - STOLLE 37A 345 | LN:115:181/922 | 119 | 119 | 115.15
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | HOMERCTY - STOLLRD 37 345 | LN:115:181/922 | 119 | 119 | 115.15
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV-HC | 119 | 119 | 114.92
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV | LN:115:181/922 | 119 | 119 | 114.86
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:5M-SR_37&W-F_171 | 119 | 119 | 114.84
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV-HC | 119 | 119 | 114.78
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:5M-SR_37&W-F_171 | 119 | 119 | 114.7
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_STOL_HOMER_345 | 119 | 119 | 114.7
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | 5 MILE - STOLLE 37A 345 | 119 | 119 | 114.7
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:STOLE345 | 119 | 119 | 114.69
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | HOMERCTY - STOLLRD 37 345 | 119 | 119 | 114.69
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:5M-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 114.69
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:5MILE | 119 | 119 | 114.49
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV | 119 | 119 | 114.49
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | 5 MILE - STOLLE 37A 345 | 119 | 119 | 114.47
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_STOL_HOMER_345 | 119 | 119 | 114.47
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:STOLE345 | 119 | 119 | 114.47
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | HOMERCTY - STOLLRD 37 345 | 119 | 119 | 114.47
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:5MILE | 119 | 119 | 114.39
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV | 119 | 119 | 114.38
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV | LN:115:181/922 | 119 | 119 | 114.29
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:926 NY | LN:115:181/922 | 119 | 119 | 114.23
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | S:STOLLE345 | 119 | 119 | 114.22
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:5M-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 114.15
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | S:STOLLE345 | 119 | 119 | 114.11
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_STOL_HOMER_345 | LN:115:181/922 | 119 | 119 | 114.09
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | 5 MILE - STOLLE 37A 345 | LN:115:181/922 | 119 | 119 | 114.09
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | HOMERCTY - STOLLRD 37 345 | LN:115:181/922 | 119 | 119 | 114.09
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV-HC | LN:115:181/922 | 119 | 119 | 114.01
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_926B | 119 | 119 | 113.63
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_926B | 119 | 119 | 113.63
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:926 NY | LN:115:181/922 | 119 | 119 | 113.57
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:903 NY | LN:115:181/922 | 119 | 119 | 112.25
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:903 NY | LN:115:181/922 | 119 | 119 | 111.41
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:706 NY | LN:115:181/922 | 119 | 119 | 109.07
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_706 | LN:115:181/922 | 119 | 119 | 109.07
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:706 NY | LN:115:181/922 | 119 | 119 | 108.15
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_706 | LN:115:181/922 | 119 | 119 | 108.15
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:926 NY | 119 | 119 | 107.93
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:926 NY | 119 | 119 | 107.93
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-FV_37&W-F_171 | 119 | 119 | 107.45
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-FV_37&W-F_171 | 119 | 119 | 107.43
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - HOMERCTY | 119 | 119 | 107.41
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - HOMERCTY | 119 | 119 | 107.39
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | DUNKIRK - SRIPL 68 230 | LN:115:181/922 | 119 | 119 | 106.23
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SRIPL - ERIE E 69 230 | LN:115:181/922 | 119 | 119 | 106.16
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | DUNKIRK - SRIPL 68 230 | LN:115:181/922 | 119 | 119 | 105.6
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SRIPL - ERIE E 69 230 | LN:115:181/922 | 119 | 119 | 105.59
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | ERIE E - 4 MILE 230 | LN:115:181/922 | 119 | 119 | 104.35
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 104.33
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:FV-5M_37&W-F_171 | LN:115:181/922 | 119 | 119 | 104.33
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 104.02
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:FV-5M_37&W-F_171 | LN:115:181/922 | 119 | 119 | 104.02
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - 5MILE 345 | LN:115:181/922 | 119 | 119 | 103.93
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | ERIE E - 4 MILE 230 | LN:115:181/922 | 119 | 119 | 103.71
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - 5MILE 345 | LN:115:181/922 | 119 | 119 | 103.66
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:FV-5M_37&W-F_171 | 119 | 119 | 103.19
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-SR_37&W-F_171 | 119 | 119 | 103.19
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:FV-5M_37&W-F_171 | 119 | 119 | 103.1
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-SR_37&W-F_171 | 119 | 119 | 103.1
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:5MILE_B | 119 | 119 | 102.94
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:5MILE_B | 119 | 119 | 102.87
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:181/922 | 119 | 119 | 100.83
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | R:5M-SR_37&W-F_171 | 119 | 119 | 100.77
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | R:5M-SR_37&W-F_171 | 119 | 119 | 100.77
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - 5MILE 345 | 119 | 119 | 100.68
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - 5MILE 345 | 119 | 119 | 100.64
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:181/922 | 119 | 119 | 100.53
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:904 NY | LN:115:181/922 | 119 | 119 | 100.37
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_904 | LN:115:181/922 | 119 | 119 | 100.37
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:181/922 | 119 | 119 | 100.34
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:904 NY | LN:115:181/922 | 119 | 119 | 100.26
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_904 | LN:115:181/922 | 119 | 119 | 100.26
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:181/922 | 119 | 119 | 100.09
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | STONYCR - WTHRS 230 | LN:115:181/922 | 119 | 119 | 100.03
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | S:STOLLE345 | 119 | 119 | 100.02
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | S:STOLLE345 | 119 | 119 | 100.02
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | First:Lancaster_STOL_HOMER_345 | 119 | 119 | 100.01
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | 5 MILE - STOLLE 37A 345 | 119 | 119 | 100.01
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | B:STOLE345 | 119 | 119 | 100.01
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | HOMERCTY - STOLLRD 37 345 | 119 | 119 | 100.01
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | First:Lancaster_STOL_HOMER_345 | 119 | 119 | 100.01
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | 5 MILE - STOLLE 37A 345 | 119 | 119 | 100.01
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | B:STOLE345 | 119 | 119 | 100.01
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | HOMERCTY - STOLLRD 37 345 | 119 | 119 | 100.01
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | MEYER - CANDQUA 60 230 | LN:115:181/922 | 119 | 119 | 100.01
| 130795 DEPEW115 115 130799 ERIE 115 115 1 Max |  |  |  |  | 122.14
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 238 | 306 | 100.01
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 238 | 306 | 100.01
| 130815 HINMN115 115 131611 HARIS115 115 1 Max |  |  |  |  | 100.01
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | Base Case | 129 | 236 | 107.03
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | Base Case | 129 | 236 | 106.83
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:182S | Base Case | 129 | 236 | 100.02
| 135327 AM.S-54 115 135450 GRDNVL1 115 1 Max |  |  |  |  | 107.03
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | LN:115:133 | 168 | 206 | 100.28
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | LN:115:133 | 168 | 206 | 100.28
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 Max |  |  |  |  | 100.28
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 180 | 100.03
| 135452 LOCKPORT 115 135876 TELRDTP1 115 1 Max |  |  |  |  | 100.03
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | TB:2/1:NI2 | LN:115:129 | 239 | 298 | 101.25
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAGARA 230/115 2TR | LN:115:129 | 239 | 298 | 101.25
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | Base Case | 239 | 298 | 100.04
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:129 | 239 | 298 | 100.03
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:100 | LN:115:129 | 239 | 298 | 100.01
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:908 NY | LN:115:129 | 239 | 298 | 100.01
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:129 | 239 | 298 | 100.01
| 135455 MLPN-130 115 135461 PACK(S)W 115 1 Max |  |  |  |  | 101.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | Base Case | 160 | 206 | 111.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | Base Case | 160 | 206 | 111.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | Base Case | 160 | 206 | 104.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | Base Case | 160 | 206 | 102.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | Base Case | 160 | 206 | 100.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | Base Case | 160 | 206 | 100.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | Base Case | 160 | 206 | 100.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | Base Case | 160 | 206 | 100.01
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 Max |  |  |  |  | 111.55
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:194 | LN:115:195 | 273 | 351 | 136.75
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:195 | LN:115:194 | 273 | 351 | 127.85
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:194 | LN:115:195 | 273 | 351 | 117.4
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:195 | LN:115:194 | 273 | 351 | 108.58
| 135461 PACK(S)W 115 147851 NIAG115W 115 1 Max |  |  |  |  | 136.75
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:193 | LN:115:195 | 273 | 351 | 136.75
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:195 | LN:115:193 | 273 | 351 | 127.85
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:193 | LN:115:195 | 273 | 351 | 117.4
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:195 | LN:115:193 | 273 | 351 | 108.58
| 135461 PACK(S)W 115 147851 NIAG115W 115 2 Max |  |  |  |  | 136.75
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:193 | LN:115:194 | 273 | 351 | 126.93
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:194 | LN:115:193 | 273 | 351 | 126.93
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:193 | LN:115:194 | 273 | 351 | 107.35
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:194 | LN:115:193 | 273 | 351 | 107.35
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 Max |  |  |  |  | 126.93
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:101 | LN:115:102 | 168 | 206 | 101.32
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:102 | LN:115:101 | 168 | 206 | 101.31
| 135467 SHAW-103 115 135470 SWAN-103 115 1 Max |  |  |  |  | 101.32
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | First:Lockport_104 | LN:115:130 | 168 | 206 | 100.05
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROCH 345/115 5TR | LN:115:130 | 168 | 206 | 100.04
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | LN:115:130 | 168 | 206 | 100.02
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | LN:115:130 | 168 | 206 | 100.02
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:100 | LN:115:130 | 168 | 206 | 100.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:101 | LN:115:130 | 168 | 206 | 100.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:102 | LN:115:130 | 168 | 206 | 100.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:908 NY | LN:115:130 | 168 | 206 | 100.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:130 | 168 | 206 | 100.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:130 | 168 | 206 | 100.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:130 | 168 | 206 | 100.01
| 135497 ZRMN-133 115 135562 S214-133 115 1 Max |  |  |  |  | 100.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | Base Case | 192 | 288 | 100.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | Base Case | 192 | 288 | 100.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 192 | 288 | 100.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 192 | 288 | 100.01
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 Max |  |  |  |  | 100.04
| Grand Max |  |  |  |  | 136.75

## N-1_NTC_OH_1000
SERIES REACTORS ON 77 & 78 LINES IN-SERVICE
Niagara Dispatch | Monitored Facility | Rate Base (MVA) | Rate Cont (MVA) | Cont Name | Final AC %Loading
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 474 | 478 | DCT:230:77+78+THR | 114.4
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 474 | 478 | DCT:230:77+78 | 114.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 474 | 478 | T:77&78 | 114.3
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 474 | 478 | DCT:230:77+78+THR | 109.61
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 474 | 478 | DCT:230:77+78 | 109.53
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 474 | 478 | T:77&78 | 109.53
| 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  |  | 114.4
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | 119 | 119 | SB:PK115 30+40 | 108.78
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | 119 | 119 | SB:PK115 30+40 | 108.35
| 130795 DEPEW115 115 130799 ERIE 115 115 1 Max |  |  |  | 108.78
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | 139 | 163 | DCT:230:77+78 | 105.75
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | 139 | 163 | T:77&78 | 105.75
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | 139 | 163 | DCT:230:77+78+THR | 105.72
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | 139 | 163 | DCT:230:77+78 | 101.01
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | 139 | 163 | T:77&78 | 101.01
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | 139 | 163 | DCT:230:77+78+THR | 100.97
| 130834 N.BRW115 115 135437 CLSP-181 115 1 Max |  |  |  | 105.75
Dispatch 1 | 130847 ROLL 115 115 130857 STOLE115 115 1 | 90 | 90 | SB:181:ER | 101.77
Dispatch 2 | 130847 ROLL 115 115 130857 STOLE115 115 1 | 90 | 90 | SB:181:ER | 101.74
| 130847 ROLL 115 115 130857 STOLE115 115 1 Max |  |  |  | 101.77
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | 566 | 654 | LN:230:77 | 100.9
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | 566 | 654 | S:PA_HNTL77 | 100.79
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 Max |  |  |  | 100.9
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | 220 | 252 | DCT:230:77+80 | 102.89
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | 220 | 252 | T:77&80 | 102.89
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | 220 | 252 | DCT:230:77+80 | 102.31
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | 220 | 252 | T:77&80 | 102.31
| 135306 SAWYER79 230 135308 SAWYERB2 230 1 Max |  |  |  | 102.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 620 | 841 | T:62&BP76 | 108.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 620 | 841 | DCT:230:62+76 | 108.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 620 | 841 | SB:PK230 BS3+4 | 107.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | 620 | 841 | SB:PA230_R506 | 107.89
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 Max |  |  |  | 108.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 620 | 841 | DCT:230:61+64 | 103.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 620 | 841 | T:61&64 | 103.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 620 | 841 | SB:PK230 BS2+3 | 100.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | 620 | 841 | SB:PA230_R304 | 100.36
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 Max |  |  |  | 103.23
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | 145 | 151 | DCT:230:77+78+THR | 100.05
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | 145 | 151 | DCT:230:77+78 | 100.05
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | 145 | 151 | T:77&78 | 100.05
| 135433 AMHST-38 115 135472 S129-38 115 1 Max |  |  |  | 100.05
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | 139 | 163 | DCT:230:77+78 | 106.6
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | 139 | 163 | T:77&78 | 106.6
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | 139 | 163 | DCT:230:77+78+THR | 106.56
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | 139 | 163 | DCT:230:77+78 | 101.86
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | 139 | 163 | T:77&78 | 101.86
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | 139 | 163 | DCT:230:77+78+THR | 101.81
| 135437 CLSP-181 115 135495 YNG-181 115 1 Max |  |  |  | 106.6
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | 145 | 151 | DCT:230:77+78 | 101.64
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | 145 | 151 | DCT:230:77+78+THR | 101.64
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | 145 | 151 | T:77&78 | 101.64
| 135441 FMC-39 115 135473 S129-39 115 1 Max |  |  |  | 101.64
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 174 | 181 | DCT:230:77+78 | 110.06
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 174 | 181 | T:77&78 | 110.06
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 174 | 181 | DCT:230:77+78+THR | 110.02
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 174 | 181 | DCT:230:77+78 | 105.52
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 174 | 181 | T:77&78 | 105.52
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 174 | 181 | DCT:230:77+78+THR | 105.46
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 174 | 181 | DCT:115:180+182N | 104.56
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 174 | 181 | DCT:230:79+80+THR+ELM3-4 | 102.68
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 174 | 181 | DCT:230:79+80+ELM3-4 | 102.64
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 174 | 181 | DCT:115:180+182S | 101.18
| 135442 ECWA-181 115 135458 NI.B-181 115 1 Max |  |  |  | 110.06
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 174 | 181 | DCT:230:77+78 | 109.42
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 174 | 181 | T:77&78 | 109.42
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 174 | 181 | DCT:230:77+78+THR | 109.37
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 174 | 181 | DCT:230:77+78 | 104.92
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 174 | 181 | T:77&78 | 104.92
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 174 | 181 | DCT:230:77+78+THR | 104.85
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 174 | 181 | DCT:230:79+80+THR+ELM3-4 | 102.16
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 174 | 181 | DCT:230:79+80+ELM3-4 | 102.12
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 174 | 181 | DCT:115:180+182N | 101.68
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 174 | 181 | DCT:115:180+182S | 100.67
| 135442 ECWA-181 115 135495 YNG-181 115 1 Max |  |  |  | 109.42
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | 174 | 181 | DCT:230:77+78+THR | 106.71
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | 174 | 181 | DCT:230:77+78 | 106.64
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | 174 | 181 | T:77&78 | 106.64
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | 174 | 181 | DCT:230:77+78+THR | 101.51
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | 174 | 181 | DCT:230:77+78 | 101.43
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | 174 | 181 | T:77&78 | 101.43
| 135443 ECWA-182 115 135459 NI.B-182 115 1 Max |  |  |  | 106.71
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | 174 | 181 | DCT:230:77+78+THR | 106.85
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | 174 | 181 | DCT:230:77+78 | 106.77
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | 174 | 181 | T:77&78 | 106.77
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | 174 | 181 | DCT:230:77+78+THR | 101.61
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | 174 | 181 | DCT:230:77+78 | 101.52
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | 174 | 181 | T:77&78 | 101.52
| 135443 ECWA-182 115 135496 YNG-182 115 1 Max |  |  |  | 106.85
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 174 | 181 | DCT:230:77+78+THR | 112.96
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 174 | 181 | DCT:230:77+78 | 112.94
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 174 | 181 | T:77&78 | 112.94
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 174 | 181 | DCT:230:77+78+THR | 107.8
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 174 | 181 | DCT:230:77+78 | 107.79
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 174 | 181 | T:77&78 | 107.79
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 174 | 181 | DCT:115:180+181/922 | 105.88
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 174 | 181 | DCT:230:79+80+THR+ELM3-4 | 103.06
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 174 | 181 | DCT:230:79+80+ELM3-4 | 103.03
| 135449 GR.I-182 115 135459 NI.B-182 115 1 Max |  |  |  | 112.96
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:77+78 | 108.92
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | 200 | 208 | T:77&78 | 108.92
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:77+78+THR | 108.91
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:77+78 | 104.37
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | 200 | 208 | T:77&78 | 104.37
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:77+78+THR | 104.33
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | 200 | 208 | DCT:115:180+181/922 | 102.62
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:79+80+THR+ELM3-4 | 100.45
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:79+80+ELM3-4 | 100.42
| 135449 GR.I-182 115 135538 LONG-182 115 1 Max |  |  |  | 108.92
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | 145 | 151 | DCT:230:77+78 | 102.57
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | 145 | 151 | T:77&78 | 102.57
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | 145 | 151 | DCT:230:77+78+THR | 102.56
| 135451 HUNTLEY1 115 135472 S129-38 115 1 Max |  |  |  | 102.57
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | NF:115:133 HT | 117.5
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | NF:115:133 WL | 111.39
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | LN:115:133 | 110.63
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | LN:115:133 | 110.63
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | NF:115:133 HT | 108.74
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | DCT:230:77+78+THR | 107.89
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | DCT:230:77+78 | 107.83
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | T:77&78 | 107.83
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | BUS:115:PK-60 | 105.76
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | NF:115:129 WL | 103.7
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | NF:115:129 PK | 103.61
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | DCT:230:77+78+THR | 103.59
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | NF:115:133 WL | 103.57
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | DCT:230:77+78 | 103.51
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | T:77&78 | 103.51
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | SB:129:PK | 103.47
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | SB:WAL:129+133 | 103.45
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | LN:115:133 | 102.21
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | LN:115:133 | 102.21
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | LN:115:129 | 101.3
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | LN:115:129 | 101.3
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | DCT:230:79+80+THR+ELM3-4 | 100.68
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | 168 | 181 | DCT:230:79+80+ELM3-4 | 100.66
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 Max |  |  |  | 117.5
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | SB:130:PK | 113.82
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | DCT:230:77+78+THR | 110.93
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | DCT:230:77+78 | 110.88
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | T:77&78 | 110.88
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | LN:115:130 | 110.1
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | LN:115:130 | 110.1
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | BUS:115:PK-50 | 109.76
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | DCT:230:77+78+THR | 106.59
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | NF:115:130 PK | 106.56
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | DCT:230:77+78 | 106.54
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | T:77&78 | 106.54
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | SB:130:PK | 105.85
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | DCT:230:79+80+THR+ELM3-4 | 103.81
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | DCT:230:79+80+ELM3-4 | 103.79
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | BUS:115:PK-50 | 102.78
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | LN:115:130 | 101.75
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | LN:115:130 | 101.75
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | DCT:230:79+80+THR+ELM1-2 | 100.56
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | DCT:230:79+80+ELM1-2 | 100.53
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | 168 | 181 | DCT:230:79+80+ELM1-2 | 100.53
| 135451 HUNTLEY1 115 135562 S214-133 115 1 Max |  |  |  | 113.82
Dispatch 2 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | 233 | 253 | SB:37:LP | 103.52
Dispatch 2 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | 233 | 253 | SB:103:LP | 100.16
| 135452 LOCKPORT 115 135510 SHAW-102 115 1 Max |  |  |  | 103.52
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | 239 | 298 | SB:WAL:129+133 | 100.36
| 135455 MLPN-130 115 135461 PACK(S)W 115 1 Max |  |  |  | 100.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:115:180+182N | 130.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:77+78 | 129.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | T:77&78 | 129.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:77+78+THR | 129.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:115:180+182S | 126.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:77+78 | 124.28
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | T:77&78 | 124.28
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:77+78+THR | 124.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:115:54+182S | 122.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80+THR+ELM3-4 | 121.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80+ELM3-4 | 121.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:115:180+182N | 120.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:115:180+182S | 117.92
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:115:54+182S | 116.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80+THR+ELM1-2 | 116.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80+ELM1-2 | 116.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80+ELM1-2 | 116.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:GI115 | 116.13
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80+THR+ELM3-4 | 116.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80+ELM3-4 | 116.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80 | 115.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | T:79&80 | 115.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80+THR | 115.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:182N | 114.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:182N | 114.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:182S | 114.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:182S | 114.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | NF:115:182 GI-N | 114.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | NF:115:182 PK | 113.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:182N:PK | 113.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | BUS:115:PK-30 | 112.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80+THR+ELM1-2 | 111.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | NF:115:182 GI-S | 111.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80+ELM1-2 | 111.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80+ELM1-2 | 111.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80 | 110.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | T:79&80 | 110.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:79+80+THR | 110.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:GI115 | 108.83
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:182S | 107.33
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:182S | 107.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:115:102+180 | 106.83
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:182N | 106.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:182N | 106.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | NF:115:182 GI-N | 106.13
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | NF:115:182 PK | 105.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | GARDNVIL 115-2 | 104.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | NF:115:54 GV | 104.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | GARDNVIL 115-1 | 104.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:HUN230 BS68+C | 104.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | B:Hunt68 | 103.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:77HUN | 103.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:77+80 | 103.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | T:77&80 | 103.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:GARD230_TRC1 | 103.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:77HUN+THR | 103.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:GARD115_TRC1 | 103.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | BUS:230:HUN-68 | 103.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:78HUN+THR | 103.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:78HUN | 103.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:HUNT230_R1502 | 103.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:HUNT230_R1402 | 103.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:79HUN | 103.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:78+79 | 103.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | T:78&79 | 103.04
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | NF:115:182 GI-S | 102.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:230:77+80+THR | 102.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:GVNY230 6+7 | 102.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:103:LP | 102.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:180 | 102
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:180 | 102
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:GV:152+180 | 101.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:HUN230 BS67+C | 101.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:HUNT230_NEW | 101.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | NF:115:180 GV | 101.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | NF:115:BTCL PK | 101.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:108:LP | 101.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | NF:115:180 NI | 101.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:114:LP | 101.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | B:Hunt67 | 101.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:112:LP | 101.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | BUS:115:LP-2 | 101.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:101:LP | 101.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:111:LP | 101.44
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:182N:PK | 101.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | TOWER:66&705 | 101.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:80HUN+THR | 101.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | BUS:230:HUN-67 | 101.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:HUNT230_R1302 | 101.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:GARD230_T7-12 | 101.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:195 | 101.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:195 | 101.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:HUNT230_R1202 | 100.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:80HUN | 100.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | TB:2/1:PK3 | 100.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | TB:2/1:PK3 | 100.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:37:LP | 100.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | BUS:115:PK-30 | 100.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:77PK | 100.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | S:PA_HNTL77 | 100.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | DCT:115:185+186 | 100.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:77PK+THR | 100.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | SB:GVNY115 6+7 | 100.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:230:77 | 100.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | HUNTLEY - PACKARD 78 230 | 100.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | NF:230:78 HUN | 100.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:230:78 | 100.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | OE:HNTLEY_78 | 100.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | S:PA_HNTL78 | 100.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | HUNTLEY - PACKARD 77 230 | 100.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | TOWER:37&69 | 100.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | FARMVLY - HOMERCTY | 100.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:345:37FV-HC | 100.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | R:HC-FV_37&W-F_171 | 100.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:191 | 100.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 160 | 166 | LN:115:191 | 100.05
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 Max |  |  |  | 130.06
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:77+78 | 113.06
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 200 | 208 | T:77&78 | 113.06
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:77+78+THR | 113.03
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 200 | 208 | DCT:115:180+181/922 | 111.84
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:77+78 | 108.62
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 200 | 208 | T:77&78 | 108.62
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:77+78+THR | 108.57
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:79+80+THR+ELM3-4 | 104.56
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:79+80+ELM3-4 | 104.53
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 200 | 208 | DCT:115:180+181/922 | 103.47
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:79+80+THR+ELM3-4 | 100.17
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 200 | 208 | DCT:230:79+80+ELM3-4 | 100.13
| 135460 PACK(N)E 115 135538 LONG-182 115 1 Max |  |  |  | 113.06
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | 247 | 328 | DCT:115:101+191 | 109.36
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | 247 | 328 | DCT:230:61+191 | 103.65
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | 247 | 328 | T:61&191 | 103.65
| 135460 PACK(N)E 115 147850 NIAG115E 115 2 Max |  |  |  | 109.36
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | 273 | 351 | DCT:115:193+194 | 129.47
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | 273 | 351 | DCT:115:193+194 | 109.93
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | 273 | 351 | SB:129:PK | 109.66
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | 273 | 351 | BUS:115:PK-60 | 108.55
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | 273 | 351 | SB:129:PK | 100.84
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 Max |  |  |  | 129.47
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | SB:130:PK | 114.24
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:77+78+THR | 111.71
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:77+78 | 111.67
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | T:77&78 | 111.67
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | LN:115:130 | 110.6
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | LN:115:130 | 110.6
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | BUS:115:PK-50 | 110.34
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:77+78+THR | 107.43
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:77+78 | 107.39
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | T:77&78 | 107.39
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | NF:115:130 PK | 107.21
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | SB:130:PK | 106.43
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:79+80+THR+ELM3-4 | 104.77
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:79+80+ELM3-4 | 104.75
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | BUS:115:PK-50 | 103.52
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | LN:115:130 | 102.42
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | LN:115:130 | 102.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:79+80+THR+ELM1-2 | 101.51
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:79+80+ELM1-2 | 101.48
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:79+80+ELM1-2 | 101.48
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:79+80 | 100.93
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | T:79&80 | 100.93
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:79+80+THR | 100.9
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:79+80+THR+ELM3-4 | 100.47
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | DCT:230:79+80+ELM3-4 | 100.45
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | 168 | 185 | NF:115:130 PK | 100.04
| 135497 ZRMN-133 115 135562 S214-133 115 1 Max |  |  |  | 114.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | DCT:230:77+78+THR | 125.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | DCT:230:77+78 | 125.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | T:77&78 | 125.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | DCT:230:79+80+THR+ELM3-4 | 113.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | DCT:230:79+80+ELM3-4 | 113.43
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | SB:78PK | 111.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | SB:78PK+THR | 111.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | SB:PA230_R3230 | 111.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | DCT:230:79+80+THR+ELM1-2 | 108.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | DCT:230:79+80+ELM1-2 | 108.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | DCT:230:79+80+ELM1-2 | 108.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | DCT:230:61+64 | 106.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | T:61&64 | 106.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | DCT:230:79+80 | 106.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | T:79&80 | 106.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | 192 | 239 | DCT:230:79+80+THR | 106.75
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 Max |  |  |  | 125.6
| Grand Max |  |  |  | 130.06

## N-2_NTC_OH_1000_Fixed
SERIES REACTORS ON 77 & 78 LINES IN-SERVICE
Niagara Dispatch | Monitored Facility | First Level Scenario | Cont Name | Rate Base (MVA) | Rate Cont (MVA) | Final AC %Loading
Dispatch 1 | 130754 SOMERSET345 345 149690 NEWROCH345 345 1 | STOLLRD - SHLDON 67 230 | HILLSIDE 230/115 4TR | 1301 | 1501 | NConv
Dispatch 1 | 130754 SOMERSET345 345 149690 NEWROCH345 345 1 | STOLLRD - SHLDON 67 230 | B:HILLSIDE | 1301 | 1501 | NConv
Dispatch 1 | 130754 SOMERSET345 345 149690 NEWROCH345 345 1 | STOLLRD - SHLDON 67 230 | SB:HILL_B412 | 1301 | 1501 | NConv
Dispatch 1 | 130754 SOMERSET345 345 149690 NEWROCH345 345 1 | STOLLRD - SHLDON 67 230 | SB:STONYRIDGE | 1301 | 1501 | NConv
Dispatch 1 | 130754 SOMERSET345 345 149690 NEWROCH345 345 1 | STOLLRD - SHLDON 67 230 | CANDQUA - STNYRDG 68A 230 | 1301 | 1501 | NConv
Dispatch 1 | 130754 SOMERSET345 345 149690 NEWROCH345 345 1 | STOLLRD - SHLDON 67 230 | S:AVOCA | 1301 | 1501 | NConv
Dispatch 2 | 130754 SOMERSET345 345 149690 NEWROCH345 345 1 | STOLLRD - SHLDON 67 230 | HILLSIDE 230/115 4TR | 1301 | 1501 | NConv
Dispatch 2 | 130754 SOMERSET345 345 149690 NEWROCH345 345 1 | STOLLRD - SHLDON 67 230 | B:HILLSIDE | 1301 | 1501 | NConv
Dispatch 2 | 130754 SOMERSET345 345 149690 NEWROCH345 345 1 | STOLLRD - SHLDON 67 230 | SB:HILL_B412 | 1301 | 1501 | NConv
| 130754 SOMERSET345 345 149690 NEWROCH345 345 1 Max |  |  |  |  | 0
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | T:72&69 | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | STOLLRD - SHLDON 67 230 | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:67&37A | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | SB:SHLDN230 | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | MEYER - CANDQUA 60 230 | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | MEYER - CANDQUA 60 230 | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | T:67&37A | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | STOLLRD - SHLDON 67 230 | 474 | 478 | NConv
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | T:72&69 | 474 | 478 | NConv
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 474 | 478 | NConv
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | MEYER - CANDQUA 60 230 | 474 | 478 | NConv
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | MEYER - CANDQUA 60 230 | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:77&78 | 474 | 478 | 147.52
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:77&78 | 474 | 478 | 143.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 474 | 478 | 135.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | T:77&78 | 474 | 478 | 131.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 474 | 478 | 130.78
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 127.98
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | T:77&78 | 474 | 478 | 127.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:79&80 | 474 | 478 | 127.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:180 | T:77&78 | 474 | 478 | 125.76
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:182N | T:77&78 | 474 | 478 | 125.71
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | T:77&78 | 474 | 478 | 125.53
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:345:37S-FM-FV-HC | T:77&78 | 474 | 478 | 125.32
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | T:77&78 | 474 | 478 | 124.47
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:182S | T:77&78 | 474 | 478 | 124.45
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 474 | 478 | 124.22
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:181/922 | T:77&78 | 474 | 478 | 124.2
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | T:77&78 | 474 | 478 | 124.08
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 123.63
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - HOMERCTY | T:77&78 | 474 | 478 | 123.36
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:79&80 | 474 | 478 | 123.25
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 474 | 478 | 123.14
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 474 | 478 | 123.14
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | T:77&78 | 474 | 478 | 123.11
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | T:77&78 | 474 | 478 | 122.69
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:345:37S-FM-FV-HC | T:77&78 | 474 | 478 | 122.11
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:345:37S-FM-FV | T:77&78 | 474 | 478 | 122.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:180 | T:77&78 | 474 | 478 | 121.97
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:182N | T:77&78 | 474 | 478 | 121.73
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:ROB | T:77&78 | 474 | 478 | 121.72
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:NI1 | T:77&78 | 474 | 478 | 121.69
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 1TR | T:77&78 | 474 | 478 | 121.69
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:38 | T:77&78 | 474 | 478 | 121.61
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:39 | T:77&78 | 474 | 478 | 121.26
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | T:77&78 | 474 | 478 | 120.91
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:182S | T:77&78 | 474 | 478 | 120.48
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 474 | 478 | 120.26
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:181/922 | T:77&78 | 474 | 478 | 120.18
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 3TR | T:77&78 | 474 | 478 | 120.11
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | T:77&78 | 474 | 478 | 119.78
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 474 | 478 | 119.76
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:907 NY | T:77&78 | 474 | 478 | 119.7
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SHLDON - STONYCR 230 | T:77&78 | 474 | 478 | 119.64
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_907 | T:77&78 | 474 | 478 | 119.43
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | T:77&78 | 474 | 478 | 119.4
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:133 | T:77&78 | 474 | 478 | 119.26
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:130 | T:77&78 | 474 | 478 | 119.11
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 474 | 478 | 118.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 474 | 478 | 118.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - HOMERCTY | T:77&78 | 474 | 478 | 118.77
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 474 | 478 | 118.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:129 | T:77&78 | 474 | 478 | 118.62
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS1 | T:77&78 | 474 | 478 | 118.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | T:77&78 | 474 | 478 | 118.36
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:345:37S-FM-FV | T:77&78 | 474 | 478 | 118.19
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | T:77&78 | 474 | 478 | 118.06
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_922 | T:77&78 | 474 | 478 | 117.88
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:INDEK-OL | T:77&78 | 474 | 478 | 117.7
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 474 | 478 | 117.62
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 474 | 478 | 117.62
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 474 | 478 | 117.61
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:38 | T:77&78 | 474 | 478 | 117.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 4 | T:77&78 | 474 | 478 | 117.01
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 5 | T:77&78 | 474 | 478 | 117.01
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 6 | T:77&78 | 474 | 478 | 117.01
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 7 | T:77&78 | 474 | 478 | 116.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:39 | T:77&78 | 474 | 478 | 116.91
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN7 | T:77&78 | 474 | 478 | 116.83
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | T:77&78 | 474 | 478 | 116.83
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAG - NEWROCH 1 345 | T:77&78 | 474 | 478 | 116.77
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 474 | 478 | 116.59
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 474 | 478 | 116.21
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:966 NY | T:77&78 | 474 | 478 | 116.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS2 | T:77&78 | 474 | 478 | 115.92
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 474 | 478 | 115.67
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:NI2 | T:77&78 | 474 | 478 | 115.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 2TR | T:77&78 | 474 | 478 | 115.66
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:HUN | T:77&78 | 474 | 478 | 115.62
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/1:FMR | T:77&78 | 474 | 478 | 115.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE 345/115 1TR | T:77&78 | 474 | 478 | 115.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | 4 MILE - ERIE SE 230 | T:77&78 | 474 | 478 | 115.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:PK4 | T:77&78 | 474 | 478 | 115.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 4TR | T:77&78 | 474 | 478 | 115.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 1 | T:77&78 | 474 | 478 | 115.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 2 | T:77&78 | 474 | 478 | 115.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 3 | T:77&78 | 474 | 478 | 115.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:968 NY | T:77&78 | 474 | 478 | 115.5
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 474 | 478 | 115.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:ROB | T:77&78 | 474 | 478 | 115.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SHLDON - STONYCR 230 | T:77&78 | 474 | 478 | 115.45
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:DUPONT46 | T:77&78 | 474 | 478 | 115.41
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 115.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | T:77&78 | 474 | 478 | 115.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 115.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 115.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 115.34
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | T:77&78 | 474 | 478 | 115.11
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:5M-SR_37&W-F_171 | T:77&78 | 474 | 478 | 115.02
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 474 | 478 | 114.98
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 474 | 478 | 114.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:133 | T:77&78 | 474 | 478 | 114.84
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:130 | T:77&78 | 474 | 478 | 114.65
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:NI1 | T:77&78 | 474 | 478 | 114.45
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA 230/115 1TR | T:77&78 | 474 | 478 | 114.45
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | TB:2/1:MEYER | 474 | 478 | 114.21
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:129 | T:77&78 | 474 | 478 | 114.21
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | PACKARD 230/115 3TR | T:77&78 | 474 | 478 | 114.21
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS1 | T:77&78 | 474 | 478 | 113.8
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 113.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 474 | 478 | 113.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 474 | 478 | 113.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 474 | 478 | 113.62
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | CANDQUA - STNYRDG 68A 230 | 474 | 478 | 113.55
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | S:AVOCA | 474 | 478 | 113.55
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:907 NY | T:77&78 | 474 | 478 | 113.5
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | SB:STONYRIDGE | 474 | 478 | 113.48
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lancaster_922 | T:77&78 | 474 | 478 | 113.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:KAMINE | T:77&78 | 474 | 478 | 113.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE - WATERCURE 69 230 | T:77&78 | 474 | 478 | 113.22
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE - ETWANDA 70 230 | T:77&78 | 474 | 478 | 113.22
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_907 | T:77&78 | 474 | 478 | 113.22
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:141 | T:77&78 | 474 | 478 | 113.21
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:906 NY | T:77&78 | 474 | 478 | 113.2
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:120 | T:77&78 | 474 | 478 | 113.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:142 | T:77&78 | 474 | 478 | 113.09
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:161 | T:77&78 | 474 | 478 | 113.07
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:102 | T:77&78 | 474 | 478 | 113.05
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 4 | T:77&78 | 474 | 478 | 113.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 5 | T:77&78 | 474 | 478 | 113.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 6 | T:77&78 | 474 | 478 | 113.03
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:INDEK-OL | T:77&78 | 474 | 478 | 113.02
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 7 | T:77&78 | 474 | 478 | 113.01
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:GINNA | T:77&78 | 474 | 478 | 112.99
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | ERIE E - 4 MILE 230 | T:77&78 | 474 | 478 | 112.99
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDL - FRASER 32 345 | T:77&78 | 474 | 478 | 112.98
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:GINNA | T:77&78 | 474 | 478 | 112.97
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:101 | T:77&78 | 474 | 478 | 112.95
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:934 NY | T:77&78 | 474 | 478 | 112.87
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - DUNKIRK 73 230 | T:77&78 | 474 | 478 | 112.87
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - DUNKIRK 74 230 | T:77&78 | 474 | 478 | 112.86
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:54/921 | T:77&78 | 474 | 478 | 112.84
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:195 | T:77&78 | 474 | 478 | 112.41
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:79&80 | 474 | 478 | 112.39
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAG - NEWROCH 1 345 | T:77&78 | 474 | 478 | 112.39
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:903 NY | T:77&78 | 474 | 478 | 112.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/2:FV | T:77&78 | 474 | 478 | 112.21
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - FARMVLY | T:77&78 | 474 | 478 | 112.21
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:JAMESGN7 | T:77&78 | 474 | 478 | 112.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:192 | T:77&78 | 474 | 478 | 112.18
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:191 | T:77&78 | 474 | 478 | 112.16
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | TB:2/1:MEYER | 474 | 478 | 112.12
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 112.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 474 | 478 | 112.05
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 474 | 478 | 111.65
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt68 | 474 | 478 | 111.64
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | S:AVOCA | 474 | 478 | 111.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | CANDQUA - STNYRDG 68A 230 | 474 | 478 | 111.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:966 NY | T:77&78 | 474 | 478 | 111.41
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:160 | T:77&78 | 474 | 478 | 111.4
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | SB:STONYRIDGE | 474 | 478 | 111.39
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:77&80 | 474 | 478 | 111.37
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK - SRIPL 68 230 | T:77&78 | 474 | 478 | 111.36
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:HUN | T:77&78 | 474 | 478 | 111.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SRIPL - ERIE E 69 230 | T:77&78 | 474 | 478 | 111.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1502 | 474 | 478 | 111.31
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 1 | T:77&78 | 474 | 478 | 111.31
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 2 | T:77&78 | 474 | 478 | 111.31
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:NIAG. 3 | T:77&78 | 474 | 478 | 111.31
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:BLISS2 | T:77&78 | 474 | 478 | 111.2
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | T:79&80 | 474 | 478 | 111.08
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 474 | 478 | 110.95
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1402 | 474 | 478 | 110.91
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:78&79 | 474 | 478 | 110.91
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 4 MILE - ERIE SE 230 | T:77&78 | 474 | 478 | 110.84
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:968 NY | T:77&78 | 474 | 478 | 110.79
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 474 | 478 | 110.78
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:DUPONT46 | T:77&78 | 474 | 478 | 110.78
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/1:FMR | T:77&78 | 474 | 478 | 110.73
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | 5 MILE 345/115 1TR | T:77&78 | 474 | 478 | 110.73
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 110.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 110.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 474 | 478 | 110.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 110.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 110.57
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 474 | 478 | 110.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:PA230_R3230 | 474 | 478 | 109.64
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_NEW | 474 | 478 | 109.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:GV1 | T:77&78 | 474 | 478 | 109.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:GV2 | T:77&78 | 474 | 478 | 109.28
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | LN:115:908 NY | 474 | 478 | 109
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 108.91
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt68 | 474 | 478 | 108.85
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | WTHRS - MEYER 230 | 474 | 478 | 108.6
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | B:MEYER | 474 | 478 | 108.57
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt67 | 474 | 478 | 108.56
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:77&80 | 474 | 478 | 108.53
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1502 | 474 | 478 | 108.44
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:120 | T:77&78 | 474 | 478 | 108.38
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:142 | T:77&78 | 474 | 478 | 108.38
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:161 | T:77&78 | 474 | 478 | 108.36
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1302 | 474 | 478 | 108.31
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | ERIE E - 4 MILE 230 | T:77&78 | 474 | 478 | 108.29
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:102 | T:77&78 | 474 | 478 | 108.21
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | OAKDL - FRASER 32 345 | T:77&78 | 474 | 478 | 108.2
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GEN:115:GINNA | T:77&78 | 474 | 478 | 108.19
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:934 NY | T:77&78 | 474 | 478 | 108.19
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | G:GINNA | T:77&78 | 474 | 478 | 108.16
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1202 | 474 | 478 | 108.14
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - DUNKIRK 73 230 | T:77&78 | 474 | 478 | 108.13
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | GARDENVILL - DUNKIRK 74 230 | T:77&78 | 474 | 478 | 108.11
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:54/921 | T:77&78 | 474 | 478 | 108.1
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:101 | T:77&78 | 474 | 478 | 108.1
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | T:79&80 | 474 | 478 | 108.09
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1402 | 474 | 478 | 107.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:78&79 | 474 | 478 | 107.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:195 | T:77&78 | 474 | 478 | 107.79
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | LN:115:100 | 474 | 478 | 107.73
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 107.71
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | WTHRS - MEYER 230 | 474 | 478 | 107.63
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:903 NY | T:77&78 | 474 | 478 | 107.61
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:MEYER | 474 | 478 | 107.58
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | WTHRS - MEYER 230 | 474 | 478 | 107.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 474 | 478 | 107.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:MEYER | 474 | 478 | 107.51
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:192 | T:77&78 | 474 | 478 | 107.5
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:191 | T:77&78 | 474 | 478 | 107.47
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:3/2:FV | T:77&78 | 474 | 478 | 107.43
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | FARMVLY - FARMVLY | T:77&78 | 474 | 478 | 107.43
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | S:PA_HNTL77 | 474 | 478 | 107.37
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | WTHRS - MEYER 230 | 474 | 478 | 107.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 107.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | S:PA_HNTL78 | 474 | 478 | 107.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | B:MEYER | 474 | 478 | 107.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 107.25
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STONYCR - WTHRS 230 | T:79&80 | 474 | 478 | 107.06
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | DUNKIRK - SRIPL 68 230 | T:77&78 | 474 | 478 | 106.71
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:160 | T:77&78 | 474 | 478 | 106.66
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | SRIPL - ERIE E 69 230 | T:77&78 | 474 | 478 | 106.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_NEW | 474 | 478 | 106.52
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:PA230_R3230 | 474 | 478 | 106.44
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | TB:2/1:ROB | 474 | 478 | 106.16
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:PA230_R3430 | 474 | 478 | 105.93
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt67 | 474 | 478 | 105.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:ROB | WTHRS - MEYER 230 | 474 | 478 | 105.73
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:ROB | B:MEYER | 474 | 478 | 105.69
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 474 | 478 | 105.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1302 | 474 | 478 | 105.53
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | LN:115:908 NY | 474 | 478 | 105.39
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:HUNT230_R1202 | 474 | 478 | 105.26
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | WTHRS - MEYER 230 | 474 | 478 | 104.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | WTHRS - MEYER 230 | 474 | 478 | 104.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | B:MEYER | 474 | 478 | 104.95
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:MEYER | 474 | 478 | 104.91
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | WTHRS - MEYER 230 | 474 | 478 | 104.9
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:MEYER | 474 | 478 | 104.85
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | S:PA_HNTL77 | 474 | 478 | 104.73
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | S:PA_HNTL78 | 474 | 478 | 104.67
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 104.67
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 104.62
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:GV1 | T:77&78 | 474 | 478 | 104.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CAP:115:GV2 | T:77&78 | 474 | 478 | 104.46
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 474 | 478 | 104.3
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | LN:115:907 NY | 474 | 478 | 103.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | LN:115:100 | 474 | 478 | 103.95
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 103.91
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 474 | 478 | 103.89
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | WTHRS - MEYER 230 | 474 | 478 | 103.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:907 NY | WTHRS - MEYER 230 | 474 | 478 | 103.55
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | First:Lockport_907 | 474 | 478 | 103.53
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | B:MEYER | 474 | 478 | 103.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:907 NY | B:MEYER | 474 | 478 | 103.51
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-WC_30&W-F_171 | T:77&78 | 474 | 478 | 103.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 474 | 478 | 103.22
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 474 | 478 | 103.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 474 | 478 | 103.15
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_907 | WTHRS - MEYER 230 | 474 | 478 | 103.14
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 474 | 478 | 103.12
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_907 | B:MEYER | 474 | 478 | 103.1
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 474 | 478 | 103.08
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:PA230_R3430 | 474 | 478 | 102.96
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | S:HNT_GRD80 | 474 | 478 | 102.87
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | WTHRS - MEYER 230 | 474 | 478 | 102.86
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | WTHRS - MEYER 230 | 474 | 478 | 102.85
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | B:MEYER | 474 | 478 | 102.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - GARDENVILL 79 230 | 474 | 478 | 102.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | B:MEYER | 474 | 478 | 102.8
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - GARDENVILL 80 230 | 474 | 478 | 102.8
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 474 | 478 | 102.63
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HCWC/NWES | T:77&78 | 474 | 478 | 102.61
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:MBWC/NWES | T:77&78 | 474 | 478 | 102.61
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | MEYER - CANDQUA 60 230 | T:79&80 | 474 | 478 | 102.55
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 474 | 478 | 102.39
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | TB:2/1:ROB | 474 | 478 | 102.38
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 474 | 478 | 102.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 474 | 478 | 102.2
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:ROB | WTHRS - MEYER 230 | 474 | 478 | 101.95
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:ROB | B:MEYER | 474 | 478 | 101.91
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:GARD72&79 | 474 | 478 | 101.89
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | DCT:230:79+80+ELM1-2 | 474 | 478 | 101.89
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 474 | 478 | 101.82
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | DCT:230:79+80+ELM1-2 | 474 | 478 | 101.72
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 474 | 478 | 101.42
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 474 | 478 | 101.41
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 474 | 478 | 101.38
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | SB:GARD230_R873 | 474 | 478 | 100.99
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:GARD73&80 | 474 | 478 | 100.64
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 100.54
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | DCT:230:79+80+ELM1-2 | 474 | 478 | 100.43
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | T:79&80 | 474 | 478 | 100.4
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | LN:115:907 NY | 474 | 478 | 100.35
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:41&33 | 474 | 478 | 100.33
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | S:HNT_GRD80 | 474 | 478 | 100.33
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | WTHRS - MEYER 230 | 474 | 478 | 100.3
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | WTHRS - MEYER 230 | 474 | 478 | 100.29
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - GARDENVILL 79 230 | 474 | 478 | 100.27
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - GARDENVILL 80 230 | 474 | 478 | 100.26
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | B:MEYER | 474 | 478 | 100.25
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | SHLDON - STONYCR 230 | DCT:230:79+80+ELM1-2 | 474 | 478 | 100.24
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | B:MEYER | 474 | 478 | 100.24
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 474 | 478 | 100.23
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | T:40&41 | 474 | 478 | 100.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | T:79&80 | 474 | 478 | 100.13
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 474 | 478 | 100.09
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 474 | 478 | 100.05
| 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  |  |  | 147.52
Dispatch 1 | 130766 ROBIN230 230 130767 STOLE230 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 550 | 637 | NConv
Dispatch 1 | 130766 ROBIN230 230 130767 STOLE230 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 550 | 637 | NConv
Dispatch 1 | 130766 ROBIN230 230 130767 STOLE230 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 550 | 637 | NConv
Dispatch 1 | 130766 ROBIN230 230 130767 STOLE230 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 550 | 637 | NConv
Dispatch 1 | 130766 ROBIN230 230 130767 STOLE230 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 550 | 637 | NConv
Dispatch 2 | 130766 ROBIN230 230 130767 STOLE230 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 550 | 637 | NConv
Dispatch 2 | 130766 ROBIN230 230 130767 STOLE230 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 550 | 637 | NConv
Dispatch 2 | 130766 ROBIN230 230 130767 STOLE230 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 550 | 637 | NConv
Dispatch 2 | 130766 ROBIN230 230 130767 STOLE230 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 550 | 637 | NConv
Dispatch 2 | 130766 ROBIN230 230 130767 STOLE230 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 550 | 637 | NConv
| 130766 ROBIN230 230 130767 STOLE230 230 1 Max |  |  |  |  | 0
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 496 | 657 | NConv
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 496 | 657 | NConv
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 496 | 657 | NConv
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 496 | 657 | NConv
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 496 | 657 | NConv
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 496 | 657 | NConv
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 496 | 657 | NConv
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 496 | 657 | NConv
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 496 | 657 | NConv
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 496 | 657 | NConv
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - NEWROCH 1 345 | T:77&78 | 496 | 657 | 113.16
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 496 | 657 | 109.47
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - NEWROCH 1 345 | T:77&78 | 496 | 657 | 105.87
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | TB:2/1:NI1 | T:77&78 | 496 | 657 | 104.22
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAGARA 230/115 1TR | T:77&78 | 496 | 657 | 104.22
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 496 | 657 | 102.12
| 130766 ROBIN230 230 147841 NIAGAR2E 230 1 Max |  |  |  |  | 113.16
Dispatch 1 | 130775 BIGTR115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 1 | 130775 BIGTR115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 139 | 163 | NConv
Dispatch 1 | 130775 BIGTR115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 139 | 163 | NConv
Dispatch 1 | 130775 BIGTR115 115 131467 LANGN115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 1 | 130775 BIGTR115 115 131467 LANGN115 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 139 | 163 | NConv
Dispatch 2 | 130775 BIGTR115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 2 | 130775 BIGTR115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 139 | 163 | NConv
Dispatch 2 | 130775 BIGTR115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 139 | 163 | NConv
Dispatch 2 | 130775 BIGTR115 115 131467 LANGN115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 2 | 130775 BIGTR115 115 131467 LANGN115 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 139 | 163 | NConv
| 130775 BIGTR115 115 131467 LANGN115 115 1 Max |  |  |  |  | 0
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 119 | 119 | NConv
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 119 | 119 | NConv
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 119 | 119 | NConv
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 119 | 119 | NConv
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 119 | 119 | NConv
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 119 | 119 | NConv
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 119 | 119 | NConv
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 119 | 119 | NConv
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 119 | 119 | NConv
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 119 | 119 | NConv
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:705 NY | 119 | 119 | 125.4
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_705 | 119 | 119 | 125.4
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | LN:115:181/922 | 119 | 119 | 125.11
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | LN:115:181/922 | 119 | 119 | 125.11
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:705 NY | 119 | 119 | 124.45
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_705 | 119 | 119 | 124.45
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | LN:115:181/922 | 119 | 119 | 124.21
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | LN:115:181/922 | 119 | 119 | 124.21
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-FV_37&W-F_171 | 119 | 119 | 121.49
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - HOMERCTY | 119 | 119 | 121.35
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-FV_37&W-F_171 | 119 | 119 | 120.92
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - HOMERCTY | 119 | 119 | 120.82
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_926B | LN:115:181/922 | 119 | 119 | 119.57
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_926B | LN:115:181/922 | 119 | 119 | 119.46
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-FV_37&W-F_171 | LN:115:181/922 | 119 | 119 | 118.39
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_926B | 119 | 119 | 118.3
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_926B | 119 | 119 | 118.26
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - HOMERCTY | LN:115:181/922 | 119 | 119 | 118.24
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-FV_37&W-F_171 | LN:115:181/922 | 119 | 119 | 117.85
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - HOMERCTY | LN:115:181/922 | 119 | 119 | 117.71
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV-HC | 119 | 119 | 116.56
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:5M-SR_37&W-F_171 | 119 | 119 | 116.22
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV-HC | 119 | 119 | 116
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_STOL_HOMER_345 | 119 | 119 | 116
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | 5 MILE - STOLLE 37A 345 | 119 | 119 | 116
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:STOLE345 | 119 | 119 | 116
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | HOMERCTY - STOLLRD 37 345 | 119 | 119 | 116
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:5MILE | 119 | 119 | 115.96
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV | 119 | 119 | 115.96
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:5M-SR_37&W-F_171 | 119 | 119 | 115.82
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_STOL_HOMER_345 | 119 | 119 | 115.62
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | 5 MILE - STOLLE 37A 345 | 119 | 119 | 115.62
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:STOLE345 | 119 | 119 | 115.62
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | HOMERCTY - STOLLRD 37 345 | 119 | 119 | 115.62
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | S:STOLLE345 | 119 | 119 | 115.6
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:67&37A | 119 | 119 | 115.5
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:5MILE | 119 | 119 | 115.46
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV | 119 | 119 | 115.46
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:5M-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 115.33
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV-HC | LN:115:181/922 | 119 | 119 | 115.27
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | S:STOLLE345 | 119 | 119 | 115.15
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_STOL_HOMER_345 | LN:115:181/922 | 119 | 119 | 115.14
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | 5 MILE - STOLLE 37A 345 | LN:115:181/922 | 119 | 119 | 115.14
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | HOMERCTY - STOLLRD 37 345 | LN:115:181/922 | 119 | 119 | 115.14
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:67&37A | 119 | 119 | 115.07
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV | LN:115:181/922 | 119 | 119 | 114.97
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:903 NY | LN:115:181/922 | 119 | 119 | 114.88
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:903 NY | 119 | 119 | 114.72
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:5M-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 114.25
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV-HC | LN:115:181/922 | 119 | 119 | 114.2
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:903 NY | LN:115:181/922 | 119 | 119 | 114.2
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_STOL_HOMER_345 | LN:115:181/922 | 119 | 119 | 114.06
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | 5 MILE - STOLLE 37A 345 | LN:115:181/922 | 119 | 119 | 114.06
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | HOMERCTY - STOLLRD 37 345 | LN:115:181/922 | 119 | 119 | 114.06
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:903 NY | 119 | 119 | 114.01
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV | LN:115:181/922 | 119 | 119 | 113.83
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:926 NY | LN:115:181/922 | 119 | 119 | 113.66
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:926 NY | LN:115:181/922 | 119 | 119 | 113.45
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:926 NY | 119 | 119 | 112.45
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:926 NY | 119 | 119 | 112.23
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:706 NY | 119 | 119 | 112.02
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_706 | 119 | 119 | 112.02
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:706 NY | LN:115:181/922 | 119 | 119 | 111.71
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_706 | LN:115:181/922 | 119 | 119 | 111.71
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:706 NY | 119 | 119 | 111.08
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_706 | 119 | 119 | 111.08
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:706 NY | LN:115:181/922 | 119 | 119 | 110.79
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_706 | LN:115:181/922 | 119 | 119 | 110.79
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:DUNK230_R1312 | 119 | 119 | 109.77
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:DUNK230_R1312 | 119 | 119 | 109.15
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:73&74 | 119 | 119 | 108.88
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | DUNKIRK - SRIPL 68 230 | LN:115:181/922 | 119 | 119 | 108.61
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SRIPL - ERIE E 69 230 | LN:115:181/922 | 119 | 119 | 108.5
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:5MILE_B | 119 | 119 | 108.37
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:73&74 | 119 | 119 | 108.28
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:5MILE_B | 119 | 119 | 108.1
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SRIPL - ERIE E 69 230 | LN:115:181/922 | 119 | 119 | 107.72
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | DUNKIRK - SRIPL 68 230 | LN:115:181/922 | 119 | 119 | 107.7
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | ERIE E - 4 MILE 230 | LN:115:181/922 | 119 | 119 | 106.73
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-SR_37&W-F_171 | 119 | 119 | 106.52
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:FV-5M_37&W-F_171 | 119 | 119 | 106.52
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 106.35
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:FV-5M_37&W-F_171 | LN:115:181/922 | 119 | 119 | 106.35
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-SR_37&W-F_171 | 119 | 119 | 106.29
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:FV-5M_37&W-F_171 | 119 | 119 | 106.29
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:41&33 | 119 | 119 | 106.28
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - 5MILE 345 | 119 | 119 | 106.22
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | ERIE E - 4 MILE 230 | LN:115:181/922 | 119 | 119 | 106.09
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 106.02
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:FV-5M_37&W-F_171 | LN:115:181/922 | 119 | 119 | 106.02
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:DUNKG4 | 119 | 119 | 105.99
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - 5MILE 345 | 119 | 119 | 105.91
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | WTHRS - MEYER 230 | LN:115:181/922 | 119 | 119 | 105.78
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - 5MILE 345 | LN:115:181/922 | 119 | 119 | 105.77
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:40&41 | 119 | 119 | 105.67
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:41&33 | 119 | 119 | 105.63
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - 5MILE 345 | LN:115:181/922 | 119 | 119 | 105.53
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | WTHRS - MEYER 230 | 119 | 119 | 105.52
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:MEYER | 119 | 119 | 105.4
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:DUNKG4 | 119 | 119 | 105.34
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:68&160 | 119 | 119 | 105.33
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:EESR/WF/NWES | 119 | 119 | 105.33
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:34&42 | 119 | 119 | 105.24
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:DKSR/WRFL | 119 | 119 | 105.18
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | WTHRS - MEYER 230 | LN:115:181/922 | 119 | 119 | 105.15
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:EESR/WRFL | 119 | 119 | 105.06
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:40&41 | 119 | 119 | 104.99
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | WTHRS - MEYER 230 | 119 | 119 | 104.85
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:MEYER | 119 | 119 | 104.74
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:68&160 | 119 | 119 | 104.68
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:EESR/WF/NWES | 119 | 119 | 104.66
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:34&42 | 119 | 119 | 104.58
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:DKSR/WRFL | 119 | 119 | 104.51
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:EESR/WRFL | 119 | 119 | 104.39
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:EESR/NWES | 119 | 119 | 104.29
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | DUNKIRK - SRIPL 68 230 | 119 | 119 | 104.16
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:SRIPLEY | 119 | 119 | 104.15
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SRIPL - ERIE E 69 230 | 119 | 119 | 104.04
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:EESR/NWES | 119 | 119 | 103.64
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | CANDQUA - STNYRDG 68A 230 | LN:115:181/922 | 119 | 119 | 103.53
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | DUNKIRK - SRIPL 68 230 | 119 | 119 | 103.5
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:SRIPLEY | 119 | 119 | 103.49
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | NIAG - NEWROCH 1 345 | LN:115:181/922 | 119 | 119 | 103.45
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SRIPL - ERIE E 69 230 | 119 | 119 | 103.38
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:904 NY | 119 | 119 | 103.22
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_904 | 119 | 119 | 103.22
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:181/922 | 119 | 119 | 103.08
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | ERIE E - 4 MILE 230 | 119 | 119 | 103.01
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:NIAG345_3108 | 119 | 119 | 103
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | NIAG - NEWROCH 1 345 | 119 | 119 | 102.98
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | CANDQUA - STNYRDG 68A 230 | 119 | 119 | 102.93
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | S:AVOCA | 119 | 119 | 102.93
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:255_345B302 | 119 | 119 | 102.93
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | CANDQUA - STNYRDG 68A 230 | LN:115:181/922 | 119 | 119 | 102.88
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:STONYRIDGE | 119 | 119 | 102.82
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:181/922 | 119 | 119 | 102.74
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:904 NY | LN:115:181/922 | 119 | 119 | 102.7
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_904 | LN:115:181/922 | 119 | 119 | 102.7
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | NIAG - NEWROCH 1 345 | LN:115:181/922 | 119 | 119 | 102.65
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_904 | 119 | 119 | 102.48
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:904 NY | 119 | 119 | 102.48
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:181/922 | 119 | 119 | 102.44
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:NIAG345_3108 | 119 | 119 | 102.38
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | ERIE E - 4 MILE 230 | 119 | 119 | 102.35
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | NIAG - NEWROCH 1 345 | 119 | 119 | 102.34
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:255_345B302 | 119 | 119 | 102.3
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | S:AVOCA | 119 | 119 | 102.28
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | CANDQUA - STNYRDG 68A 230 | 119 | 119 | 102.28
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:181/922 | 119 | 119 | 102.17
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:STONYRIDGE | 119 | 119 | 102.16
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | STONYCR - WTHRS 230 | LN:115:181/922 | 119 | 119 | 102.15
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | STONYCR - WTHRS 230 | 119 | 119 | 102.07
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:904 NY | LN:115:181/922 | 119 | 119 | 102.02
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_904 | LN:115:181/922 | 119 | 119 | 102.02
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:255_345B202 | 119 | 119 | 101.95
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:167 | 119 | 119 | 101.94
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SOMERSET - NEWROCH 1 345 | 119 | 119 | 101.9
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:167 | LN:115:181/922 | 119 | 119 | 101.73
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:181/922 | 119 | 119 | 101.6
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:WTHERS230 | 119 | 119 | 101.55
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | STONYCR - WTHRS 230 | LN:115:181/922 | 119 | 119 | 101.51
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | STONYCR - WTHRS 230 | 119 | 119 | 101.4
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:255_345B202 | 119 | 119 | 101.26
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:167 | 119 | 119 | 101.24
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:COOP345_42-4182 | 119 | 119 | 101.24
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SOMERSET - NEWROCH 1 345 | 119 | 119 | 101.22
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:181/922 | 119 | 119 | 101.07
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:167 | LN:115:181/922 | 119 | 119 | 101.06
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:31&41 | 119 | 119 | 101.05
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:LAPER_345_2 | 119 | 119 | 100.96
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:LAPER_345_1 | 119 | 119 | 100.96
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LFYTE - CLARKCRNS 36A 345 | 119 | 119 | 100.92
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:LAFAYETT | 119 | 119 | 100.9
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:WTHERS230 | 119 | 119 | 100.88
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:LAPER_345_4 | 119 | 119 | 100.78
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:LAPER_345_3 | 119 | 119 | 100.78
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | HILLSIDE 230/115 4TR | LN:115:181/922 | 119 | 119 | 100.73
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:77&76 | 119 | 119 | 100.72
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:OAKD345_B5 | 119 | 119 | 100.71
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | OAKDLE - CLARKCRNS 36B 345 | 119 | 119 | 100.7
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:OAKD345_B6 | 119 | 119 | 100.7
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | MEYER - CANDQUA 60 230 | LN:115:181/922 | 119 | 119 | 100.61
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:COOP345_42-4182 | 119 | 119 | 100.59
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:COOP345_4182 | 119 | 119 | 100.55
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:MP11&41 | 119 | 119 | 100.55
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:MARC345_3208 | 119 | 119 | 100.54
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:MARC345_3202 | 119 | 119 | 100.5
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | MARCY - COOPERS 345 SC | 119 | 119 | 100.45
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:31&41 | 119 | 119 | 100.4
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:EDIC345_R915 | 119 | 119 | 100.37
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | MEYER - CANDQUA 60 230 | 119 | 119 | 100.34
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:LAPER_345_1 | 119 | 119 | 100.32
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:LAPER_345_2 | 119 | 119 | 100.32
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:LAFA_ELB | 119 | 119 | 100.32
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LFYTE - CLARKCRNS 36A 345 | 119 | 119 | 100.29
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | GARDENVILL - DUNKIRK 74 230 | LN:115:181/922 | 119 | 119 | 100.29
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:LAFAYETT | 119 | 119 | 100.26
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | GARDENVILL - DUNKIRK 73 230 | LN:115:181/922 | 119 | 119 | 100.25
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:LAPER_345_4 | 119 | 119 | 100.15
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:LAPER_345_3 | 119 | 119 | 100.15
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | HILLSIDE 230/115 4TR | LN:115:181/922 | 119 | 119 | 100.15
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:OAKD345_B5 | 119 | 119 | 100.07
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | T:77&76 | 119 | 119 | 100.07
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | OAKDLE - CLARKCRNS 36B 345 | 119 | 119 | 100.06
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:OAKD345_B6 | 119 | 119 | 100.06
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:CNDGUA | 119 | 119 | 100.05
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | G:INDEK-OL | LN:115:181/922 | 119 | 119 | 100.01
| 130795 DEPEW115 115 130799 ERIE 115 115 1 Max |  |  |  |  | 125.4
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 124 | 139 | NConv
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 124 | 139 | NConv
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 124 | 139 | NConv
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 124 | 139 | NConv
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 124 | 139 | NConv
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 124 | 139 | NConv
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 124 | 139 | NConv
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 124 | 139 | NConv
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 124 | 139 | NConv
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 124 | 139 | NConv
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 124 | 139 | NConv
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 124 | 139 | NConv
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 124 | 139 | NConv
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 124 | 139 | 130.93
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 124 | 139 | 126.6
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 124 | 139 | 123.72
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 124 | 139 | 119.15
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:180 | T:77&78 | 124 | 139 | 114.33
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 124 | 139 | 113.5
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:182S | T:77&78 | 124 | 139 | 111.17
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 124 | 139 | 109.11
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 124 | 139 | 108.83
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:180 | T:77&78 | 124 | 139 | 107.81
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:195 | T:77&78 | 124 | 139 | 106.91
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:182N | T:77&78 | 124 | 139 | 106.14
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:191 | T:77&78 | 124 | 139 | 105.78
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 124 | 139 | 105.7
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:192 | T:77&78 | 124 | 139 | 105.62
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 124 | 139 | 105.57
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 124 | 139 | 105.55
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | TB:2/1:PK3 | T:77&78 | 124 | 139 | 105.33
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | FARMVLY - HOMERCTY | T:77&78 | 124 | 139 | 105.26
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 124 | 139 | 105.25
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 124 | 139 | 104.6
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:182S | T:77&78 | 124 | 139 | 104.58
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 124 | 139 | 103.71
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 124 | 139 | 103.2
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 124 | 139 | 103.2
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 124 | 139 | 102.87
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:38 | T:77&78 | 124 | 139 | 102.62
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 124 | 139 | 102.62
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 124 | 139 | 102.14
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:39 | T:77&78 | 124 | 139 | 102.07
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:195 | T:77&78 | 124 | 139 | 101.43
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 124 | 139 | 101.24
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 124 | 139 | 101.01
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 124 | 139 | 100.95
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:191 | T:77&78 | 124 | 139 | 100.76
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:192 | T:77&78 | 124 | 139 | 100.66
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 124 | 139 | 100.39
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | LN:115:182N | T:77&78 | 124 | 139 | 100.33
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 124 | 139 | 100.2
Dispatch 1 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | FARMVLY - HOMERCTY | T:77&78 | 124 | 139 | 100
| 130799 ERIE 115 115 130834 N.BRW115 115 1 Max |  |  |  |  | 130.93
Dispatch 1 | 130806 GARDV115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 1 | 130806 GARDV115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 139 | 163 | NConv
Dispatch 1 | 130806 GARDV115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 139 | 163 | NConv
Dispatch 1 | 130806 GARDV115 115 131467 LANGN115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 1 | 130806 GARDV115 115 131467 LANGN115 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 139 | 163 | NConv
Dispatch 2 | 130806 GARDV115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 2 | 130806 GARDV115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 139 | 163 | NConv
Dispatch 2 | 130806 GARDV115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 139 | 163 | NConv
Dispatch 2 | 130806 GARDV115 115 131467 LANGN115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 2 | 130806 GARDV115 115 131467 LANGN115 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 139 | 163 | NConv
| 130806 GARDV115 115 131467 LANGN115 115 1 Max |  |  |  |  | 0
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 238 | 287 | NConv
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 238 | 287 | NConv
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 238 | 287 | NConv
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 238 | 287 | NConv
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 238 | 287 | NConv
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 238 | 287 | NConv
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 238 | 287 | NConv
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 238 | 287 | NConv
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 238 | 287 | NConv
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 238 | 287 | NConv
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 238 | 287 | 116.11
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 238 | 287 | 116.03
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 238 | 287 | 115.54
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 238 | 287 | 114.34
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | WTHRS - MEYER 230 | SB:GARD230_T7-12 | 238 | 287 | 113.4
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 238 | 287 | 112.56
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | B:MEYER | 238 | 287 | 111.72
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | WTHRS - MEYER 230 | 238 | 287 | 111.68
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 238 | 287 | 107.01
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 238 | 287 | 106.98
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 238 | 287 | 106.13
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 238 | 287 | 105.69
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | B:STOLE230 | 238 | 287 | 105.38
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | ROBINSON - STOLLRD 65 230 | 238 | 287 | 105.32
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 238 | 287 | 104.37
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | ROBINSON - STOLLRD 65 230 | Base Case | 238 | 287 | 103.94
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 238 | 287 | 103.94
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STONYCR - WTHRS 230 | SB:GARD230_T7-12 | 238 | 287 | 103.43
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | WTHRS - MEYER 230 | SB:GARD230_T7-12 | 238 | 287 | 103.43
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 238 | 287 | 103.35
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 238 | 287 | 103.26
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 238 | 287 | 102.65
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STONYCR - WTHRS 230 | STOLLRD - GARDENVILL 66 230 | 238 | 287 | 102.6
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | SB:WTHERS230 | 238 | 287 | 102.54
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | ROBINSON - STOLLRD 65 230 | SB:255_345B302 | 238 | 287 | 102.2
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | ROBINSON - STOLLRD 65 230 | 238 | 287 | 102.07
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | STONYCR - WTHRS 230 | 238 | 287 | 102.07
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | B:STOLE230 | 238 | 287 | 102.06
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | ROBINSON - STOLLRD 65 230 | SB:NIAG345_3108 | 238 | 287 | 101.94
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | ROBINSON - STOLLRD 65 230 | NIAG - NEWROCH 1 345 | 238 | 287 | 101.84
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | B:MEYER | 238 | 287 | 101.74
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | WTHRS - MEYER 230 | 238 | 287 | 101.69
| 130815 HINMN115 115 131611 HARIS115 115 1 Max |  |  |  |  | 116.11
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 220 | 252 | NConv
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 220 | 252 | NConv
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 220 | 252 | NConv
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 220 | 252 | NConv
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 220 | 252 | NConv
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 220 | 252 | NConv
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 220 | 252 | NConv
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 220 | 252 | NConv
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 220 | 252 | NConv
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 220 | 252 | NConv
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 220 | 252 | 117.6
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 220 | 252 | 117.48
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 220 | 252 | 117.11
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | WTHRS - MEYER 230 | SB:GARD230_T7-12 | 220 | 252 | 116.93
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 220 | 252 | 115.95
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STOLLRD - GARDENVILL 66 230 | B:MEYER | 220 | 252 | 114.97
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STOLLRD - GARDENVILL 66 230 | WTHRS - MEYER 230 | 220 | 252 | 114.92
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 220 | 252 | 114.53
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 220 | 252 | 107.29
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | B:STOLE230 | 220 | 252 | 107
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | ROBINSON - STOLLRD 65 230 | 220 | 252 | 106.92
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 220 | 252 | 106.41
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 220 | 252 | 106.34
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 220 | 252 | 105.75
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | WTHRS - MEYER 230 | SB:GARD230_T7-12 | 220 | 252 | 105.05
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STONYCR - WTHRS 230 | SB:GARD230_T7-12 | 220 | 252 | 105.02
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 220 | 252 | 104.44
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 220 | 252 | 104.19
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STONYCR - WTHRS 230 | STOLLRD - GARDENVILL 66 230 | 220 | 252 | 104.04
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STOLLRD - GARDENVILL 66 230 | SB:WTHERS230 | 220 | 252 | 103.96
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 220 | 252 | 103.89
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 220 | 252 | 103.79
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STOLLRD - GARDENVILL 66 230 | STONYCR - WTHRS 230 | 220 | 252 | 103.43
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | ROBINSON - STOLLRD 65 230 | SB:255_345B302 | 220 | 252 | 103.27
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | SOMERSET - NEWROCH 1 345 | ROBINSON - STOLLRD 65 230 | 220 | 252 | 103.16
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STOLLRD - GARDENVILL 66 230 | B:MEYER | 220 | 252 | 103.15
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | SOMERSET - NEWROCH 1 345 | B:STOLE230 | 220 | 252 | 103.13
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STOLLRD - GARDENVILL 66 230 | WTHRS - MEYER 230 | 220 | 252 | 103.1
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | ROBINSON - STOLLRD 65 230 | SB:NIAG345_3108 | 220 | 252 | 102.98
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | ROBINSON - STOLLRD 65 230 | NIAG - NEWROCH 1 345 | 220 | 252 | 102.86
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 220 | 252 | 102.81
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | ROBINSON - STOLLRD 65 230 | SB:255_345B202 | 220 | 252 | 100.38
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | ROBINSON - STOLLRD 65 230 | SOMERSET - NEWROCH 1 345 | 220 | 252 | 100.28
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 220 | 252 | 100.01
| 130815 HINMN115 115 135452 LOCKPORT 115 1 Max |  |  |  |  | 117.6
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 139 | 163 | NConv
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 139 | 163 | NConv
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 139 | 163 | NConv
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 139 | 163 | NConv
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 139 | 163 | NConv
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 139 | 163 | NConv
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 139 | 163 | NConv
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 139 | 163 | NConv
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 139 | 163 | 142.05
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 139 | 163 | 139.06
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 139 | 163 | 131.46
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 139 | 163 | 127.23
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:180 | T:77&78 | 139 | 163 | 122.71
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 139 | 163 | 121.95
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 139 | 163 | 118.26
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:182S | T:77&78 | 139 | 163 | 117.99
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 139 | 163 | 117.82
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:180 | T:77&78 | 139 | 163 | 116.96
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:195 | T:77&78 | 139 | 163 | 116.47
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 139 | 163 | 116.12
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | FARMVLY - HOMERCTY | T:77&78 | 139 | 163 | 115.55
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 139 | 163 | 115.48
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:191 | T:77&78 | 139 | 163 | 115.46
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 139 | 163 | 115.38
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:192 | T:77&78 | 139 | 163 | 115.32
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 139 | 163 | 115.03
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 139 | 163 | 115.03
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | TB:2/1:PK3 | T:77&78 | 139 | 163 | 114.94
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:182N | T:77&78 | 139 | 163 | 114.81
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 139 | 163 | 114.79
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 139 | 163 | 114.71
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 139 | 163 | 114.67
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 139 | 163 | 113.54
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 139 | 163 | 113.02
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:345:37S-FM-FV | T:77&78 | 139 | 163 | 112.78
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 139 | 163 | 112.61
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 139 | 163 | 112.58
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:38 | T:77&78 | 139 | 163 | 112.35
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 139 | 163 | 112.29
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:182S | T:77&78 | 139 | 163 | 112.14
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:39 | T:77&78 | 139 | 163 | 111.79
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 139 | 163 | 111.57
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:195 | T:77&78 | 139 | 163 | 111.51
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 139 | 163 | 111.34
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 139 | 163 | 111.02
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 139 | 163 | 110.96
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:191 | T:77&78 | 139 | 163 | 110.92
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | FARMVLY - HOMERCTY | T:77&78 | 139 | 163 | 110.84
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:192 | T:77&78 | 139 | 163 | 110.82
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 139 | 163 | 110.56
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 139 | 163 | 110.37
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 139 | 163 | 110.37
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 139 | 163 | 110.1
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 139 | 163 | 110.1
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 139 | 163 | 110.1
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 139 | 163 | 109.73
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:182N | T:77&78 | 139 | 163 | 109.7
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:101 | T:77&78 | 139 | 163 | 109.65
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:102 | T:77&78 | 139 | 163 | 109.43
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:120 | T:77&78 | 139 | 163 | 109.27
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:133 | T:77&78 | 139 | 163 | 108.91
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 139 | 163 | 108.79
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | G:BLISS1 | T:77&78 | 139 | 163 | 108.78
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:130 | T:77&78 | 139 | 163 | 108.69
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | TB:2/1:PK3 | T:77&78 | 139 | 163 | 108.66
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 139 | 163 | 108.64
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | G:INDEK-OL | T:77&78 | 139 | 163 | 108.63
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 139 | 163 | 108.49
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:129 | T:77&78 | 139 | 163 | 108.47
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 139 | 163 | 108.46
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:345:37S-FM-FV | T:77&78 | 139 | 163 | 108.21
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 139 | 163 | 108.2
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 139 | 163 | 108.12
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:705 NY | T:77&78 | 139 | 163 | 108.07
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | First:Lancaster_705 | T:77&78 | 139 | 163 | 108.07
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAG - KINTIGH 345 | T:77&78 | 139 | 163 | 107.82
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:180 | T:79&80 | 139 | 163 | 107.6
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 139 | 163 | 107.51
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 139 | 163 | 107.49
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 139 | 163 | 107.38
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:38 | T:77&78 | 139 | 163 | 107.33
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 139 | 163 | 107.33
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 139 | 163 | 106.88
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 139 | 163 | 106.88
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 139 | 163 | 106.88
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 139 | 163 | 106.88
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:39 | T:77&78 | 139 | 163 | 106.77
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 139 | 163 | 106.29
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 139 | 163 | 105.62
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 139 | 163 | 105.57
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 139 | 163 | 105.57
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 139 | 163 | 105.57
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:101 | T:77&78 | 139 | 163 | 104.45
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:102 | T:77&78 | 139 | 163 | 104.25
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:120 | T:77&78 | 139 | 163 | 104.16
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | G:BLISS1 | T:77&78 | 139 | 163 | 104.03
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:133 | T:77&78 | 139 | 163 | 103.95
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | G:INDEK-OL | T:77&78 | 139 | 163 | 103.86
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:130 | T:77&78 | 139 | 163 | 103.76
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 139 | 163 | 103.75
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 139 | 163 | 103.75
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | TB:2/1:ROB | T:77&78 | 139 | 163 | 103.67
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | STONYCR - WTHRS 230 | T:77&78 | 139 | 163 | 103.66
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 139 | 163 | 103.61
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:129 | T:77&78 | 139 | 163 | 103.49
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 139 | 163 | 103.45
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:705 NY | T:77&78 | 139 | 163 | 103.23
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | First:Lancaster_705 | T:77&78 | 139 | 163 | 103.23
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAG - KINTIGH 345 | T:77&78 | 139 | 163 | 103.18
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:100 | T:77&78 | 139 | 163 | 103.16
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | G:GINNA | T:77&78 | 139 | 163 | 103.09
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | GEN:115:GINNA | T:77&78 | 139 | 163 | 103.07
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 139 | 163 | 103.06
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 139 | 163 | 102.99
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:195 | T:79&80 | 139 | 163 | 102.89
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 139 | 163 | 102.78
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 139 | 163 | 102.77
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:908 NY | T:77&78 | 139 | 163 | 102.73
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 139 | 163 | 102.69
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 139 | 163 | 102.6
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 139 | 163 | 102.58
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 139 | 163 | 102.43
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 139 | 163 | 102.4
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 139 | 163 | 102.37
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | R:HC-FV_37&W-F_171 | T:79&80 | 139 | 163 | 102.34
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 139 | 163 | 102.26
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | First:Lancaster_926B | T:77&78 | 139 | 163 | 102.19
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 139 | 163 | 102.18
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 139 | 163 | 102.18
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 139 | 163 | 102.18
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 139 | 163 | 102.18
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | FARMVLY - HOMERCTY | T:79&80 | 139 | 163 | 102.05
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 139 | 163 | 101.88
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:191 | T:79&80 | 139 | 163 | 101.87
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | TB:2/1:PK3 | T:79&80 | 139 | 163 | 101.86
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:180 | T:79&80 | 139 | 163 | 101.76
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:192 | T:79&80 | 139 | 163 | 101.73
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | WTHRS - MEYER 230 | T:77&78 | 139 | 163 | 101.64
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 139 | 163 | 101.56
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:182S | T:79&80 | 139 | 163 | 101.53
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | TB:3/2:FV | T:77&78 | 139 | 163 | 101.41
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | FARMVLY - FARMVLY | T:77&78 | 139 | 163 | 101.41
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:926 NY | T:77&78 | 139 | 163 | 101.33
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | CAP:115:GV1 | T:77&78 | 139 | 163 | 101.3
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | CAP:115:GV2 | T:77&78 | 139 | 163 | 101.3
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 139 | 163 | 101.14
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | GEN:345:SOMERSET | T:77&78 | 139 | 163 | 101.11
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | GEN:KINTIGH | T:77&78 | 139 | 163 | 101.11
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 139 | 163 | 101.1
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 139 | 163 | 100.95
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LN:115:182N | T:79&80 | 139 | 163 | 100.94
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 139 | 163 | 100.3
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 139 | 163 | 100.26
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 139 | 163 | 100.23
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 139 | 163 | 100.15
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 139 | 163 | 100.09
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 139 | 163 | 100.04
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 139 | 163 | 100.01
| 130834 N.BRW115 115 135437 CLSP-181 115 1 Max |  |  |  |  | 142.05
Dispatch 1 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 215 | 247 | NConv
Dispatch 1 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 215 | 247 | NConv
Dispatch 1 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 215 | 247 | NConv
Dispatch 1 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 215 | 247 | NConv
Dispatch 1 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 215 | 247 | NConv
Dispatch 2 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 215 | 247 | NConv
Dispatch 2 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 215 | 247 | NConv
Dispatch 2 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 215 | 247 | NConv
Dispatch 2 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 215 | 247 | NConv
Dispatch 2 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 215 | 247 | NConv
| 130846 ROBIN115 115 130853 A.LUD TP 115 1 Max |  |  |  |  | 0
Dispatch 1 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 215 | 247 | NConv
Dispatch 1 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 215 | 247 | NConv
Dispatch 1 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 215 | 247 | NConv
Dispatch 1 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 215 | 247 | NConv
Dispatch 1 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 215 | 247 | NConv
Dispatch 2 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 215 | 247 | NConv
Dispatch 2 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 215 | 247 | NConv
Dispatch 2 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 215 | 247 | NConv
Dispatch 2 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 215 | 247 | NConv
Dispatch 2 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 215 | 247 | NConv
| 130853 A.LUD TP 115 131611 HARIS115 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 444 | 444 | NConv
Dispatch 1 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 444 | 444 | NConv
Dispatch 1 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 444 | 444 | NConv
Dispatch 1 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 444 | 444 | NConv
Dispatch 1 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 444 | 444 | NConv
Dispatch 1 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | HILLSIDE 230/115 4TR | B:MEYER | 444 | 444 | NConv
Dispatch 2 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 444 | 444 | NConv
Dispatch 2 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 444 | 444 | NConv
Dispatch 2 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 444 | 444 | NConv
Dispatch 2 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 444 | 444 | NConv
Dispatch 2 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 444 | 444 | NConv
Dispatch 2 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | HILLSIDE 230/115 4TR | B:MEYER | 444 | 444 | NConv
| 135250 DUNKIRK 230 135251 S RIPLEY 230 1 Max |  |  |  |  | 0
Dispatch 1 | 135253 S224-36 115 135256 S214-36 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 1 | 135253 S224-36 115 135256 S214-36 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 1 | 135253 S224-36 115 135256 S214-36 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 1 | 135253 S224-36 115 135256 S214-36 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 1 | 135253 S224-36 115 135256 S214-36 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135253 S224-36 115 135256 S214-36 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 2 | 135253 S224-36 115 135256 S214-36 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135253 S224-36 115 135256 S214-36 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135253 S224-36 115 135256 S214-36 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
| 135253 S224-36 115 135256 S214-36 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 148 | 148 | NConv
Dispatch 1 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 148 | 148 | NConv
Dispatch 1 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 148 | 148 | NConv
Dispatch 1 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 148 | 148 | NConv
Dispatch 1 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 148 | 148 | NConv
Dispatch 2 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 148 | 148 | NConv
Dispatch 2 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 148 | 148 | NConv
Dispatch 2 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 148 | 148 | NConv
Dispatch 2 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 148 | 148 | NConv
Dispatch 2 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 148 | 148 | NConv
| 135254 S224-37 115 135451 HUNTLEY1 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 168 | 176 | NConv
Dispatch 1 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 176 | NConv
Dispatch 1 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 168 | 176 | NConv
Dispatch 1 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 168 | 176 | NConv
Dispatch 1 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 176 | NConv
Dispatch 2 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 168 | 176 | NConv
Dispatch 2 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 176 | NConv
Dispatch 2 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 168 | 176 | NConv
Dispatch 2 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 168 | 176 | NConv
Dispatch 2 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 176 | NConv
| 135256 S214-36 115 135451 HUNTLEY1 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 1 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 1 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 2 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 2 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 109.85
Dispatch 1 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 109.08
Dispatch 2 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | LN:115:142 | SB:DUNK230_R1312 | 88 | 101 | 107.81
Dispatch 1 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | LN:115:142 | SB:DUNK230_R1312 | 88 | 101 | 107.35
Dispatch 2 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 102.83
Dispatch 1 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 102.2
Dispatch 2 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 101.69
Dispatch 2 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 101.69
Dispatch 1 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 101.04
Dispatch 1 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 101.04
| 135268 CLVB-141 115 135292 SHALTNTP 115 1 Max |  |  |  |  | 109.85
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 120.51
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 119.75
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | LN:115:142 | SB:DUNK230_R1312 | 88 | 101 | 119.57
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | LN:115:142 | SB:DUNK230_R1312 | 88 | 101 | 119.1
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 108.06
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 107.43
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 106.94
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 106.94
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 106.3
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 106.3
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 104.6
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 103.99
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 103.85
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 101 | 103.27
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 103.21
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | LFYTE - CLARKCRNS 36A 345 | T:73&74 | 88 | 101 | 102.85
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:73&74 | 88 | 101 | 102.76
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 101 | 102.61
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | LFYTE - CLARKCRNS 36A 345 | T:73&74 | 88 | 101 | 102.26
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:73&74 | 88 | 101 | 102.18
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | LN:345:37S-FM-FV-HC | T:73&74 | 88 | 101 | 102.09
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | MEYER - CANDQUA 60 230 | T:73&74 | 88 | 101 | 101.25
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | HILLSIDE 230/115 4TR | T:73&74 | 88 | 101 | 101.17
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | LN:345:37S-FM-FV-HC | T:73&74 | 88 | 101 | 101.05
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | T:73&74 | 88 | 101 | 100.87
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | MEYER - CANDQUA 60 230 | T:73&74 | 88 | 101 | 100.63
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | LN:115:167 | T:73&74 | 88 | 101 | 100.62
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | HILLSIDE 230/115 4TR | T:73&74 | 88 | 101 | 100.6
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | 4 MILE - ERIE SE 230 | T:73&74 | 88 | 101 | 100.45
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | T:73&74 | 88 | 101 | 100.44
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | SHLDON - STONYCR 230 | T:73&74 | 88 | 101 | 100.43
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | G:JAMESGN7 | T:73&74 | 88 | 101 | 100.31
| 135268 CLVB-141 115 135483 S55-141 115 1 Max |  |  |  |  | 120.51
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LN:115:141 | T:73&74 | 88 | 101 | 122.26
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LN:115:141 | T:73&74 | 88 | 101 | 121.48
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LN:115:141 | SB:DUNK230_R1312 | 88 | 101 | 121.08
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LN:115:141 | SB:DUNK230_R1312 | 88 | 101 | 120.6
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 110.38
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 109.73
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 109.35
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 109.35
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 108.68
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 108.68
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 106.84
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 106.21
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 106.07
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 101 | 105.46
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 105.41
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LFYTE - CLARKCRNS 36A 345 | T:73&74 | 88 | 101 | 105.04
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:73&74 | 88 | 101 | 104.95
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 101 | 104.78
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LFYTE - CLARKCRNS 36A 345 | T:73&74 | 88 | 101 | 104.43
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:73&74 | 88 | 101 | 104.35
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LN:345:37S-FM-FV-HC | T:73&74 | 88 | 101 | 104.15
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | MEYER - CANDQUA 60 230 | T:73&74 | 88 | 101 | 103.39
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | HILLSIDE 230/115 4TR | T:73&74 | 88 | 101 | 103.31
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LN:345:37S-FM-FV-HC | T:73&74 | 88 | 101 | 103.09
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | SOMERSET - NEWROCH 1 345 | T:73&74 | 88 | 101 | 103
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | MEYER - CANDQUA 60 230 | T:73&74 | 88 | 101 | 102.76
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | HILLSIDE 230/115 4TR | T:73&74 | 88 | 101 | 102.73
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | 4 MILE - ERIE SE 230 | T:73&74 | 88 | 101 | 102.64
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LN:115:167 | T:73&74 | 88 | 101 | 102.59
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | SOMERSET - NEWROCH 1 345 | T:73&74 | 88 | 101 | 102.56
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | SHLDON - STONYCR 230 | T:73&74 | 88 | 101 | 102.56
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | G:JAMESGN7 | T:73&74 | 88 | 101 | 102.46
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | 4 MILE - ERIE SE 230 | T:73&74 | 88 | 101 | 102.07
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LN:115:167 | T:73&74 | 88 | 101 | 101.93
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | SHLDON - STONYCR 230 | T:73&74 | 88 | 101 | 101.9
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | G:JAMESGN7 | T:73&74 | 88 | 101 | 101.83
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | STNYRDG - HILLSIDE 68B 230 | T:73&74 | 88 | 101 | 101.37
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LN:115:153 | T:73&74 | 88 | 101 | 100.91
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | STNYRDG - HILLSIDE 68B 230 | T:73&74 | 88 | 101 | 100.74
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | R:5M-SR_37&W-F_171 | T:73&74 | 88 | 101 | 100.73
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LN:115:154 | T:73&74 | 88 | 101 | 100.63
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | First:Lancaster_STOL_HOMER_345 | T:73&74 | 88 | 101 | 100.28
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | 5 MILE - STOLLE 37A 345 | T:73&74 | 88 | 101 | 100.28
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LN:115:153 | T:73&74 | 88 | 101 | 100.27
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | HOMERCTY - STOLLRD 37 345 | T:73&74 | 88 | 101 | 100.27
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | G:INDEK-OL | T:73&74 | 88 | 101 | 100.2
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | LN:115:705 NY | T:73&74 | 88 | 101 | 100.09
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | First:Lancaster_705 | T:73&74 | 88 | 101 | 100.09
| 135269 CLVB-142 115 135445 FORD-142 115 1 Max |  |  |  |  | 122.26
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | LN:115:141 | T:73&74 | 88 | 101 | 111.49
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | LN:115:141 | T:73&74 | 88 | 101 | 110.71
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | LN:115:141 | SB:DUNK230_R1312 | 88 | 101 | 109.28
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | LN:115:141 | SB:DUNK230_R1312 | 88 | 101 | 108.8
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 104.97
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 104.32
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 103.92
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 103.92
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 103.25
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 103.25
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 101.44
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 100.82
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 100.68
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 101 | 100.08
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 100.03
| 135269 CLVB-142 115 135569 LAKEVIEW 115 1 Max |  |  |  |  | 111.49
Dispatch 2 | 135270 DELMTR-1 115 135287 NANG-141 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 101.77
Dispatch 1 | 135270 DELMTR-1 115 135287 NANG-141 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 101
| 135270 DELMTR-1 115 135287 NANG-141 115 1 Max |  |  |  |  | 101.77
Dispatch 2 | 135270 DELMTR-1 115 135579 LAKEV141 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 101.88
Dispatch 1 | 135270 DELMTR-1 115 135579 LAKEV141 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 101.11
| 135270 DELMTR-1 115 135579 LAKEV141 115 1 Max |  |  |  |  | 101.88
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | LN:115:141 | T:73&74 | 88 | 101 | 111.43
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | LN:115:141 | T:73&74 | 88 | 101 | 110.65
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | LN:115:141 | SB:DUNK230_R1312 | 88 | 101 | 109.27
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | LN:115:141 | SB:DUNK230_R1312 | 88 | 101 | 108.78
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 104.91
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 104.26
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 103.86
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 103.86
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 103.2
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 103.2
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 101.38
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 100.76
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 100.62
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 101 | 100.01
| 135271 DLTR-142 115 135569 LAKEVIEW 115 1 Max |  |  |  |  | 111.43
Dispatch 2 | 135277 FALCONER 115 200579 26WARREN 115 1 | SRIPL - ERIE E 69 230 | SIN:90 | 116 | 116 | 113.56
Dispatch 2 | 135277 FALCONER 115 200579 26WARREN 115 1 | DUNKIRK - SRIPL 68 230 | SIN:90 | 116 | 116 | 113.47
Dispatch 1 | 135277 FALCONER 115 200579 26WARREN 115 1 | SRIPL - ERIE E 69 230 | SIN:90 | 116 | 116 | 113.01
Dispatch 1 | 135277 FALCONER 115 200579 26WARREN 115 1 | DUNKIRK - SRIPL 68 230 | SIN:90 | 116 | 116 | 112.93
Dispatch 2 | 135277 FALCONER 115 200579 26WARREN 115 1 | ERIE E - 4 MILE 230 | SIN:90 | 116 | 116 | 107.17
Dispatch 1 | 135277 FALCONER 115 200579 26WARREN 115 1 | ERIE E - 4 MILE 230 | SIN:90 | 116 | 116 | 106.88
Dispatch 2 | 135277 FALCONER 115 200579 26WARREN 115 1 | 4MILE 230/115 1TR | SIN:90 | 116 | 116 | 103.7
Dispatch 1 | 135277 FALCONER 115 200579 26WARREN 115 1 | 4MILE 230/115 1TR | SIN:90 | 116 | 116 | 103.43
| 135277 FALCONER 115 200579 26WARREN 115 1 Max |  |  |  |  | 113.56
Dispatch 1 | 135284 MCHS-151 115 135401 GERNATT 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 129 | 148 | NConv
Dispatch 1 | 135284 MCHS-151 115 135401 GERNATT 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 129 | 148 | NConv
Dispatch 1 | 135284 MCHS-151 115 135401 GERNATT 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 129 | 148 | NConv
Dispatch 1 | 135284 MCHS-151 115 135401 GERNATT 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 129 | 148 | NConv
Dispatch 1 | 135284 MCHS-151 115 135401 GERNATT 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 129 | 148 | NConv
Dispatch 2 | 135284 MCHS-151 115 135401 GERNATT 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 129 | 148 | NConv
Dispatch 2 | 135284 MCHS-151 115 135401 GERNATT 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 129 | 148 | NConv
Dispatch 2 | 135284 MCHS-151 115 135401 GERNATT 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 129 | 148 | NConv
Dispatch 2 | 135284 MCHS-151 115 135401 GERNATT 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 129 | 148 | NConv
Dispatch 2 | 135284 MCHS-151 115 135401 GERNATT 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 129 | 148 | NConv
| 135284 MCHS-151 115 135401 GERNATT 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 1 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 1 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 2 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 2 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 108.8
Dispatch 1 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 108.03
Dispatch 2 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | LN:115:142 | SB:DUNK230_R1312 | 88 | 101 | 106.67
Dispatch 1 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | LN:115:142 | SB:DUNK230_R1312 | 88 | 101 | 106.19
Dispatch 2 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 102.08
Dispatch 1 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 101.44
Dispatch 2 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 101.06
Dispatch 2 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 101.06
Dispatch 1 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 100.41
Dispatch 1 | 135292 SHALTNTP 115 135579 LAKEV141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 100.41
| 135292 SHALTNTP 115 135579 LAKEV141 115 1 Max |  |  |  |  | 108.8
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | T:67&37A | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:SHLDN230 | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | T:67&37A | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | T:67&37A | 566 | 654 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 566 | 654 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | T:67&37A | 566 | 654 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3230 | 566 | 654 | 116.15
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3230 | 566 | 654 | 113.95
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 566 | 654 | 113.87
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 566 | 654 | 113.2
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 112.32
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 112.12
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL78 | 566 | 654 | 112.12
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3230 | 566 | 654 | 112.09
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 345 | 566 | 654 | 111.9
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 566 | 654 | 111.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 111.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_T7-12 | 566 | 654 | 110.4
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 109.89
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 566 | 654 | 109.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 109.74
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 566 | 654 | 109.71
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3230 | 566 | 654 | 108.36
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | Base Case | 566 | 654 | 108.18
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 566 | 654 | 107.89
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3230 | 566 | 654 | 107.6
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 566 | 654 | 107.58
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3230 | 566 | 654 | 107.08
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 106.72
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 106.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 566 | 654 | 106.06
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3230 | 566 | 654 | 105.74
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 105.63
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL78 | 566 | 654 | 105.63
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 345 | 566 | 654 | 105.45
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_T7-12 | 566 | 654 | 105.05
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3230 | 566 | 654 | 104.75
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 104.46
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 566 | 654 | 104.34
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 104.34
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 104.18
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 566 | 654 | 104.18
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | TB:2/1:NI1 | SB:PA230_R3230 | 566 | 654 | 103.91
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAGARA 230/115 1TR | SB:PA230_R3230 | 566 | 654 | 103.91
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 566 | 654 | 103.67
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B302 | 566 | 654 | 103
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAG345_3108 | 566 | 654 | 102.98
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - NEWROCH 1 345 | 566 | 654 | 102.92
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | Base Case | 566 | 654 | 102.65
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 566 | 654 | 102.1
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 566 | 654 | 102.1
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B202 | 566 | 654 | 101.57
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | SOMERSET - NEWROCH 1 345 | 566 | 654 | 101.51
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3230 | 566 | 654 | 101.29
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 116.15
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | T:67&37A | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | SB:SHLDN230 | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE 230/115 4TR | T:67&37A | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE 230/115 4TR | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | T:67&37A | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | SB:SHLDN230 | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE 230/115 4TR | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE 230/115 4TR | T:67&37A | 566 | 654 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL77 | 566 | 654 | 120.45
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 566 | 654 | 119.7
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 566 | 654 | 118.07
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 566 | 654 | 114.26
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL77 | 566 | 654 | 113.96
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 566 | 654 | 113.81
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 566 | 654 | 113.14
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 566 | 654 | 112.65
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 566 | 654 | 112.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 112.26
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 112.08
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 345 | 566 | 654 | 111.84
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 111.3
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 566 | 654 | 110.54
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_T7-12 | 566 | 654 | 110.33
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 109.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 109.69
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:61&64 | 566 | 654 | 109.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3430 | 566 | 654 | 109.18
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | Base Case | 566 | 654 | 108.12
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | T:77&80 | 566 | 654 | 107.95
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3430 | 566 | 654 | 107.92
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 566 | 654 | 107.9
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 566 | 654 | 107.83
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 345 | T:77&80 | 566 | 654 | 107.77
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 566 | 654 | 107.51
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 566 | 654 | 106.65
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3430 | 566 | 654 | 106.56
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL77 | 566 | 654 | 106.41
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | T:77&80 | 566 | 654 | 106.11
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:182N | S:PA_HNTL77 | 566 | 654 | 106.1
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 106.01
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | TB:2/1:NI1 | S:PA_HNTL77 | 566 | 654 | 105.86
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA 230/115 1TR | S:PA_HNTL77 | 566 | 654 | 105.86
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:180 | S:PA_HNTL77 | 566 | 654 | 105.75
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:181/922 | S:PA_HNTL77 | 566 | 654 | 105.7
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL77 | 566 | 654 | 105.7
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 105.58
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 566 | 654 | 105.47
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 345 | 566 | 654 | 105.4
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:182S | S:PA_HNTL77 | 566 | 654 | 104.99
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:GARD230_T7-12 | 566 | 654 | 104.98
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | PACKARD 230/115 3TR | S:PA_HNTL77 | 566 | 654 | 104.86
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:133 | S:PA_HNTL77 | 566 | 654 | 104.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 566 | 654 | 104.39
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 104.29
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:130 | S:PA_HNTL77 | 566 | 654 | 104.26
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 104.14
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:129 | S:PA_HNTL77 | 566 | 654 | 103.96
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | T:61&64 | 566 | 654 | 103.61
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-FV_37&W-F_171 | S:PA_HNTL77 | 566 | 654 | 103.47
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | T:77&80 | 566 | 654 | 103.47
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - HOMERCTY | S:PA_HNTL77 | 566 | 654 | 103.43
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:38 | S:PA_HNTL77 | 566 | 654 | 103.39
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - KINTIGH 345 | S:PA_HNTL77 | 566 | 654 | 103.39
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:39 | S:PA_HNTL77 | 566 | 654 | 103.24
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | First:Lancaster_GRDN_GRDN_230 | S:PA_HNTL77 | 566 | 654 | 103.15
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:255_345B302 | 566 | 654 | 102.95
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS1 | S:PA_HNTL77 | 566 | 654 | 102.95
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:NIAG345_3108 | 566 | 654 | 102.93
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | NIAG - NEWROCH 1 345 | 566 | 654 | 102.88
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 345 | T:77&80 | 566 | 654 | 102.62
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:INDEK-OL | S:PA_HNTL77 | 566 | 654 | 102.6
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | Base Case | 566 | 654 | 102.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:345:37S-FM-FV-HC | S:PA_HNTL77 | 566 | 654 | 102.48
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | First:Lancaster_922 | S:PA_HNTL77 | 566 | 654 | 102.4
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3430 | 566 | 654 | 102.18
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3430 | 566 | 654 | 102.14
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:JAMESGN7 | S:PA_HNTL77 | 566 | 654 | 102.1
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 566 | 654 | 102.06
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:4 | S:PA_HNTL77 | 566 | 654 | 101.96
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:969 | S:PA_HNTL77 | 566 | 654 | 101.96
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CLAY - DEW 13 345 | S:PA_HNTL77 | 566 | 654 | 101.94
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R3430 | 566 | 654 | 101.86
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:HC-SR_37&W-F_171 | S:PA_HNTL77 | 566 | 654 | 101.82
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | R:FV-5M_37&W-F_171 | S:PA_HNTL77 | 566 | 654 | 101.82
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:182N | S:PA_HNTL77 | 566 | 654 | 101.74
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | T:77&80 | 566 | 654 | 101.73
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:8 | S:PA_HNTL77 | 566 | 654 | 101.71
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | FARMVLY - 5MILE 345 | S:PA_HNTL77 | 566 | 654 | 101.65
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL77 | 566 | 654 | 101.64
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | G:BLISS2 | S:PA_HNTL77 | 566 | 654 | 101.63
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | DEWITT3 - LAFAYTTE 345 | S:PA_HNTL77 | 566 | 654 | 101.56
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:180 | S:PA_HNTL77 | 566 | 654 | 101.54
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SB:255_345B202 | 566 | 654 | 101.53
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | SOMERSET - NEWROCH 1 345 | 566 | 654 | 101.46
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:181/922 | S:PA_HNTL77 | 566 | 654 | 101.3
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL77 | 566 | 654 | 100.92
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3430 | 566 | 654 | 100.73
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | LN:115:182S | S:PA_HNTL77 | 566 | 654 | 100.7
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | T:77&80 | 566 | 654 | 100.65
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 Max |  |  |  |  | 120.45
Dispatch 1 | 135305 SAWYER80 230 135309 SAWYERB3 230 1 | HUNTLEY - GARDENVILL 79 230 | T:77&78 | 220 | 252 | 105.37
Dispatch 1 | 135305 SAWYER80 230 135309 SAWYERB3 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 220 | 252 | 105.26
Dispatch 2 | 135305 SAWYER80 230 135309 SAWYERB3 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 220 | 252 | 104.7
Dispatch 2 | 135305 SAWYER80 230 135309 SAWYERB3 230 1 | HUNTLEY - GARDENVILL 79 230 | T:77&78 | 220 | 252 | 104.7
| 135305 SAWYER80 230 135309 SAWYERB3 230 1 Max |  |  |  |  | 105.37
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | T:67&37A | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:SHLDN230 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | T:67&37A | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | T:67&37A | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | T:67&37A | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:ROBI230 | 566 | 654 | 101.36
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - GARDENVILL 79 230 | 566 | 654 | 100.46
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 79 230 | B:STOLE230 | 566 | 654 | 100.16
| 135305 SAWYER80 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 101.36
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
| 135305 SAWYER80 230 135419 SUNY-80 230 1 Max |  |  |  |  | 0
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&80 | 220 | 252 | 109.28
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:182N | T:77&80 | 220 | 252 | 109.08
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | CAP:115:DK | T:77&80 | 220 | 252 | 109.07
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | CAP:115:DK | T:77&80 | 220 | 252 | 109.06
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | R:HC-SR_37&W-F_171 | T:77&80 | 220 | 252 | 109.01
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | R:FV-5M_37&W-F_171 | T:77&80 | 220 | 252 | 109.01
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:181/922 | T:77&80 | 220 | 252 | 108.99
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&80 | 220 | 252 | 108.99
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&80 | 220 | 252 | 108.98
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | CAP:115:HUN | T:77&80 | 220 | 252 | 108.97
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:181/922 | T:77&80 | 220 | 252 | 108.97
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | R:HC-SR_37&W-F_171 | T:77&80 | 220 | 252 | 108.93
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | R:FV-5M_37&W-F_171 | T:77&80 | 220 | 252 | 108.93
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | CAP:115:HUN | T:77&80 | 220 | 252 | 108.8
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | ROBINSON - STOLLRD 65 230 | T:77&80 | 220 | 252 | 108.73
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | NIAGARA - ROBINSON 64 345 | T:77&80 | 220 | 252 | 108.69
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | ROBINSON - STOLLRD 65 230 | T:77&80 | 220 | 252 | 108.68
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | NIAGARA - ROBINSON 64 345 | T:77&80 | 220 | 252 | 108.62
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | STOLLRD - GARDENVILL 66 230 | T:77&80 | 220 | 252 | 108.52
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | R:5M-SR_37&W-F_171 | T:77&80 | 220 | 252 | 108.47
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:345:37S-FM-FV-HC | T:77&80 | 220 | 252 | 108.34
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | R:5M-SR_37&W-F_171 | T:77&80 | 220 | 252 | 108.3
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:345:37S-FM-FV | T:77&80 | 220 | 252 | 108.29
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:345:37S-FM-FV-HC | T:77&80 | 220 | 252 | 108.23
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | SOMERSET - NEWROCH 1 345 | T:77&80 | 220 | 252 | 108.18
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | STOLLRD - GARDENVILL 66 230 | T:77&80 | 220 | 252 | 108.17
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | NIAG - NEWROCH 1 345 | T:77&80 | 220 | 252 | 108.13
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | SOMERSET - NEWROCH 1 345 | T:77&80 | 220 | 252 | 108.09
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | NIAG - NEWROCH 1 345 | T:77&80 | 220 | 252 | 108.01
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | First:Lancaster_STOL_HOMER_345 | T:77&80 | 220 | 252 | 107.89
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | 5 MILE - STOLLE 37A 345 | T:77&80 | 220 | 252 | 107.89
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&80 | 220 | 252 | 107.89
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:345:37S-FM-FV | T:77&80 | 220 | 252 | 107.86
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | First:Lancaster_STOL_HOMER_345 | T:77&80 | 220 | 252 | 107.85
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | 5 MILE - STOLLE 37A 345 | T:77&80 | 220 | 252 | 107.85
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | HOMERCTY - STOLLRD 37 345 | T:77&80 | 220 | 252 | 107.85
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&80 | 220 | 252 | 107.66
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:182N | T:77&80 | 220 | 252 | 107.44
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | R:HC-FV_37&W-F_171 | T:77&80 | 220 | 252 | 107.25
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | R:HC-FV_37&W-F_171 | T:77&80 | 220 | 252 | 107.18
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | FARMVLY - 5MILE 345 | T:77&80 | 220 | 252 | 107.04
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:180 | T:77&80 | 220 | 252 | 106.26
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | FARMVLY - 5MILE 345 | T:77&80 | 220 | 252 | 105.7
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | 4 MILE - ERIE SE 230 | T:77&80 | 220 | 252 | 105.69
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | ERIE E - 4 MILE 230 | T:77&80 | 220 | 252 | 105.46
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | ERIE E - 4 MILE 230 | T:77&80 | 220 | 252 | 105.35
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | FARMVLY - HOMERCTY | T:77&80 | 220 | 252 | 105.33
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | GARDENVILL - ELM 71 230 | T:77&80 | 220 | 252 | 105.24
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | CBL:230:72 | T:77&80 | 220 | 252 | 105.23
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | FARMVLY - HOMERCTY | T:77&80 | 220 | 252 | 105.07
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:903 NY | T:77&80 | 220 | 252 | 105.06
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:903 NY | T:77&80 | 220 | 252 | 104.88
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:182S | T:77&80 | 220 | 252 | 104.73
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | HUNTLEY - GARDENVILL 80 230 | T:77&78 | 220 | 252 | 104.6
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 220 | 252 | 104.57
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | HUNTLEY - GARDENVILL 80 230 | T:77&78 | 220 | 252 | 104.51
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | OAKDL - FRASER 32 345 | T:77&80 | 220 | 252 | 100.83
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | G:NIAG. 1 | T:77&80 | 220 | 252 | 100.81
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | G:NIAG. 2 | T:77&80 | 220 | 252 | 100.81
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | G:NIAG. 3 | T:77&80 | 220 | 252 | 100.81
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | SHLDON - STONYCR 230 | T:77&80 | 220 | 252 | 100.68
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | CAP:115:GV1 | T:77&80 | 220 | 252 | 100.52
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | CAP:115:GV2 | T:77&80 | 220 | 252 | 100.52
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:119 | T:77&80 | 220 | 252 | 100.38
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:160 | T:77&80 | 220 | 252 | 100.33
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | G:MODERNLF | T:77&80 | 220 | 252 | 100.32
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | CLAY - VOLNEY 6 345 | T:77&80 | 220 | 252 | 100.27
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | CLAY - INDEPNC 26 345 | T:77&80 | 220 | 252 | 100.27
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | OKDLE 230/115 1TR | T:77&80 | 220 | 252 | 100.27
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:968 NY | T:77&80 | 220 | 252 | 100.26
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | WATERCURE - OAKDALE 71 230 | T:77&80 | 220 | 252 | 100.26
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:155 | T:77&80 | 220 | 252 | 100.25
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | MEYER - CANDQUA 60 230 | T:77&80 | 220 | 252 | 100.25
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:195 | T:77&80 | 220 | 252 | 100.22
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | HUNTLEY - ELM 70 230 | T:77&80 | 220 | 252 | 100.2
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:145 | T:77&80 | 220 | 252 | 100.19
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:191 | T:77&80 | 220 | 252 | 100.16
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:192 | T:77&80 | 220 | 252 | 100.16
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:156 | T:77&80 | 220 | 252 | 100.15
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | TB:3/1:FMR | T:77&80 | 220 | 252 | 100.14
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | 5 MILE 345/115 1TR | T:77&80 | 220 | 252 | 100.14
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | LN:115:54/921 | T:77&80 | 220 | 252 | 100.09
Dispatch 2 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | TB:2/1:PK3 | T:77&80 | 220 | 252 | 100.09
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | OAKDL - FRASER 32 345 | T:77&80 | 220 | 252 | 100.06
Dispatch 1 | 135306 SAWYER79 230 135308 SAWYERB2 230 1 | SHLDON - STONYCR 230 | T:77&80 | 220 | 252 | 100.04
| 135306 SAWYER79 230 135308 SAWYERB2 230 1 Max |  |  |  |  | 109.28
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | T:67&37A | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SB:SHLDN230 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | T:67&37A | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | T:67&37A | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | STOLLRD - SHLDON 67 230 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | T:67&37A | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 345 | S:HNT_GRD80 | 566 | 654 | 105.27
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | S:HNT_GRD80 | 566 | 654 | 103.89
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 345 | SB:GARD230_R873 | 566 | 654 | 103.4
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | S:HNT_GRD80 | 566 | 654 | 102.79
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | SB:GARD230_R873 | 566 | 654 | 101.77
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:ROBI230 | 566 | 654 | 101.43
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | STOLLRD - GARDENVILL 66 230 | T:77&80 | 566 | 654 | 101.07
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | ROBINSON - STOLLRD 65 230 | SB:GARD230_R873 | 566 | 654 | 100.84
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - GARDENVILL 80 230 | 566 | 654 | 100.53
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAGARA - ROBINSON 64 345 | T:77&80 | 566 | 654 | 100.51
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HUNTLEY - GARDENVILL 80 230 | B:STOLE230 | 566 | 654 | 100.23
| 135306 SAWYER79 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 105.27
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
| 135306 SAWYER79 230 135418 SUNY-79 230 1 Max |  |  |  |  | 0
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 129 | 182 | NConv
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 129 | 182 | NConv
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 129 | 182 | NConv
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 129 | 182 | NConv
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 129 | 182 | NConv
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 129 | 182 | NConv
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 129 | 182 | NConv
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 129 | 182 | NConv
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 129 | 182 | NConv
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 129 | 182 | NConv
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | Base Case | 129 | 182 | 121.89
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | Base Case | 129 | 182 | 121.49
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | LN:115:705 NY | 129 | 182 | 104.31
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | First:Lancaster_705 | 129 | 182 | 104.31
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:705 NY | LN:115:181/922 | 129 | 182 | 104.07
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | First:Lancaster_705 | LN:115:181/922 | 129 | 182 | 104.07
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | First:Lancaster_705 | 129 | 182 | 103.83
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | LN:115:705 NY | 129 | 182 | 103.83
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:705 NY | LN:115:181/922 | 129 | 182 | 103.63
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | First:Lancaster_705 | LN:115:181/922 | 129 | 182 | 103.63
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | First:Lancaster_926B | LN:115:181/922 | 129 | 182 | 103.06
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | First:Lancaster_926B | LN:115:181/922 | 129 | 182 | 102.85
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | R:HC-FV_37&W-F_171 | 129 | 182 | 102.39
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | FARMVLY - HOMERCTY | 129 | 182 | 102.25
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | R:HC-FV_37&W-F_171 | 129 | 182 | 102.14
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | FARMVLY - HOMERCTY | 129 | 182 | 102.05
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | First:Lancaster_926B | 129 | 182 | 102
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | First:Lancaster_926B | 129 | 182 | 101.88
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | LN:345:37S-FM-FV-HC | 129 | 182 | 101.72
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | R:5M-SR_37&W-F_171 | 129 | 182 | 101.52
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | LN:345:37S-FM-FV-HC | 129 | 182 | 101.38
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | First:Lancaster_STOL_HOMER_345 | 129 | 182 | 101.34
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | 5 MILE - STOLLE 37A 345 | 129 | 182 | 101.34
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | B:STOLE345 | 129 | 182 | 101.34
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | HOMERCTY - STOLLRD 37 345 | 129 | 182 | 101.34
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | R:5M-SR_37&W-F_171 | 129 | 182 | 101.31
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | SB:5MILE | 129 | 182 | 101.27
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | LN:345:37S-FM-FV | 129 | 182 | 101.27
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | 5 MILE - STOLLE 37A 345 | 129 | 182 | 101.14
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | First:Lancaster_STOL_HOMER_345 | 129 | 182 | 101.14
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | B:STOLE345 | 129 | 182 | 101.14
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | HOMERCTY - STOLLRD 37 345 | 129 | 182 | 101.14
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | S:STOLLE345 | 129 | 182 | 101.02
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | SB:5MILE | 129 | 182 | 100.98
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | LN:345:37S-FM-FV | 129 | 182 | 100.98
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | T:67&37A | 129 | 182 | 100.94
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | R:5M-SR_37&W-F_171 | LN:115:181/922 | 129 | 182 | 100.86
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | S:STOLLE345 | 129 | 182 | 100.77
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:345:37S-FM-FV-HC | LN:115:181/922 | 129 | 182 | 100.75
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | First:Lancaster_STOL_HOMER_345 | LN:115:181/922 | 129 | 182 | 100.71
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | 5 MILE - STOLLE 37A 345 | LN:115:181/922 | 129 | 182 | 100.71
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | HOMERCTY - STOLLRD 37 345 | LN:115:181/922 | 129 | 182 | 100.71
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | T:67&37A | 129 | 182 | 100.7
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:345:37S-FM-FV | LN:115:181/922 | 129 | 182 | 100.53
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | R:HC-FV_37&W-F_171 | LN:115:181/922 | 129 | 182 | 100.33
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | FARMVLY - HOMERCTY | LN:115:181/922 | 129 | 182 | 100.19
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | R:5M-SR_37&W-F_171 | LN:115:181/922 | 129 | 182 | 100.14
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | R:HC-FV_37&W-F_171 | LN:115:181/922 | 129 | 182 | 100.11
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:182S | Base Case | 129 | 182 | 100.09
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:345:37S-FM-FV-HC | LN:115:181/922 | 129 | 182 | 100.03
| 135327 AM.S-54 115 135450 GRDNVL1 115 1 Max |  |  |  |  | 121.89
Dispatch 1 | 135327 AM.S-54 115 135493 LUDWIG 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 187 | 215 | NConv
Dispatch 1 | 135327 AM.S-54 115 135493 LUDWIG 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 187 | 215 | NConv
Dispatch 1 | 135327 AM.S-54 115 135493 LUDWIG 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 187 | 215 | NConv
Dispatch 1 | 135327 AM.S-54 115 135493 LUDWIG 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 187 | 215 | NConv
Dispatch 1 | 135327 AM.S-54 115 135493 LUDWIG 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 187 | 215 | NConv
Dispatch 2 | 135327 AM.S-54 115 135493 LUDWIG 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 187 | 215 | NConv
Dispatch 2 | 135327 AM.S-54 115 135493 LUDWIG 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 187 | 215 | NConv
Dispatch 2 | 135327 AM.S-54 115 135493 LUDWIG 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 187 | 215 | NConv
Dispatch 2 | 135327 AM.S-54 115 135493 LUDWIG 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 187 | 215 | NConv
Dispatch 2 | 135327 AM.S-54 115 135493 LUDWIG 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 187 | 215 | NConv
| 135327 AM.S-54 115 135493 LUDWIG 115 1 Max |  |  |  |  | 0
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 140.49
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 137.16
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 130.08
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 125.69
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 174 | 181 | 118.46
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:180 | T:77&78 | 174 | 181 | 118.37
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | First:Lancaster_922 | T:77&78 | 174 | 181 | 115.11
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 174 | 181 | 114.31
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 113.71
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:180 | T:77&78 | 174 | 181 | 111.7
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:195 | T:77&78 | 174 | 181 | 109.9
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 174 | 181 | 109.73
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 109.68
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | First:Lancaster_922 | T:77&78 | 174 | 181 | 108.71
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:191 | T:77&78 | 174 | 181 | 108.69
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:192 | T:77&78 | 174 | 181 | 108.53
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | TB:2/1:PK3 | T:77&78 | 174 | 181 | 108.19
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 107.99
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:181/922 | T:77&78 | 174 | 181 | 107.53
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 174 | 181 | 106.26
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:38 | T:77&78 | 174 | 181 | 105.36
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 174 | 181 | 105.25
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 105.17
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 174 | 181 | 104.82
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 174 | 181 | 104.56
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:195 | T:77&78 | 174 | 181 | 104.36
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.9
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 174 | 181 | 103.84
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:191 | T:77&78 | 174 | 181 | 103.62
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:192 | T:77&78 | 174 | 181 | 103.49
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 174 | 181 | 103.07
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 181 | 102.29
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 174 | 181 | 102.28
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:101 | T:77&78 | 174 | 181 | 101.81
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | FARMVLY - HOMERCTY | T:77&78 | 174 | 181 | 101.81
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 181 | 101.7
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 181 | 101.7
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:102 | T:77&78 | 174 | 181 | 101.54
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:181/922 | T:77&78 | 174 | 181 | 101.43
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:133 | T:77&78 | 174 | 181 | 101.37
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:120 | T:77&78 | 174 | 181 | 101.35
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:130 | T:77&78 | 174 | 181 | 101.21
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | TB:2/1:PK3 | T:77&78 | 174 | 181 | 101.14
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:115:129 | T:77&78 | 174 | 181 | 100.88
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 174 | 181 | 100.83
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | LN:345:37S-FM-FV | T:77&78 | 174 | 181 | 100.53
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | G:BLISS1 | T:77&78 | 174 | 181 | 100.36
Dispatch 1 | 135383 S219-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 174 | 181 | 100.3
Dispatch 2 | 135383 S219-182 115 135496 YNG-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 181 | 100.13
| 135383 S219-182 115 135496 YNG-182 115 1 Max |  |  |  |  | 140.49
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 168 | 181 | NConv
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 168 | 181 | NConv
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 168 | 181 | NConv
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 181 | 139.5
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 181 | 136.02
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 181 | 129.38
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 181 | 125
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 168 | 181 | 117.78
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:180 | T:77&78 | 168 | 181 | 117.7
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | First:Lancaster_922 | T:77&78 | 168 | 181 | 114.45
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 168 | 181 | 113.64
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 113.02
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:180 | T:77&78 | 168 | 181 | 111.04
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:195 | T:77&78 | 168 | 181 | 109.23
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 168 | 181 | 109.04
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 108.99
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | First:Lancaster_922 | T:77&78 | 168 | 181 | 108.06
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:191 | T:77&78 | 168 | 181 | 108.03
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:192 | T:77&78 | 168 | 181 | 107.86
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | TB:2/1:PK3 | T:77&78 | 168 | 181 | 107.52
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 107.32
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:181/922 | T:77&78 | 168 | 181 | 106.9
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 168 | 181 | 105.57
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:38 | T:77&78 | 168 | 181 | 104.7
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 168 | 181 | 104.55
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:39 | T:77&78 | 168 | 181 | 104.51
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 168 | 181 | 104.14
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 168 | 181 | 103.88
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:195 | T:77&78 | 168 | 181 | 103.69
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.24
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 168 | 181 | 103.16
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:191 | T:77&78 | 168 | 181 | 102.96
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:192 | T:77&78 | 168 | 181 | 102.83
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 168 | 181 | 102.4
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 168 | 181 | 101.61
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 168 | 181 | 101.52
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:101 | T:77&78 | 168 | 181 | 101.14
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | FARMVLY - HOMERCTY | T:77&78 | 168 | 181 | 101.14
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 168 | 181 | 100.99
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 168 | 181 | 100.99
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:102 | T:77&78 | 168 | 181 | 100.88
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:181/922 | T:77&78 | 168 | 181 | 100.79
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:133 | T:77&78 | 168 | 181 | 100.71
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:120 | T:77&78 | 168 | 181 | 100.69
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:130 | T:77&78 | 168 | 181 | 100.55
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | TB:2/1:PK3 | T:77&78 | 168 | 181 | 100.48
Dispatch 2 | 135383 S219-182 115 135505 WALDENTP 115 1 | LN:115:129 | T:77&78 | 168 | 181 | 100.23
Dispatch 1 | 135383 S219-182 115 135505 WALDENTP 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 168 | 181 | 100.15
| 135383 S219-182 115 135505 WALDENTP 115 1 Max |  |  |  |  | 139.5
Dispatch 1 | 135401 GERNATT 115 147875 ARCADE 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 129 | 148 | NConv
Dispatch 1 | 135401 GERNATT 115 147875 ARCADE 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 129 | 148 | NConv
Dispatch 1 | 135401 GERNATT 115 147875 ARCADE 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 129 | 148 | NConv
Dispatch 1 | 135401 GERNATT 115 147875 ARCADE 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 129 | 148 | NConv
Dispatch 1 | 135401 GERNATT 115 147875 ARCADE 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 129 | 148 | NConv
Dispatch 2 | 135401 GERNATT 115 147875 ARCADE 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 129 | 148 | NConv
Dispatch 2 | 135401 GERNATT 115 147875 ARCADE 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 129 | 148 | NConv
Dispatch 2 | 135401 GERNATT 115 147875 ARCADE 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 129 | 148 | NConv
Dispatch 2 | 135401 GERNATT 115 147875 ARCADE 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 129 | 148 | NConv
Dispatch 2 | 135401 GERNATT 115 147875 ARCADE 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 129 | 148 | NConv
| 135401 GERNATT 115 147875 ARCADE 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
| 135413 GRDNVL2 230 135418 SUNY-79 230 1 Max |  |  |  |  | 0
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 654 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 654 | NConv
| 135413 GRDNVL2 230 135419 SUNY-80 230 1 Max |  |  |  |  | 0
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 189 | 250 | NConv
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 189 | 250 | NConv
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 189 | 250 | NConv
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 189 | 250 | NConv
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 189 | 250 | NConv
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 189 | 250 | NConv
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 189 | 250 | NConv
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 189 | 250 | NConv
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 189 | 250 | NConv
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 189 | 250 | NConv
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | TB:2/1:NI1 | T:77&78 | 189 | 250 | 135.34
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | T:77&78 | 189 | 250 | 135.34
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 189 | 250 | 133.36
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 189 | 250 | 123.62
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 189 | 250 | 115.78
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | TB:2/1:NI1 | DCT:230:79+80+ELM1-2 | 189 | 250 | 114.69
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | DCT:230:79+80+ELM1-2 | 189 | 250 | 114.69
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 189 | 250 | 113.19
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 189 | 250 | 113.19
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | TB:2/1:NI1 | T:79&80 | 189 | 250 | 113.04
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | T:79&80 | 189 | 250 | 113.04
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 189 | 250 | 110.72
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 189 | 250 | 110.42
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 189 | 250 | 110.16
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 189 | 250 | 110.1
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | G:NIAG. 4 | T:77&78 | 189 | 250 | 104.5
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | G:NIAG. 5 | T:77&78 | 189 | 250 | 104.5
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | G:NIAG. 6 | T:77&78 | 189 | 250 | 104.5
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | G:NIAG. 7 | T:77&78 | 189 | 250 | 104.46
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | LN:115:908 NY | T:77&78 | 189 | 250 | 103.39
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | LN:115:100 | T:77&78 | 189 | 250 | 102.29
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | LN:115:133 | T:77&78 | 189 | 250 | 102.06
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | LN:115:130 | T:77&78 | 189 | 250 | 101.78
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | TB:2/1:ROB | T:77&78 | 189 | 250 | 101.03
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | LN:115:129 | T:77&78 | 189 | 250 | 100.99
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | TB:2/1:NI1 | T:77&78 | 189 | 250 | 100.42
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | T:77&78 | 189 | 250 | 100.42
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 189 | 250 | 100.06
| 135415 PACKARD2 230 135460 PACK(N)E 115 1 Max |  |  |  |  | 135.34
Dispatch 2 | 135415 PACKARD2 230 135461 PACK(S)W 115 2 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 190 | 250 | 117.59
Dispatch 1 | 135415 PACKARD2 230 135461 PACK(S)W 115 2 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 190 | 250 | 109.17
Dispatch 2 | 135415 PACKARD2 230 135461 PACK(S)W 115 2 | NIAGARA - PACKARD 61 230 | T:62&BP76 | 190 | 250 | 100.33
| 135415 PACKARD2 230 135461 PACK(S)W 115 2 Max |  |  |  |  | 117.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:62&BP76 | 620 | 841 | 131.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R506 | 620 | 841 | 129.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:62&BP76 | 620 | 841 | 125.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:62&BP76 | 620 | 841 | 124.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:62&BP76 | 620 | 841 | 123.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R506 | 620 | 841 | 123.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R506 | 620 | 841 | 122.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R506 | 620 | 841 | 122.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:62&BP76 | 620 | 841 | 122.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:NI1 | T:62&BP76 | 620 | 841 | 120.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | T:62&BP76 | 620 | 841 | 120.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R506 | 620 | 841 | 120.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:NI1 | SB:PA230_R506 | 620 | 841 | 119.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | SB:PA230_R506 | 620 | 841 | 119.07
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R506 | 620 | 841 | 116.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | T:62&BP76 | 620 | 841 | 114.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | Base Case | 620 | 841 | 114.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:62&BP76 | 620 | 841 | 114.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R506 | 620 | 841 | 113.69
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:62&BP76 | 620 | 841 | 113.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R506 | 620 | 841 | 112.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:NI2 | T:62&BP76 | 620 | 841 | 112.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | T:62&BP76 | 620 | 841 | 112.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:908 NY | T:62&BP76 | 620 | 841 | 112.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | T:62&BP76 | 620 | 841 | 112.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:100 | T:62&BP76 | 620 | 841 | 112.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | T:62&BP76 | 620 | 841 | 112.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | T:62&BP76 | 620 | 841 | 112.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 1 | T:62&BP76 | 620 | 841 | 112.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 2 | T:62&BP76 | 620 | 841 | 112.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 3 | T:62&BP76 | 620 | 841 | 112.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:62&BP76 | 620 | 841 | 111.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:62&BP76 | 620 | 841 | 111.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:62&BP76 | 620 | 841 | 111.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:62&BP76 | 620 | 841 | 111.77
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R506 | 620 | 841 | 111.75
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R506 | 620 | 841 | 111.75
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:ROB | T:62&BP76 | 620 | 841 | 111.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:133 | SB:PA230_R506 | 620 | 841 | 111.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:180 | T:62&BP76 | 620 | 841 | 111.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:130 | SB:PA230_R506 | 620 | 841 | 111.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS1 | T:62&BP76 | 620 | 841 | 111.25
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R506 | 620 | 841 | 111.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | SB:PA230_R506 | 620 | 841 | 111.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:129 | SB:PA230_R506 | 620 | 841 | 110.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:907 NY | T:62&BP76 | 620 | 841 | 110.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | First:Lockport_907 | T:62&BP76 | 620 | 841 | 110.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | SB:PA230_R506 | 620 | 841 | 110.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R506 | 620 | 841 | 110.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:INDEK-OL | T:62&BP76 | 620 | 841 | 110.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV-HC | T:62&BP76 | 620 | 841 | 110.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:PA230_R506 | 620 | 841 | 110.77
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:PA230_R506 | 620 | 841 | 110.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:PA230_R506 | 620 | 841 | 110.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:PA230_R506 | 620 | 841 | 110.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:PA230_R506 | 620 | 841 | 110.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LOCKPORT | T:62&BP76 | 620 | 841 | 110.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:182N | T:62&BP76 | 620 | 841 | 110.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:100 | SB:PA230_R506 | 620 | 841 | 110.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:JAMESGN7 | T:62&BP76 | 620 | 841 | 110.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:NI2 | SB:PA230_R506 | 620 | 841 | 110.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | SB:PA230_R506 | 620 | 841 | 110.28
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:181/922 | T:62&BP76 | 620 | 841 | 110.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:180 | SB:PA230_R506 | 620 | 841 | 110.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 13 345 | T:62&BP76 | 620 | 841 | 110.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:192 | T:62&BP76 | 620 | 841 | 110.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:195 | T:62&BP76 | 620 | 841 | 110.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:4 | T:62&BP76 | 620 | 841 | 110.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:969 | T:62&BP76 | 620 | 841 | 110.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | T:62&BP76 | 620 | 841 | 110.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS1 | SB:PA230_R506 | 620 | 841 | 110.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:191 | T:62&BP76 | 620 | 841 | 110.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:182S | T:62&BP76 | 620 | 841 | 110.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:ROB | SB:PA230_R506 | 620 | 841 | 110
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:OXBOWNUG | T:62&BP76 | 620 | 841 | 109.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:193 | T:62&BP76 | 620 | 841 | 109.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:194 | T:62&BP76 | 620 | 841 | 109.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:38 | T:62&BP76 | 620 | 841 | 109.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | T:62&BP76 | 620 | 841 | 109.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | T:62&BP76 | 620 | 841 | 109.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:UDG-184 | T:62&BP76 | 620 | 841 | 109.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:8 | T:62&BP76 | 620 | 841 | 109.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | T:62&BP76 | 620 | 841 | 109.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS2 | T:62&BP76 | 620 | 841 | 109.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV | T:62&BP76 | 620 | 841 | 109.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:DUPONT46 | T:62&BP76 | 620 | 841 | 109.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DEWITT3 - LAFAYTTE 345 | T:62&BP76 | 620 | 841 | 109.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:39 | T:62&BP76 | 620 | 841 | 109.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:INDEK-OL | SB:PA230_R506 | 620 | 841 | 109.77
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:115:AMERT | T:62&BP76 | 620 | 841 | 109.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:38 | SB:PA230_R506 | 620 | 841 | 109.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - WATERCURE 69 230 | T:62&BP76 | 620 | 841 | 109.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - ETWANDA 70 230 | T:62&BP76 | 620 | 841 | 109.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | First:Lockport_104 | T:62&BP76 | 620 | 841 | 109.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-1 345 | T:62&BP76 | 620 | 841 | 109.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-2 345 | T:62&BP76 | 620 | 841 | 109.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - EDIC 2-15 345 | T:62&BP76 | 620 | 841 | 109.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL - CLAY PC-1 345 | T:62&BP76 | 620 | 841 | 109.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL - CLAY PC-2 345 | T:62&BP76 | 620 | 841 | 109.6
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:39 | SB:PA230_R506 | 620 | 841 | 109.57
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV-HC | SB:PA230_R506 | 620 | 841 | 109.57
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 62 230 | 620 | 841 | 109.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:907 NY | SB:PA230_R506 | 620 | 841 | 109.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | First:Lockport_907 | SB:PA230_R506 | 620 | 841 | 109.4
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:62&BP76 | 620 | 841 | 109.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:JAMESGN7 | SB:PA230_R506 | 620 | 841 | 109.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:182N | SB:PA230_R506 | 620 | 841 | 109.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LOCKPORT | SB:PA230_R506 | 620 | 841 | 109.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - DEW 13 345 | SB:PA230_R506 | 620 | 841 | 109.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | BECK - PACKARD BP76 230 | 620 | 841 | 109.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:969 | SB:PA230_R506 | 620 | 841 | 109.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:4 | SB:PA230_R506 | 620 | 841 | 109.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:181/922 | SB:PA230_R506 | 620 | 841 | 109
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | SB:PA230_R506 | 620 | 841 | 108.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:182S | SB:PA230_R506 | 620 | 841 | 108.87
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R506 | 620 | 841 | 108.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:8 | SB:PA230_R506 | 620 | 841 | 108.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R506 | 620 | 841 | 108.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R506 | 620 | 841 | 108.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:BLISS2 | SB:PA230_R506 | 620 | 841 | 108.77
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R506 | 620 | 841 | 108.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R506 | 620 | 841 | 108.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:115:AMERT | SB:PA230_R506 | 620 | 841 | 108.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R506 | 620 | 841 | 108.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R506 | 620 | 841 | 108.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV | SB:PA230_R506 | 620 | 841 | 108.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-2 345 | SB:PA230_R506 | 620 | 841 | 108.59
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROCH - PANNELL RP-1 345 | SB:PA230_R506 | 620 | 841 | 108.58
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CLAY - EDIC 2-15 345 | SB:PA230_R506 | 620 | 841 | 108.57
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL - CLAY PC-1 345 | SB:PA230_R506 | 620 | 841 | 108.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PANL - CLAY PC-2 345 | SB:PA230_R506 | 620 | 841 | 108.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | T:62&PA27 | 620 | 841 | 108.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | First:Lancaster_GRDN_GRDN_230 | T:62&BP76 | 620 | 841 | 108.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | B:PACKT4 | 620 | 841 | 108.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:141 | T:62&BP76 | 620 | 841 | 108.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:142 | T:62&BP76 | 620 | 841 | 108.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:161 | T:62&BP76 | 620 | 841 | 108.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/2:PA27 | T:62&BP76 | 620 | 841 | 108.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - BECK PA27 230 | T:62&BP76 | 620 | 841 | 108.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:120 | T:62&BP76 | 620 | 841 | 108.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:OSWEGO 5 | T:62&BP76 | 620 | 841 | 108.15
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:62&BP76 | 620 | 841 | 108.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:PA27&BP76 | 620 | 841 | 108.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:102 | T:62&BP76 | 620 | 841 | 108.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:OSWEGO 6 | T:62&BP76 | 620 | 841 | 108.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:101 | T:62&BP76 | 620 | 841 | 108.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:114 | T:62&BP76 | 620 | 841 | 107.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:113 | T:62&BP76 | 620 | 841 | 107.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:119 | T:62&BP76 | 620 | 841 | 107.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:PK4 | T:62&BP76 | 620 | 841 | 107.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | T:62&BP76 | 620 | 841 | 107.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 73 230 | T:62&BP76 | 620 | 841 | 107.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 74 230 | T:62&BP76 | 620 | 841 | 107.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:54/921 | T:62&BP76 | 620 | 841 | 107.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - ELM 70 230 | T:62&BP76 | 620 | 841 | 107.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:903 NY | T:62&BP76 | 620 | 841 | 107.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:3/2:FV | T:62&BP76 | 620 | 841 | 107.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - FARMVLY | T:62&BP76 | 620 | 841 | 107.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:FITZPATR | T:62&BP76 | 620 | 841 | 107.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:111 | T:62&BP76 | 620 | 841 | 107.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STNYRDG - HILLSIDE 68B 230 | T:62&BP76 | 620 | 841 | 107.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:9MIPT1 | T:62&BP76 | 620 | 841 | 107.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 7-9 | T:62&BP76 | 620 | 841 | 107.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 10-12 | T:62&BP76 | 620 | 841 | 107.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 1-3 | T:62&BP76 | 620 | 841 | 107.68
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 4-6 | T:62&BP76 | 620 | 841 | 107.68
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:62&BP76 | 620 | 841 | 107.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:160 | T:62&BP76 | 620 | 841 | 107.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:141 | SB:PA230_R506 | 620 | 841 | 107.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/2:PA27 | SB:PA230_R506 | 620 | 841 | 107.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | First:Lancaster_GRDN_GRDN_230 | SB:PA230_R506 | 620 | 841 | 107.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - BECK PA27 230 | SB:PA230_R506 | 620 | 841 | 107.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:GV6 | SB:PA230_R506 | 620 | 841 | 107.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:GV8 | SB:PA230_R506 | 620 | 841 | 107.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL 230/115 M6TR | SB:PA230_R506 | 620 | 841 | 107.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL 230/115 M8TR | SB:PA230_R506 | 620 | 841 | 107.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:142 | SB:PA230_R506 | 620 | 841 | 107.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:161 | SB:PA230_R506 | 620 | 841 | 107.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:FITZPATR | SB:PA230_R506 | 620 | 841 | 107.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MEYER - CANDQUA 60 230 | T:62&BP76 | 620 | 841 | 107.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 1 | SB:PA230_R506 | 620 | 841 | 107.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 2 | SB:PA230_R506 | 620 | 841 | 107.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 3 | SB:PA230_R506 | 620 | 841 | 107.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:114 | SB:PA230_R506 | 620 | 841 | 107.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:119 | SB:PA230_R506 | 620 | 841 | 107.05
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:113 | SB:PA230_R506 | 620 | 841 | 107.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - WTRCR 31 345 | T:62&BP76 | 620 | 841 | 107.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:111 | SB:PA230_R506 | 620 | 841 | 106.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:9MIPT1 | SB:PA230_R506 | 620 | 841 | 106.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:54/921 | SB:PA230_R506 | 620 | 841 | 106.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:3/2:FV | SB:PA230_R506 | 620 | 841 | 106.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | FARMVLY - FARMVLY | SB:PA230_R506 | 620 | 841 | 106.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:903 NY | SB:PA230_R506 | 620 | 841 | 106.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 73 230 | SB:PA230_R506 | 620 | 841 | 106.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GARDENVILL - DUNKIRK 74 230 | SB:PA230_R506 | 620 | 841 | 106.77
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:120 | SB:PA230_R506 | 620 | 841 | 106.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 7-9 | SB:PA230_R506 | 620 | 841 | 106.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 10-12 | SB:PA230_R506 | 620 | 841 | 106.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - ELM 70 230 | SB:PA230_R506 | 620 | 841 | 106.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 1-3 | SB:PA230_R506 | 620 | 841 | 106.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:LEW 4-6 | SB:PA230_R506 | 620 | 841 | 106.71
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STNYRDG - HILLSIDE 68B 230 | SB:PA230_R506 | 620 | 841 | 106.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:102 | SB:PA230_R506 | 620 | 841 | 106.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:101 | SB:PA230_R506 | 620 | 841 | 106.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:MEYER | T:62&BP76 | 620 | 841 | 106.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | T:62&BP76 | 620 | 841 | 106.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:160 | SB:PA230_R506 | 620 | 841 | 106.3
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:62&BP76 | 620 | 841 | 106.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SHLDON - STONYCR 230 | T:62&BP76 | 620 | 841 | 106.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:9 MI PT2 | T:62&BP76 | 620 | 841 | 106.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ERIE E - 4 MILE 230 | T:62&BP76 | 620 | 841 | 106.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MEYER - CANDQUA 60 230 | SB:PA230_R506 | 620 | 841 | 105.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - WTRCR 31 345 | SB:PA230_R506 | 620 | 841 | 105.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:115:GINNA | T:62&BP76 | 620 | 841 | 105.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:GINNA | T:62&BP76 | 620 | 841 | 105.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CAP:115:GV1 | T:62&BP76 | 620 | 841 | 105.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CAP:115:GV2 | T:62&BP76 | 620 | 841 | 105.76
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:9 MI PT2 | SB:PA230_R506 | 620 | 841 | 105.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | T:62&BP76 | 620 | 841 | 105.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SRIPL - ERIE E 69 230 | T:62&BP76 | 620 | 841 | 105.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DUNKIRK - SRIPL 68 230 | T:62&BP76 | 620 | 841 | 105.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | SB:PA230_R506 | 620 | 841 | 105.42
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:MEYER | SB:PA230_R506 | 620 | 841 | 105.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:195 | SB:PA230_R506 | 620 | 841 | 105.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SHLDON - STONYCR 230 | SB:PA230_R506 | 620 | 841 | 105.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:192 | SB:PA230_R506 | 620 | 841 | 105.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:191 | SB:PA230_R506 | 620 | 841 | 105.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | ERIE E - 4 MILE 230 | SB:PA230_R506 | 620 | 841 | 105.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:115:GINNA | SB:PA230_R506 | 620 | 841 | 105
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:GINNA | SB:PA230_R506 | 620 | 841 | 104.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CAP:115:GV1 | SB:PA230_R506 | 620 | 841 | 104.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CAP:115:GV2 | SB:PA230_R506 | 620 | 841 | 104.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | NIAGARA - PACKARD 62 230 | 620 | 841 | 104.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:PK3 | T:62&BP76 | 620 | 841 | 104.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | SB:PA230_R506 | 620 | 841 | 104.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SRIPL - ERIE E 69 230 | SB:PA230_R506 | 620 | 841 | 104.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 11 | T:62&BP76 | 620 | 841 | 104.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 12 | T:62&BP76 | 620 | 841 | 104.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 13 | T:62&BP76 | 620 | 841 | 104.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 8 | T:62&BP76 | 620 | 841 | 104.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 9 | T:62&BP76 | 620 | 841 | 104.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 10 | T:62&BP76 | 620 | 841 | 104.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | DUNKIRK - SRIPL 68 230 | SB:PA230_R506 | 620 | 841 | 104.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROBI230 | 620 | 841 | 104.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | T:62&BP76 | 620 | 841 | 103.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - ROBINSON 64 345 | 620 | 841 | 103.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 11 | SB:PA230_R506 | 620 | 841 | 103.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 12 | SB:PA230_R506 | 620 | 841 | 103.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 13 | SB:PA230_R506 | 620 | 841 | 103.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 8 | SB:PA230_R506 | 620 | 841 | 103.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 9 | SB:PA230_R506 | 620 | 841 | 103.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 10 | SB:PA230_R506 | 620 | 841 | 103.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | T:62&BP76 | 620 | 841 | 103.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | T:62&BP76 | 620 | 841 | 103.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCWC/NWES | T:62&BP76 | 620 | 841 | 103.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:MBWC/NWES | T:62&BP76 | 620 | 841 | 103.36
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R506 | 620 | 841 | 102.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | SB:PA230_R506 | 620 | 841 | 102.73
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | TB:2/1:NI1 | SB:PA230_R506 | 620 | 841 | 102.64
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA 230/115 1TR | SB:PA230_R506 | 620 | 841 | 102.64
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | SB:PA230_R506 | 620 | 841 | 102.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCWC/NWES | SB:PA230_R506 | 620 | 841 | 102.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:MBWC/NWES | SB:PA230_R506 | 620 | 841 | 102.44
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R506 | 620 | 841 | 102.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCMB/NWES | T:62&BP76 | 620 | 841 | 102.07
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R506 | 620 | 841 | 102.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | T:62&BP76 | 620 | 841 | 101.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | T:62&BP76 | 620 | 841 | 101.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | B:PACKT4 | 620 | 841 | 101.83
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:62&PA27 | 620 | 841 | 101.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HCMB/NWES | SB:PA230_R506 | 620 | 841 | 101.17
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:133 | SB:PA230_R506 | 620 | 841 | 101.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | SB:PA230_R506 | 620 | 841 | 101.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R506 | 620 | 841 | 101.02
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:130 | SB:PA230_R506 | 620 | 841 | 100.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:PA230_R506 | 620 | 841 | 100.81
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:PA230_R506 | 620 | 841 | 100.81
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:PA230_R506 | 620 | 841 | 100.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:345:SOMERSET | T:62&BP76 | 620 | 841 | 100.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:KINTIGH | T:62&BP76 | 620 | 841 | 100.8
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:62&BP76 | 620 | 841 | 100.79
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:PA230_R506 | 620 | 841 | 100.79
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | LN:115:129 | SB:PA230_R506 | 620 | 841 | 100.56
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | T:62&BP76 | 620 | 841 | 100.53
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:345:SOMERSET | SB:PA230_R506 | 620 | 841 | 100.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | GEN:KINTIGH | SB:PA230_R506 | 620 | 841 | 100.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | T:62&BP76 | 620 | 841 | 100.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | T:62&BP76 | 620 | 841 | 100.13
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 Max |  |  |  |  | 131.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE 230/115 4TR | B:STOLE230 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | T:61&64 | 620 | 841 | 130.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 345 | SB:PA230_R304 | 620 | 841 | 120.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | T:61&64 | 620 | 841 | 120.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:2/1:NI1 | T:61&64 | 620 | 841 | 120.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 1TR | T:61&64 | 620 | 841 | 120.38
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | T:61&64 | 620 | 841 | 117.17
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R304 | 620 | 841 | 115.54
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R304 | 620 | 841 | 114.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R304 | 620 | 841 | 114.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | Base Case | 620 | 841 | 113.87
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | T:61&64 | 620 | 841 | 112.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | SB:PA230_R304 | 620 | 841 | 111.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | T:61&191 | 620 | 841 | 111.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:2/1:NI1 | SB:PA230_R304 | 620 | 841 | 109.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 1TR | SB:PA230_R304 | 620 | 841 | 109.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 61 230 | 620 | 841 | 109.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LFYTE - CLARKCRNS 36A 345 | T:61&64 | 620 | 841 | 108.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | BECK - PACKARD BP76 230 | 620 | 841 | 108.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:2/1:NI2 | T:61&64 | 620 | 841 | 108.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 2TR | T:61&64 | 620 | 841 | 108.7
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - CLARKCRNS 36B 345 | T:61&64 | 620 | 841 | 108.1
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | T:PA27&BP76 | 620 | 841 | 107.91
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - KINTIGH 345 | T:61&64 | 620 | 841 | 107.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:3/2:NI3 | T:61&64 | 620 | 841 | 106.81
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 4TR | T:61&64 | 620 | 841 | 106.81
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 345 | SB:PA230_R304 | 620 | 841 | 106.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-FV_37&W-F_171 | T:61&64 | 620 | 841 | 105.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R304 | 620 | 841 | 105.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - HOMERCTY | T:61&64 | 620 | 841 | 105.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:180 | T:61&64 | 620 | 841 | 105.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 345 | T:61&191 | 620 | 841 | 105.66
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | T:61&64 | 620 | 841 | 105.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LOCKPORT | T:61&64 | 620 | 841 | 105.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:195 | SB:PA230_R304 | 620 | 841 | 105.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:192 | SB:PA230_R304 | 620 | 841 | 105.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R304 | 620 | 841 | 105.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 4 | T:61&64 | 620 | 841 | 105.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 5 | T:61&64 | 620 | 841 | 105.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 6 | T:61&64 | 620 | 841 | 105.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS1 | T:61&64 | 620 | 841 | 105.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 7 | T:61&64 | 620 | 841 | 105.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:191 | SB:PA230_R304 | 620 | 841 | 105.14
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:182N | T:61&64 | 620 | 841 | 105.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:345:37S-FM-FV-HC | T:61&64 | 620 | 841 | 104.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:INDEK-OL | T:61&64 | 620 | 841 | 104.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:181/922 | T:61&64 | 620 | 841 | 104.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 1 | T:61&64 | 620 | 841 | 104.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 2 | T:61&64 | 620 | 841 | 104.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 3 | T:61&64 | 620 | 841 | 104.74
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:3/2:NI1 | T:61&64 | 620 | 841 | 104.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:3/2:NI2 | T:61&64 | 620 | 841 | 104.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 3TR | T:61&64 | 620 | 841 | 104.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 345/230 5TR | T:61&64 | 620 | 841 | 104.62
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:182S | T:61&64 | 620 | 841 | 104.61
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | T:61&64 | 620 | 841 | 104.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 5TR | T:61&64 | 620 | 841 | 104.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 13 345 | T:61&64 | 620 | 841 | 104.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:JAMESGN7 | T:61&64 | 620 | 841 | 104.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:969 | T:61&64 | 620 | 841 | 104.42
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | T:61&64 | 620 | 841 | 104.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:4 | T:61&64 | 620 | 841 | 104.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:2/1:NI2 | SB:PA230_R304 | 620 | 841 | 104.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA 230/115 2TR | SB:PA230_R304 | 620 | 841 | 104.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | First:Lockport_907 | T:61&64 | 620 | 841 | 104.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - SHLDON 67 230 | T:61&64 | 620 | 841 | 104.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:2/1:PK3 | SB:PA230_R304 | 620 | 841 | 104.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | First:Lockport_104 | T:61&64 | 620 | 841 | 104.27
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:130 | T:61&64 | 620 | 841 | 104.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-SR_37&W-F_171 | T:61&64 | 620 | 841 | 104.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:FV-5M_37&W-F_171 | T:61&64 | 620 | 841 | 104.26
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:38 | T:61&64 | 620 | 841 | 104.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:133 | T:61&64 | 620 | 841 | 104.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:193 | T:61&64 | 620 | 841 | 104.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:194 | T:61&64 | 620 | 841 | 104.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:129 | T:61&64 | 620 | 841 | 104.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:8 | T:61&64 | 620 | 841 | 104.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - 5MILE 345 | T:61&64 | 620 | 841 | 104.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:39 | T:61&64 | 620 | 841 | 104.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:345:37S-FM-FV | T:61&64 | 620 | 841 | 104.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:907 NY | T:61&64 | 620 | 841 | 104.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 345 | T:61&64 | 620 | 841 | 104.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 345 | NIAGARA - PACKARD 61 230 | 620 | 841 | 104.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - WATERCURE 69 230 | T:61&64 | 620 | 841 | 104.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - ETWANDA 70 230 | T:61&64 | 620 | 841 | 104.06
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DEWITT3 - LAFAYTTE 345 | T:61&64 | 620 | 841 | 104.03
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS2 | T:61&64 | 620 | 841 | 103.99
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | First:Lockport_103 | T:61&64 | 620 | 841 | 103.98
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-2 345 | T:61&64 | 620 | 841 | 103.97
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-1 345 | T:61&64 | 620 | 841 | 103.96
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:182N | SB:PA230_R304 | 620 | 841 | 103.95
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:180 | SB:PA230_R304 | 620 | 841 | 103.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:OXBOWNUG | T:61&64 | 620 | 841 | 103.93
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:DUPONT46 | T:61&64 | 620 | 841 | 103.92
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL - CLAY PC-2 345 | T:61&64 | 620 | 841 | 103.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - EDIC 2-15 345 | T:61&64 | 620 | 841 | 103.9
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:934 NY | T:61&64 | 620 | 841 | 103.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PANL - CLAY PC-1 345 | T:61&64 | 620 | 841 | 103.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | SB:ROBI230 | 620 | 841 | 103.88
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE 230/115 3TR | T:61&64 | 620 | 841 | 103.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:110 | T:61&64 | 620 | 841 | 103.84
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 1 | SB:PA230_R304 | 620 | 841 | 103.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 2 | SB:PA230_R304 | 620 | 841 | 103.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 3 | SB:PA230_R304 | 620 | 841 | 103.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:181/922 | SB:PA230_R304 | 620 | 841 | 103.73
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA - ROBINSON 64 345 | 620 | 841 | 103.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - KINTIGH 345 | SB:PA230_R304 | 620 | 841 | 103.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-FV_37&W-F_171 | SB:PA230_R304 | 620 | 841 | 103.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - HOMERCTY | SB:PA230_R304 | 620 | 841 | 103.12
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:182S | SB:PA230_R304 | 620 | 841 | 102.9
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R304 | 620 | 841 | 102.86
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:161 | T:61&64 | 620 | 841 | 102.63
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:908 NY | T:61&64 | 620 | 841 | 102.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE 230/115 4TR | T:61&64 | 620 | 841 | 102.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS1 | SB:PA230_R304 | 620 | 841 | 102.5
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:OSWEGO 5 | T:61&64 | 620 | 841 | 102.47
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:908 NY | SB:PA230_R304 | 620 | 841 | 102.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HUNTLEY - ELM 70 230 | T:61&64 | 620 | 841 | 102.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:OSWEGO 6 | T:61&64 | 620 | 841 | 102.39
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 73 230 | T:61&64 | 620 | 841 | 102.36
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:3/2:FV | T:61&64 | 620 | 841 | 102.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:114 | T:61&64 | 620 | 841 | 102.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - FARMVLY | T:61&64 | 620 | 841 | 102.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GARDENVILL - DUNKIRK 74 230 | T:61&64 | 620 | 841 | 102.35
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:113 | T:61&64 | 620 | 841 | 102.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:119 | T:61&64 | 620 | 841 | 102.31
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:903 NY | T:61&64 | 620 | 841 | 102.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:54/921 | T:61&64 | 620 | 841 | 102.28
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROBINSON - STOLLRD 65 230 | SB:PA230_R304 | 620 | 841 | 102.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:100 | SB:PA230_R304 | 620 | 841 | 102.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:111 | T:61&64 | 620 | 841 | 102.23
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:FITZPATR | T:61&64 | 620 | 841 | 102.22
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:INDEK-OL | SB:PA230_R304 | 620 | 841 | 102.15
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:9MIPT1 | T:61&64 | 620 | 841 | 102.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:345:37S-FM-FV-HC | SB:PA230_R304 | 620 | 841 | 102.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:2/1:ROB | SB:PA230_R304 | 620 | 841 | 101.92
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | SB:PA230_R304 | 620 | 841 | 101.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:160 | T:61&64 | 620 | 841 | 101.85
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | STNYRDG - HILLSIDE 68B 230 | T:61&64 | 620 | 841 | 101.82
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:JAMESGN7 | SB:PA230_R304 | 620 | 841 | 101.65
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - DEW 13 345 | SB:PA230_R304 | 620 | 841 | 101.52
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:907 NY | SB:PA230_R304 | 620 | 841 | 101.51
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | First:Lockport_907 | SB:PA230_R304 | 620 | 841 | 101.5
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 1-3 | T:61&64 | 620 | 841 | 101.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 4-6 | T:61&64 | 620 | 841 | 101.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 7-9 | T:61&64 | 620 | 841 | 101.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LEW 10-12 | T:61&64 | 620 | 841 | 101.49
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:4 | SB:PA230_R304 | 620 | 841 | 101.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:969 | SB:PA230_R304 | 620 | 841 | 101.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDLE - WTRCR 31 345 | T:61&64 | 620 | 841 | 101.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:UDG-184 | SB:PA230_R304 | 620 | 841 | 101.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:OXBOWNUG | SB:PA230_R304 | 620 | 841 | 101.37
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:193 | SB:PA230_R304 | 620 | 841 | 101.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:194 | SB:PA230_R304 | 620 | 841 | 101.33
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | First:Lancaster_922 | SB:PA230_R304 | 620 | 841 | 101.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:38 | SB:PA230_R304 | 620 | 841 | 101.29
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:HC-SR_37&W-F_171 | SB:PA230_R304 | 620 | 841 | 101.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | R:FV-5M_37&W-F_171 | SB:PA230_R304 | 620 | 841 | 101.25
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:8 | SB:PA230_R304 | 620 | 841 | 101.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH 345/115 5TR | SB:PA230_R304 | 620 | 841 | 101.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 4 | SB:PA230_R304 | 620 | 841 | 101.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 5 | SB:PA230_R304 | 620 | 841 | 101.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 6 | SB:PA230_R304 | 620 | 841 | 101.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:NIAG. 7 | SB:PA230_R304 | 620 | 841 | 101.24
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:LOCKPORT | SB:PA230_R304 | 620 | 841 | 101.2
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:BLISS2 | SB:PA230_R304 | 620 | 841 | 101.19
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | FARMVLY - 5MILE 345 | SB:PA230_R304 | 620 | 841 | 101.18
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:115:39 | SB:PA230_R304 | 620 | 841 | 101.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:DUPONT46 | SB:PA230_R304 | 620 | 841 | 101.16
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DEWITT3 - LAFAYTTE 345 | SB:PA230_R304 | 620 | 841 | 101.13
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | MEYER - CANDQUA 60 230 | T:61&64 | 620 | 841 | 101.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | LN:345:37S-FM-FV | SB:PA230_R304 | 620 | 841 | 101.08
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - WATERCURE 69 230 | SB:PA230_R304 | 620 | 841 | 101.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE - ETWANDA 70 230 | SB:PA230_R304 | 620 | 841 | 101.07
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ERIE E - 4 MILE 230 | T:61&64 | 620 | 841 | 101.04
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-2 345 | SB:PA230_R304 | 620 | 841 | 101.02
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | T:61&64 | 620 | 841 | 101.02
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | ROCH - PANNELL RP-1 345 | SB:PA230_R304 | 620 | 841 | 101.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CLAY - EDIC 2-15 345 | SB:PA230_R304 | 620 | 841 | 101.01
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SHLDON - STONYCR 230 | T:61&64 | 620 | 841 | 100.94
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:2/2:PA27 | T:61&64 | 620 | 841 | 100.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - BECK PA27 230 | T:61&64 | 620 | 841 | 100.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | OAKDL - FRASER 32 345 | T:61&64 | 620 | 841 | 100.89
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:2/1:MEYER | T:61&64 | 620 | 841 | 100.79
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | B:PACKT3 | 620 | 841 | 100.78
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | TB:2/1:PK4 | T:61&64 | 620 | 841 | 100.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | PACKARD 230/115 4TR | T:61&64 | 620 | 841 | 100.72
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:9 MI PT2 | T:61&64 | 620 | 841 | 100.67
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SRIPL - ERIE E 69 230 | T:61&64 | 620 | 841 | 100.46
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | DUNKIRK - SRIPL 68 230 | T:61&64 | 620 | 841 | 100.45
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CAP:115:GV1 | T:61&64 | 620 | 841 | 100.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CAP:115:GV2 | T:61&64 | 620 | 841 | 100.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | GEN:115:GINNA | T:61&64 | 620 | 841 | 100.41
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | G:GINNA | T:61&64 | 620 | 841 | 100.4
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | First:Lancaster_GRDN_GRDN_230 | T:61&64 | 620 | 841 | 100.29
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 Max |  |  |  |  | 130.19
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 500 | 587 | NConv
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 500 | 587 | NConv
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | T:61&64 | 500 | 587 | 130.32
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | T:61&64 | 500 | 587 | 114.06
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | B:PACKT4 | 500 | 587 | 113.93
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | T:61&191 | 500 | 587 | 110.23
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | NIAGARA - PACKARD 62 230 | 500 | 587 | 107.94
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - PACKARD 61 230 | 500 | 587 | 107.94
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | T:62&PA27 | 500 | 587 | 107.37
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | B:PACKT3 | 500 | 587 | 105.43
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R3430 | 500 | 587 | 104.08
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | B:PACKT4 | 500 | 587 | 103.61
| 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 Max |  |  |  |  | 130.32
Dispatch 2 | 135432 AM.S-182 115 135450 GRDNVL1 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 129 | 182 | 126.52
Dispatch 1 | 135432 AM.S-182 115 135450 GRDNVL1 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 129 | 182 | 122.76
Dispatch 2 | 135432 AM.S-182 115 135450 GRDNVL1 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 129 | 182 | 119.97
Dispatch 1 | 135432 AM.S-182 115 135450 GRDNVL1 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 129 | 182 | 115.72
Dispatch 2 | 135432 AM.S-182 115 135450 GRDNVL1 115 1 | LN:115:180 | T:77&78 | 129 | 182 | 108.69
Dispatch 2 | 135432 AM.S-182 115 135450 GRDNVL1 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 129 | 182 | 108.63
Dispatch 2 | 135432 AM.S-182 115 135450 GRDNVL1 115 1 | First:Lancaster_922 | T:77&78 | 129 | 182 | 105.53
Dispatch 1 | 135432 AM.S-182 115 135450 GRDNVL1 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 129 | 182 | 104.65
Dispatch 2 | 135432 AM.S-182 115 135450 GRDNVL1 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 129 | 182 | 103.69
Dispatch 1 | 135432 AM.S-182 115 135450 GRDNVL1 115 1 | LN:115:180 | T:77&78 | 129 | 182 | 102.05
Dispatch 2 | 135432 AM.S-182 115 135450 GRDNVL1 115 1 | LN:115:195 | T:77&78 | 129 | 182 | 100.11
| 135432 AM.S-182 115 135450 GRDNVL1 115 1 Max |  |  |  |  | 126.52
Dispatch 2 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 185 | 125.09
Dispatch 1 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 185 | 121.41
Dispatch 2 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 185 | 118.45
Dispatch 1 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 185 | 114.26
Dispatch 2 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | LN:115:180 | T:77&78 | 168 | 185 | 107.34
Dispatch 2 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 168 | 185 | 107.29
Dispatch 2 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | First:Lancaster_922 | T:77&78 | 168 | 185 | 104.23
Dispatch 1 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 168 | 185 | 103.36
Dispatch 2 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 185 | 102.43
Dispatch 1 | 135432 AM.S-182 115 135505 WALDENTP 115 1 | LN:115:180 | T:77&78 | 168 | 185 | 100.8
| 135432 AM.S-182 115 135505 WALDENTP 115 1 Max |  |  |  |  | 125.09
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 151 | 159.36
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 151 | 159.34
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 151 | 138.49
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:39 | T:77&78 | 145 | 151 | 136.98
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 151 | 135.71
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:39 | T:77&78 | 145 | 151 | 131.46
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 120.57
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 145 | 151 | 119.43
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 118.59
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 145 | 151 | 116.72
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 145 | 151 | 116.37
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:180 | T:77&78 | 145 | 151 | 115.47
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:182N | T:77&78 | 145 | 151 | 114.89
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 145 | 151 | 113.84
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 113.78
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:182S | T:77&78 | 145 | 151 | 113.44
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:39 | DCT:230:79+80+ELM1-2 | 145 | 151 | 113.43
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:181/922 | T:77&78 | 145 | 151 | 113.43
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:39 | T:79&80 | 145 | 151 | 111.98
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 111.12
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:180 | T:77&78 | 145 | 151 | 110.48
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 145 | 151 | 110.48
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:182N | T:77&78 | 145 | 151 | 110.24
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 145 | 151 | 109.63
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:181/922 | T:77&78 | 145 | 151 | 108.87
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 145 | 151 | 108.67
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:182S | T:77&78 | 145 | 151 | 108.65
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 145 | 151 | 108.07
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 145 | 151 | 108.02
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 145 | 151 | 108.02
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 145 | 151 | 108
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:39 | DCT:230:79+80+ELM1-2 | 145 | 151 | 107.94
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 145 | 151 | 107.72
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 145 | 151 | 107.35
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:345:37S-FM-FV | T:77&78 | 145 | 151 | 107.23
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | FARMVLY - HOMERCTY | T:77&78 | 145 | 151 | 107.21
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 145 | 151 | 106.38
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:39 | T:79&80 | 145 | 151 | 106.14
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 145 | 151 | 105.46
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 145 | 151 | 105.4
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | First:Lancaster_922 | T:77&78 | 145 | 151 | 104.95
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 145 | 151 | 104.69
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 145 | 151 | 104.61
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 145 | 151 | 104.3
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 145 | 151 | 104.03
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 145 | 151 | 104.03
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | G:BLISS1 | T:77&78 | 145 | 151 | 103.98
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 145 | 151 | 103.9
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 145 | 151 | 103.64
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 145 | 151 | 103.64
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 145 | 151 | 103.64
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 145 | 151 | 103.64
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:345:37S-FM-FV | T:77&78 | 145 | 151 | 103.43
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | CAP:115:HUN | T:77&78 | 145 | 151 | 103.41
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 145 | 151 | 103.38
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | G:INDEK-OL | T:77&78 | 145 | 151 | 103.22
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | PACKARD 230/115 3TR | T:77&78 | 145 | 151 | 103.21
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | FARMVLY - HOMERCTY | T:77&78 | 145 | 151 | 103.14
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 145 | 151 | 102.73
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 145 | 151 | 102.48
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | G:JAMESGN7 | T:77&78 | 145 | 151 | 102.4
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:4 | T:77&78 | 145 | 151 | 102.1
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | LN:115:969 | T:77&78 | 145 | 151 | 102.06
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 145 | 151 | 101.66
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 145 | 151 | 101.55
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 145 | 151 | 101.49
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 145 | 151 | 101.32
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 145 | 151 | 101.32
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 145 | 151 | 101.32
Dispatch 2 | 135433 AMHST-38 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 145 | 151 | 101.32
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 145 | 151 | 100.74
Dispatch 1 | 135433 AMHST-38 115 135472 S129-38 115 1 | First:Lancaster_922 | T:77&78 | 145 | 151 | 100.56
| 135433 AMHST-38 115 135472 S129-38 115 1 Max |  |  |  |  | 159.36
Dispatch 1 | 135433 AMHST-38 115 135477 S140-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 132.92
Dispatch 2 | 135433 AMHST-38 115 135477 S140-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 132.88
Dispatch 2 | 135433 AMHST-38 115 135477 S140-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 115.49
Dispatch 2 | 135433 AMHST-38 115 135477 S140-38 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 114.24
Dispatch 1 | 135433 AMHST-38 115 135477 S140-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 113.18
Dispatch 1 | 135433 AMHST-38 115 135477 S140-38 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 109.64
Dispatch 2 | 135433 AMHST-38 115 135477 S140-38 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.55
| 135433 AMHST-38 115 135477 S140-38 115 1 Max |  |  |  |  | 132.92
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 151 | 158.33
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 151 | 158.3
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 151 | 137.64
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:38 | T:77&78 | 145 | 151 | 136.72
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 151 | 134.88
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:38 | T:77&78 | 145 | 151 | 131.21
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 119.79
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 145 | 151 | 118.67
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 117.82
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 145 | 151 | 115.98
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 145 | 151 | 115.61
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:180 | T:77&78 | 145 | 151 | 114.73
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:182N | T:77&78 | 145 | 151 | 114.13
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 145 | 151 | 113.2
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 145 | 151 | 113.08
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 113.02
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:182S | T:77&78 | 145 | 151 | 112.67
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:181/922 | T:77&78 | 145 | 151 | 112.47
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:38 | T:79&80 | 145 | 151 | 111.74
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 110.38
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:180 | T:77&78 | 145 | 151 | 109.76
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 145 | 151 | 109.73
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:182N | T:77&78 | 145 | 151 | 109.5
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 145 | 151 | 108.84
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:181/922 | T:77&78 | 145 | 151 | 107.93
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 145 | 151 | 107.92
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:182S | T:77&78 | 145 | 151 | 107.91
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 145 | 151 | 107.75
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 145 | 151 | 107.33
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 145 | 151 | 107.24
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 145 | 151 | 107.24
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 145 | 151 | 107.21
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 145 | 151 | 106.98
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 145 | 151 | 106.61
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:345:37S-FM-FV | T:77&78 | 145 | 151 | 106.45
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | FARMVLY - HOMERCTY | T:77&78 | 145 | 151 | 106.43
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:38 | T:79&80 | 145 | 151 | 105.97
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 145 | 151 | 105.65
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 145 | 151 | 104.68
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 145 | 151 | 104.64
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | First:Lancaster_922 | T:77&78 | 145 | 151 | 104.11
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 145 | 151 | 103.91
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 145 | 151 | 103.87
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 145 | 151 | 103.57
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | G:BLISS1 | T:77&78 | 145 | 151 | 103.27
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 145 | 151 | 103.26
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 145 | 151 | 103.26
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 145 | 151 | 103.13
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 145 | 151 | 102.92
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 145 | 151 | 102.88
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 145 | 151 | 102.88
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 145 | 151 | 102.88
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | CAP:115:HUN | T:77&78 | 145 | 151 | 102.72
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:345:37S-FM-FV | T:77&78 | 145 | 151 | 102.66
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 145 | 151 | 102.66
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | G:INDEK-OL | T:77&78 | 145 | 151 | 102.5
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | PACKARD 230/115 3TR | T:77&78 | 145 | 151 | 102.48
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | FARMVLY - HOMERCTY | T:77&78 | 145 | 151 | 102.38
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 145 | 151 | 102.01
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 145 | 151 | 101.78
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | G:JAMESGN7 | T:77&78 | 145 | 151 | 101.69
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | LN:115:4 | T:77&78 | 145 | 151 | 101.39
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 145 | 151 | 100.93
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 145 | 151 | 100.82
Dispatch 1 | 135434 AMHST-39 115 135473 S129-39 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 145 | 151 | 100.74
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 145 | 151 | 100.62
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 145 | 151 | 100.62
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 145 | 151 | 100.62
Dispatch 2 | 135434 AMHST-39 115 135473 S129-39 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 145 | 151 | 100.62
| 135434 AMHST-39 115 135473 S129-39 115 1 Max |  |  |  |  | 158.33
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 151 | 158.29
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 151 | 158.25
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 151 | 137.58
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:38 | T:77&78 | 145 | 151 | 136.67
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 151 | 134.83
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:38 | T:77&78 | 145 | 151 | 131.17
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 119.74
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 145 | 151 | 118.61
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 117.77
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 145 | 151 | 115.92
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 145 | 151 | 115.56
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:180 | T:77&78 | 145 | 151 | 114.67
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:182N | T:77&78 | 145 | 151 | 114.08
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 145 | 151 | 113.16
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 145 | 151 | 113.04
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 112.96
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:182S | T:77&78 | 145 | 151 | 112.61
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:181/922 | T:77&78 | 145 | 151 | 112.42
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:38 | T:79&80 | 145 | 151 | 111.7
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 110.32
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:180 | T:77&78 | 145 | 151 | 109.71
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 145 | 151 | 109.68
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:182N | T:77&78 | 145 | 151 | 109.45
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 145 | 151 | 108.82
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:181/922 | T:77&78 | 145 | 151 | 107.89
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 145 | 151 | 107.87
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:182S | T:77&78 | 145 | 151 | 107.85
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 145 | 151 | 107.71
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 145 | 151 | 107.27
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 145 | 151 | 107.2
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 145 | 151 | 107.2
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 145 | 151 | 107.17
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 145 | 151 | 106.93
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 145 | 151 | 106.56
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:345:37S-FM-FV | T:77&78 | 145 | 151 | 106.43
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | FARMVLY - HOMERCTY | T:77&78 | 145 | 151 | 106.38
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:38 | T:79&80 | 145 | 151 | 105.93
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 145 | 151 | 105.59
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 145 | 151 | 104.66
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 145 | 151 | 104.6
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | First:Lancaster_922 | T:77&78 | 145 | 151 | 104.05
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 145 | 151 | 103.9
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 145 | 151 | 103.82
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 145 | 151 | 103.52
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 145 | 151 | 103.23
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 145 | 151 | 103.23
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | G:BLISS1 | T:77&78 | 145 | 151 | 103.21
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 145 | 151 | 103.09
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 145 | 151 | 102.87
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 145 | 151 | 102.86
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 145 | 151 | 102.86
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 145 | 151 | 102.86
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:345:37S-FM-FV | T:77&78 | 145 | 151 | 102.65
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | CAP:115:HUN | T:77&78 | 145 | 151 | 102.63
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 145 | 151 | 102.61
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | G:INDEK-OL | T:77&78 | 145 | 151 | 102.45
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | PACKARD 230/115 3TR | T:77&78 | 145 | 151 | 102.43
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | FARMVLY - HOMERCTY | T:77&78 | 145 | 151 | 102.33
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 145 | 151 | 101.95
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 145 | 151 | 101.73
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | G:JAMESGN7 | T:77&78 | 145 | 151 | 101.64
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | LN:115:4 | T:77&78 | 145 | 151 | 101.34
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 145 | 151 | 100.9
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 145 | 151 | 100.78
Dispatch 1 | 135434 AMHST-39 115 135478 S140-39 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 145 | 151 | 100.7
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 145 | 151 | 100.56
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 145 | 151 | 100.56
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 145 | 151 | 100.56
Dispatch 2 | 135434 AMHST-39 115 135478 S140-39 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 145 | 151 | 100.56
| 135434 AMHST-39 115 135478 S140-39 115 1 Max |  |  |  |  | 158.29
Dispatch 1 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 283 | NConv
Dispatch 1 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 283 | NConv
Dispatch 1 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 283 | NConv
Dispatch 1 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 283 | NConv
Dispatch 1 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 283 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 283 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 283 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 283 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 283 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 283 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | T:77&78 | 239 | 283 | 119.81
Dispatch 1 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | T:77&78 | 239 | 283 | 115.66
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 239 | 283 | 109.88
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | T:79&80 | 239 | 283 | 109.23
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | Base Case | 239 | 283 | 107.89
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | SB:NIAW230_2014 | 239 | 283 | 106.67
Dispatch 1 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 239 | 283 | 105.69
Dispatch 1 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | T:79&80 | 239 | 283 | 104.88
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | NIAGARA 230/115 2TR | 239 | 283 | 104.82
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | TB:2/1:NI2 | 239 | 283 | 104.82
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | TB:2/1:NI2 | LN:115:130 | 239 | 283 | 104.71
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAGARA 230/115 2TR | LN:115:130 | 239 | 283 | 104.71
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | SB:PA230_R3430 | 239 | 283 | 102.16
Dispatch 1 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | Base Case | 239 | 283 | 101.49
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 239 | 283 | 101.26
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | T:61&64 | 239 | 283 | 101.09
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 239 | 283 | 100.94
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 239 | 283 | 100.72
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | SB:ROBI230 | 239 | 283 | 100.21
| 135435 SUMIT PK 115 135454 MLPN-129 115 1 Max |  |  |  |  | 119.81
Dispatch 1 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 298 | NConv
Dispatch 1 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 1 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 298 | NConv
Dispatch 1 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 298 | NConv
Dispatch 1 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 298 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 298 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 298 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
| 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 139 | 163 | NConv
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 139 | 163 | NConv
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 139 | 163 | NConv
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 139 | 163 | NConv
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 139 | 163 | NConv
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 139 | 163 | NConv
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 163 | NConv
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 139 | 163 | NConv
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 139 | 163 | NConv
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 139 | 163 | 143.3
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 139 | 163 | 140.29
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 139 | 163 | 132.34
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 139 | 163 | 128.09
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:180 | T:77&78 | 139 | 163 | 123.56
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 139 | 163 | 122.82
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 139 | 163 | 119.13
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:182S | T:77&78 | 139 | 163 | 118.81
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 139 | 163 | 118.68
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:180 | T:77&78 | 139 | 163 | 117.81
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:195 | T:77&78 | 139 | 163 | 117.32
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 139 | 163 | 116.99
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | FARMVLY - HOMERCTY | T:77&78 | 139 | 163 | 116.42
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 139 | 163 | 116.35
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:191 | T:77&78 | 139 | 163 | 116.31
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 139 | 163 | 116.26
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:192 | T:77&78 | 139 | 163 | 116.17
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 139 | 163 | 115.95
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 139 | 163 | 115.95
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | TB:2/1:PK3 | T:77&78 | 139 | 163 | 115.8
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 139 | 163 | 115.71
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:182N | T:77&78 | 139 | 163 | 115.66
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 139 | 163 | 115.65
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 139 | 163 | 115.54
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 139 | 163 | 114.42
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 139 | 163 | 113.88
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV | T:77&78 | 139 | 163 | 113.77
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 139 | 163 | 113.51
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 139 | 163 | 113.44
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:38 | T:77&78 | 139 | 163 | 113.21
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 139 | 163 | 113.15
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:182S | T:77&78 | 139 | 163 | 112.96
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:39 | T:77&78 | 139 | 163 | 112.64
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 139 | 163 | 112.45
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:195 | T:77&78 | 139 | 163 | 112.36
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 139 | 163 | 112.21
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 139 | 163 | 112
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 139 | 163 | 111.81
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:191 | T:77&78 | 139 | 163 | 111.77
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | FARMVLY - HOMERCTY | T:77&78 | 139 | 163 | 111.71
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:192 | T:77&78 | 139 | 163 | 111.68
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 139 | 163 | 111.44
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 139 | 163 | 111.27
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 139 | 163 | 111.27
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 139 | 163 | 111.08
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 139 | 163 | 111.08
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 139 | 163 | 111.07
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 139 | 163 | 110.71
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:182N | T:77&78 | 139 | 163 | 110.54
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:101 | T:77&78 | 139 | 163 | 110.51
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:102 | T:77&78 | 139 | 163 | 110.28
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:120 | T:77&78 | 139 | 163 | 110.13
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:133 | T:77&78 | 139 | 163 | 109.76
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 139 | 163 | 109.66
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | G:BLISS1 | T:77&78 | 139 | 163 | 109.64
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:130 | T:77&78 | 139 | 163 | 109.55
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | TB:2/1:PK3 | T:77&78 | 139 | 163 | 109.51
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | G:INDEK-OL | T:77&78 | 139 | 163 | 109.49
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 139 | 163 | 109.48
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 139 | 163 | 109.35
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:129 | T:77&78 | 139 | 163 | 109.32
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 139 | 163 | 109.31
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV | T:77&78 | 139 | 163 | 109.18
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 139 | 163 | 109.07
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 139 | 163 | 109.01
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:705 NY | T:77&78 | 139 | 163 | 108.92
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | First:Lancaster_705 | T:77&78 | 139 | 163 | 108.92
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAG - KINTIGH 345 | T:77&78 | 139 | 163 | 108.67
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:180 | T:79&80 | 139 | 163 | 108.45
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 139 | 163 | 108.36
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 139 | 163 | 108.35
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 139 | 163 | 108.27
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 139 | 163 | 108.22
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:38 | T:77&78 | 139 | 163 | 108.18
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 139 | 163 | 107.73
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 139 | 163 | 107.73
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 139 | 163 | 107.73
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 139 | 163 | 107.73
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:39 | T:77&78 | 139 | 163 | 107.62
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 139 | 163 | 107.26
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 139 | 163 | 106.53
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 139 | 163 | 106.53
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 139 | 163 | 106.53
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 139 | 163 | 106.48
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:101 | T:77&78 | 139 | 163 | 105.3
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:102 | T:77&78 | 139 | 163 | 105.1
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:120 | T:77&78 | 139 | 163 | 105.01
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | G:BLISS1 | T:77&78 | 139 | 163 | 104.88
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:133 | T:77&78 | 139 | 163 | 104.8
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | G:INDEK-OL | T:77&78 | 139 | 163 | 104.71
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:130 | T:77&78 | 139 | 163 | 104.61
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 139 | 163 | 104.61
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 139 | 163 | 104.59
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | TB:2/1:ROB | T:77&78 | 139 | 163 | 104.52
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | STONYCR - WTHRS 230 | T:77&78 | 139 | 163 | 104.51
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 139 | 163 | 104.46
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:129 | T:77&78 | 139 | 163 | 104.34
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 139 | 163 | 104.3
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:705 NY | T:77&78 | 139 | 163 | 104.07
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | First:Lancaster_705 | T:77&78 | 139 | 163 | 104.07
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAG - KINTIGH 345 | T:77&78 | 139 | 163 | 104.04
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:100 | T:77&78 | 139 | 163 | 104.01
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | G:GINNA | T:77&78 | 139 | 163 | 103.94
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | GEN:115:GINNA | T:77&78 | 139 | 163 | 103.93
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 139 | 163 | 103.93
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 139 | 163 | 103.84
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:195 | T:79&80 | 139 | 163 | 103.75
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 139 | 163 | 103.64
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 139 | 163 | 103.62
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:908 NY | T:77&78 | 139 | 163 | 103.58
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 139 | 163 | 103.5
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 139 | 163 | 103.49
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 139 | 163 | 103.47
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 139 | 163 | 103.28
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 139 | 163 | 103.25
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 139 | 163 | 103.24
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | T:79&80 | 139 | 163 | 103.21
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 139 | 163 | 103.11
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | First:Lancaster_926B | T:77&78 | 139 | 163 | 103.1
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 139 | 163 | 103.03
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 139 | 163 | 103.03
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 139 | 163 | 103.03
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 139 | 163 | 103.03
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | FARMVLY - HOMERCTY | T:79&80 | 139 | 163 | 102.92
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 139 | 163 | 102.72
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:191 | T:79&80 | 139 | 163 | 102.72
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | TB:2/1:PK3 | T:79&80 | 139 | 163 | 102.71
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:180 | T:79&80 | 139 | 163 | 102.61
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:192 | T:79&80 | 139 | 163 | 102.58
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | WTHRS - MEYER 230 | T:77&78 | 139 | 163 | 102.49
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 139 | 163 | 102.41
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:182S | T:79&80 | 139 | 163 | 102.34
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | TB:3/2:FV | T:77&78 | 139 | 163 | 102.26
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | FARMVLY - FARMVLY | T:77&78 | 139 | 163 | 102.26
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:926 NY | T:77&78 | 139 | 163 | 102.24
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | CAP:115:GV1 | T:77&78 | 139 | 163 | 102.14
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | CAP:115:GV2 | T:77&78 | 139 | 163 | 102.14
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 139 | 163 | 102.01
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | GEN:345:SOMERSET | T:77&78 | 139 | 163 | 101.97
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 139 | 163 | 101.97
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | GEN:KINTIGH | T:77&78 | 139 | 163 | 101.97
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 139 | 163 | 101.81
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:182N | T:79&80 | 139 | 163 | 101.78
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 139 | 163 | 101.16
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 139 | 163 | 101.12
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 139 | 163 | 101.08
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 139 | 163 | 101.01
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 139 | 163 | 100.92
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 139 | 163 | 100.87
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 139 | 163 | 100.84
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 139 | 163 | 100.78
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 139 | 163 | 100.76
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | First:Lancaster_926A | T:77&78 | 139 | 163 | 100.72
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 139 | 163 | 100.72
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:HC-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 139 | 163 | 100.66
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | R:FV-5M_37&W-F_171 | DCT:230:79+80+ELM1-2 | 139 | 163 | 100.66
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 139 | 163 | 100.56
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:79&80 | 139 | 163 | 100.34
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 139 | 163 | 100.25
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV-HC | DCT:230:79+80+ELM1-2 | 139 | 163 | 100.03
| 135437 CLSP-181 115 135495 YNG-181 115 1 Max |  |  |  |  | 143.3
Dispatch 2 | 135438 CLSP-54 115 135439 TUNGSTEN 115 1 | LN:115:181/922 | Base Case | 129 | 182 | 100.68
Dispatch 1 | 135438 CLSP-54 115 135439 TUNGSTEN 115 1 | LN:115:181/922 | Base Case | 129 | 182 | 100.07
| 135438 CLSP-54 115 135439 TUNGSTEN 115 1 Max |  |  |  |  | 100.68
Dispatch 2 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 181 | 134.83
Dispatch 1 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 181 | 134.81
Dispatch 2 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | LN:115:38 | T:77&78 | 168 | 181 | 118.16
Dispatch 2 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 181 | 116.82
Dispatch 1 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 181 | 114.49
Dispatch 1 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | LN:115:38 | T:77&78 | 168 | 181 | 113.53
Dispatch 2 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 101.91
Dispatch 2 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 168 | 181 | 100.97
Dispatch 1 | 135441 FMC-39 115 135451 HUNTLEY1 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.27
| 135441 FMC-39 115 135451 HUNTLEY1 115 1 Max |  |  |  |  | 134.83
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 151 | 161.67
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 151 | 161.65
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:38 | T:77&78 | 145 | 151 | 141.63
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 151 | 140.03
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 151 | 137.24
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:38 | T:77&78 | 145 | 151 | 136.09
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 122.16
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 145 | 151 | 121.03
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 120.18
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 145 | 151 | 118.3
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 145 | 151 | 118.05
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 145 | 151 | 117.98
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:180 | T:77&78 | 145 | 151 | 117.05
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:38 | T:79&80 | 145 | 151 | 116.61
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:182N | T:77&78 | 145 | 151 | 116.47
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 145 | 151 | 115.45
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 115.34
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:182S | T:77&78 | 145 | 151 | 114.98
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:181/922 | T:77&78 | 145 | 151 | 114.82
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 112.68
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 145 | 151 | 112.56
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:180 | T:77&78 | 145 | 151 | 112.06
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 145 | 151 | 112.06
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:182N | T:77&78 | 145 | 151 | 111.82
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 145 | 151 | 111.36
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:38 | T:79&80 | 145 | 151 | 110.81
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:181/922 | T:77&78 | 145 | 151 | 110.27
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 145 | 151 | 110.26
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:182S | T:77&78 | 145 | 151 | 110.2
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 145 | 151 | 109.72
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 145 | 151 | 109.65
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 145 | 151 | 109.65
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 145 | 151 | 109.56
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 145 | 151 | 109.31
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:345:37S-FM-FV | T:77&78 | 145 | 151 | 108.94
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 145 | 151 | 108.92
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | FARMVLY - HOMERCTY | T:77&78 | 145 | 151 | 108.76
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 145 | 151 | 108.03
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 145 | 151 | 107.16
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 145 | 151 | 107.01
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 145 | 151 | 106.4
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | First:Lancaster_922 | T:77&78 | 145 | 151 | 106.39
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 145 | 151 | 106.2
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 145 | 151 | 105.95
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 145 | 151 | 105.65
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 145 | 151 | 105.65
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | G:BLISS1 | T:77&78 | 145 | 151 | 105.57
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 145 | 151 | 105.46
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 145 | 151 | 105.35
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 145 | 151 | 105.35
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 145 | 151 | 105.34
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 145 | 151 | 105.23
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:345:37S-FM-FV | T:77&78 | 145 | 151 | 105.12
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | CAP:115:HUN | T:77&78 | 145 | 151 | 104.99
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 145 | 151 | 104.98
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | G:INDEK-OL | T:77&78 | 145 | 151 | 104.8
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | PACKARD 230/115 3TR | T:77&78 | 145 | 151 | 104.79
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | FARMVLY - HOMERCTY | T:77&78 | 145 | 151 | 104.69
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 145 | 151 | 104.39
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 145 | 151 | 104.09
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | G:JAMESGN7 | T:77&78 | 145 | 151 | 104
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:4 | T:77&78 | 145 | 151 | 103.69
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | LN:115:969 | T:77&78 | 145 | 151 | 103.65
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 145 | 151 | 103.33
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 145 | 151 | 103.22
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 145 | 151 | 103.09
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 145 | 151 | 102.92
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 145 | 151 | 102.92
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 145 | 151 | 102.92
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 145 | 151 | 102.92
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 145 | 151 | 102.44
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | First:Lancaster_922 | T:77&78 | 145 | 151 | 102.02
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 145 | 151 | 101.58
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 145 | 151 | 101.58
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 145 | 151 | 101.58
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | G:BLISS1 | T:77&78 | 145 | 151 | 101.45
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | PACKARD 230/115 3TR | T:77&78 | 145 | 151 | 101.44
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | CAP:115:HUN | T:77&78 | 145 | 151 | 101
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 145 | 151 | 100.88
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | G:INDEK-OL | T:77&78 | 145 | 151 | 100.62
Dispatch 2 | 135441 FMC-39 115 135473 S129-39 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 145 | 151 | 100.52
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | TB:2/1:NI1 | T:77&78 | 145 | 151 | 100.36
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | NIAGARA 230/115 1TR | T:77&78 | 145 | 151 | 100.36
Dispatch 1 | 135441 FMC-39 115 135473 S129-39 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 145 | 151 | 100.03
| 135441 FMC-39 115 135473 S129-39 115 1 Max |  |  |  |  | 161.67
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 150.83
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 148.47
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 135.62
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | T:77&78 | 174 | 181 | 135.11
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 131.46
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | T:77&78 | 174 | 181 | 131.24
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | T:77&78 | 174 | 181 | 129.53
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:180 | T:77&78 | 174 | 181 | 126.8
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 174 | 181 | 126.34
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | T:77&78 | 174 | 181 | 125.77
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 122.74
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 174 | 181 | 122.28
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:180 | T:77&78 | 174 | 181 | 121.24
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:195 | T:77&78 | 174 | 181 | 120.41
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 174 | 181 | 120.3
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 174 | 181 | 120
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 174 | 181 | 119.69
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 174 | 181 | 119.52
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:191 | T:77&78 | 174 | 181 | 119.42
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 119.37
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:192 | T:77&78 | 174 | 181 | 119.28
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | T:79&80 | 174 | 181 | 119.26
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 181 | 119.26
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | TB:2/1:PK3 | T:77&78 | 174 | 181 | 118.97
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 118.91
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 181 | 118.87
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 181 | 118.87
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - HOMERCTY | T:77&78 | 174 | 181 | 118.65
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 174 | 181 | 117.82
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:345:37S-FM-FV | T:77&78 | 174 | 181 | 117.7
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 174 | 181 | 117.02
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 174 | 181 | 116.99
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 174 | 181 | 116.74
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:38 | T:77&78 | 174 | 181 | 116.55
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 181 | 116.44
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 174 | 181 | 116.31
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 174 | 181 | 116.29
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 116.05
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | T:79&80 | 174 | 181 | 116.03
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 181 | 116
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:195 | T:77&78 | 174 | 181 | 115.63
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 115.22
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:191 | T:77&78 | 174 | 181 | 115.06
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 174 | 181 | 115.02
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 174 | 181 | 115.02
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 174 | 181 | 115.02
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:192 | T:77&78 | 174 | 181 | 114.96
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 174 | 181 | 114.88
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 174 | 181 | 114.88
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 174 | 181 | 114.67
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 181 | 114.61
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 181 | 114.23
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 181 | 114.23
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - HOMERCTY | T:77&78 | 174 | 181 | 114.07
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:101 | T:77&78 | 174 | 181 | 113.88
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:102 | T:77&78 | 174 | 181 | 113.66
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | T:79&80 | 174 | 181 | 113.63
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:120 | T:77&78 | 174 | 181 | 113.5
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 174 | 181 | 113.25
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:133 | T:77&78 | 174 | 181 | 113.25
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:345:37S-FM-FV | T:77&78 | 174 | 181 | 113.13
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:130 | T:77&78 | 174 | 181 | 113.03
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:BLISS1 | T:77&78 | 174 | 181 | 112.96
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | TB:2/1:PK3 | T:77&78 | 174 | 181 | 112.9
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 174 | 181 | 112.8
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:129 | T:77&78 | 174 | 181 | 112.79
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 174 | 181 | 112.78
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:INDEK-OL | T:77&78 | 174 | 181 | 112.73
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 174 | 181 | 112.7
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 174 | 181 | 112.37
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - KINTIGH 345 | T:77&78 | 174 | 181 | 112.08
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 181 | 112.02
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 174 | 181 | 111.99
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 174 | 181 | 111.93
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 111.82
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:180 | T:79&80 | 174 | 181 | 111.8
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:38 | T:77&78 | 174 | 181 | 111.72
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 174 | 181 | 111.67
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 174 | 181 | 111.66
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 181 | 111.27
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 111.23
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 174 | 181 | 111.15
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 174 | 181 | 111.15
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 174 | 181 | 111.15
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 174 | 181 | 111.15
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | T:79&80 | 174 | 181 | 110.52
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 174 | 181 | 110.51
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 174 | 181 | 110.51
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 174 | 181 | 110.51
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 174 | 181 | 109.98
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:101 | T:77&78 | 174 | 181 | 108.86
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:102 | T:77&78 | 174 | 181 | 108.67
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:120 | T:77&78 | 174 | 181 | 108.59
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:133 | T:77&78 | 174 | 181 | 108.48
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:BLISS1 | T:77&78 | 174 | 181 | 108.4
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:130 | T:77&78 | 174 | 181 | 108.29
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 108.21
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 174 | 181 | 108.15
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:INDEK-OL | T:77&78 | 174 | 181 | 108.12
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:129 | T:77&78 | 174 | 181 | 107.98
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | STONYCR - WTHRS 230 | T:77&78 | 174 | 181 | 107.83
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - KINTIGH 345 | T:77&78 | 174 | 181 | 107.62
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | GEN:115:GINNA | T:77&78 | 174 | 181 | 107.62
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:GINNA | T:77&78 | 174 | 181 | 107.61
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:100 | T:77&78 | 174 | 181 | 107.59
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:926 NY | T:77&78 | 174 | 181 | 107.53
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 174 | 181 | 107.51
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 174 | 181 | 107.38
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 174 | 181 | 107.38
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 174 | 181 | 107.37
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 174 | 181 | 107.26
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:908 NY | T:77&78 | 174 | 181 | 107.19
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:195 | T:79&80 | 174 | 181 | 106.99
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 174 | 181 | 106.64
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 174 | 181 | 106.64
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 174 | 181 | 106.64
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 174 | 181 | 106.64
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | TB:3/2:FV | T:77&78 | 174 | 181 | 106.6
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - FARMVLY | T:77&78 | 174 | 181 | 106.6
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 174 | 181 | 106.55
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 174 | 181 | 106.49
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 106.48
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 174 | 181 | 106.35
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 106.33
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | First:Lancaster_926A | T:77&78 | 174 | 181 | 106.29
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:180 | T:79&80 | 174 | 181 | 106.19
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 174 | 181 | 106.08
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | TB:2/1:PK3 | T:79&80 | 174 | 181 | 106.01
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 174 | 181 | 106.01
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:191 | T:79&80 | 174 | 181 | 106
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | CAP:115:GV1 | T:77&78 | 174 | 181 | 105.95
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | CAP:115:GV2 | T:77&78 | 174 | 181 | 105.95
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:192 | T:79&80 | 174 | 181 | 105.86
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | GEN:345:SOMERSET | T:77&78 | 174 | 181 | 105.76
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | GEN:KINTIGH | T:77&78 | 174 | 181 | 105.76
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | WTHRS - MEYER 230 | T:77&78 | 174 | 181 | 105.74
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-FV_37&W-F_171 | T:79&80 | 174 | 181 | 105.64
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 105.35
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - HOMERCTY | T:79&80 | 174 | 181 | 105.31
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 174 | 181 | 105.27
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | B:Hunt68 | 174 | 181 | 105.06
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | T:77&80 | 174 | 181 | 105.03
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 105
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | LN:115:180 | 174 | 181 | 104.82
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:180 | LN:115:182N | 174 | 181 | 104.75
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 174 | 181 | 104.66
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 174 | 181 | 104.59
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | SB:HUNT230_R1502 | 174 | 181 | 104.43
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 104.32
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 174 | 181 | 104.24
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | SB:HUNT230_R1402 | 174 | 181 | 104.23
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | T:78&79 | 174 | 181 | 104.22
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 174 | 181 | 104.22
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 174 | 181 | 104.18
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 174 | 181 | 104.14
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:345:37S-FM-FV-HC | DCT:230:79+80+ELM1-2 | 174 | 181 | 104.12
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 174 | 181 | 104.08
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 174 | 181 | 104.07
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 174 | 181 | 104.02
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 174 | 181 | 103.97
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.83
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:FV-5M_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.83
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.68
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:79&80 | 174 | 181 | 103.56
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:345:37S-FM-FV-HC | T:79&80 | 174 | 181 | 103.41
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:926 NY | T:77&78 | 174 | 181 | 103.34
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | STONYCR - WTHRS 230 | T:77&78 | 174 | 181 | 103.34
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 174 | 181 | 103.26
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:39 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.22
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 7 | T:77&78 | 174 | 181 | 103.21
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 10 | T:77&78 | 174 | 181 | 103.19
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 11 | T:77&78 | 174 | 181 | 103.19
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 12 | T:77&78 | 174 | 181 | 103.19
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 13 | T:77&78 | 174 | 181 | 103.19
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 8 | T:77&78 | 174 | 181 | 103.19
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 9 | T:77&78 | 174 | 181 | 103.19
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 4 | T:77&78 | 174 | 181 | 103.18
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 5 | T:77&78 | 174 | 181 | 103.18
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 6 | T:77&78 | 174 | 181 | 103.18
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-SR_37&W-F_171 | T:79&80 | 174 | 181 | 103.12
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:FV-5M_37&W-F_171 | T:79&80 | 174 | 181 | 103.12
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | GEN:115:GINNA | T:77&78 | 174 | 181 | 103.08
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:GINNA | T:77&78 | 174 | 181 | 103.06
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | TB:2/1:ROB | T:77&78 | 174 | 181 | 102.94
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:38 | T:79&80 | 174 | 181 | 102.91
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 174 | 181 | 102.91
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HCWC/NWES | T:77&78 | 174 | 181 | 102.9
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:MBWC/NWES | T:77&78 | 174 | 181 | 102.9
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:345:37S-FM-FV | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.88
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | SB:HUNT230_NEW | 174 | 181 | 102.84
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | TB:2/1:NI1 | T:77&78 | 174 | 181 | 102.76
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAGARA 230/115 1TR | T:77&78 | 174 | 181 | 102.76
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 174 | 181 | 102.73
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - ELM 70 230 | T:79&80 | 174 | 181 | 102.72
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - 5MILE 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.64
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | B:Hunt68 | 174 | 181 | 102.55
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | B:Hunt67 | 174 | 181 | 102.47
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:39 | T:79&80 | 174 | 181 | 102.45
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:100 | T:77&78 | 174 | 181 | 102.44
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | T:77&80 | 174 | 181 | 102.43
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.36
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | SB:GARD230_T7-12 | 174 | 181 | 102.29
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.26
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:195 | T:79&80 | 174 | 181 | 102.26
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:345:37S-FM-FV | T:79&80 | 174 | 181 | 102.26
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.18
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:101 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.13
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | First:Lancaster_926A | T:77&78 | 174 | 181 | 102.07
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:908 NY | T:77&78 | 174 | 181 | 102.05
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_NEW | 174 | 181 | 102.04
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - 5MILE 345 | T:79&80 | 174 | 181 | 102
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | SB:HUNT230_R1502 | 174 | 181 | 101.95
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.93
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | TB:3/2:FV | T:77&78 | 174 | 181 | 101.92
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - FARMVLY | T:77&78 | 174 | 181 | 101.92
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:102 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.92
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | SB:HUNT230_R1302 | 174 | 181 | 101.92
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | SB:HUNT230_R1202 | 174 | 181 | 101.9
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:120 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.77
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | PACKARD 230/115 3TR | T:77&78 | 174 | 181 | 101.75
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | SB:HUNT230_R1402 | 174 | 181 | 101.74
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | T:78&79 | 174 | 181 | 101.74
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:191 | T:79&80 | 174 | 181 | 101.64
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.62
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:5M-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.59
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:101 | T:79&80 | 174 | 181 | 101.58
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:192 | T:79&80 | 174 | 181 | 101.54
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:182N | 174 | 181 | 101.51
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 174 | 181 | 101.46
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:182N | 174 | 181 | 101.45
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:180 | LN:115:182S | 174 | 181 | 101.38
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | GEN:345:SOMERSET | T:77&78 | 174 | 181 | 101.37
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | GEN:KINTIGH | T:77&78 | 174 | 181 | 101.37
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:102 | T:79&80 | 174 | 181 | 101.37
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | CAP:115:GV1 | T:77&78 | 174 | 181 | 101.35
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | CAP:115:GV2 | T:77&78 | 174 | 181 | 101.35
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | LN:115:180 | 174 | 181 | 101.35
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HCMB/NWES | T:77&78 | 174 | 181 | 101.26
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | WTHRS - MEYER 230 | T:77&78 | 174 | 181 | 101.24
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:120 | T:79&80 | 174 | 181 | 101.22
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | First:Lancaster_STOL_HOMER_345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.22
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 5 MILE - STOLLE 37A 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.22
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HOMERCTY - STOLLRD 37 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.22
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:BLISS1 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.22
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.17
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 174 | 181 | 101.1
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:5M-SR_37&W-F_171 | T:79&80 | 174 | 181 | 101.04
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | S:PA_HNTL77 | 174 | 181 | 101.03
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | R:HC-FV_37&W-F_171 | T:79&80 | 174 | 181 | 101.02
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:INDEK-OL | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.01
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.97
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | S:PA_HNTL78 | 174 | 181 | 100.92
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | HUNTLEY - PACKARD 78 230 | 174 | 181 | 100.92
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | HUNTLEY - PACKARD 77 230 | 174 | 181 | 100.86
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.84
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.79
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.74
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | B:STOLE230 | 174 | 181 | 100.74
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | FARMVLY - HOMERCTY | T:79&80 | 174 | 181 | 100.72
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | First:Lancaster_STOL_HOMER_345 | T:79&80 | 174 | 181 | 100.67
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | 5 MILE - STOLLE 37A 345 | T:79&80 | 174 | 181 | 100.67
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:79&80 | 174 | 181 | 100.67
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:BLISS1 | T:79&80 | 174 | 181 | 100.59
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 174 | 181 | 100.54
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.52
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:54/921 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.5
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:705 NY | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.5
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | First:Lancaster_705 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.5
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:182N | 174 | 181 | 100.46
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:133 | T:79&80 | 174 | 181 | 100.44
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | SB:HUNT230_NEW | 174 | 181 | 100.44
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:INDEK-OL | T:79&80 | 174 | 181 | 100.39
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 7 | T:77&78 | 174 | 181 | 100.34
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 4 | T:77&78 | 174 | 181 | 100.32
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 5 | T:77&78 | 174 | 181 | 100.32
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | G:NIAG. 6 | T:77&78 | 174 | 181 | 100.32
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:130 | T:79&80 | 174 | 181 | 100.23
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:54/921 | T:79&80 | 174 | 181 | 100.16
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182S | B:Hunt67 | 174 | 181 | 100.08
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | TB:2/1:PK3 | T:79&80 | 174 | 181 | 100.03
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:129 | T:79&80 | 174 | 181 | 100.03
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | FARMVLY - HOMERCTY | 174 | 181 | 100.03
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 174 | 181 | 100
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:182N | R:HC-FV_37&W-F_171 | 174 | 181 | 100
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | LN:115:705 NY | T:79&80 | 174 | 181 | 100
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | First:Lancaster_705 | T:79&80 | 174 | 181 | 100
| 135442 ECWA-181 115 135458 NI.B-181 115 1 Max |  |  |  |  | 150.83
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 149.57
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 147.22
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 134.64
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | T:77&78 | 174 | 181 | 131.02
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182S | T:77&78 | 174 | 181 | 130.67
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 130.52
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:180 | T:77&78 | 174 | 181 | 125.92
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | T:77&78 | 174 | 181 | 125.62
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 174 | 181 | 125.47
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182S | T:77&78 | 174 | 181 | 125.21
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 121.91
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 174 | 181 | 121.44
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:180 | T:77&78 | 174 | 181 | 120.42
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:195 | T:77&78 | 174 | 181 | 119.66
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 174 | 181 | 119.21
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 174 | 181 | 119.04
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 174 | 181 | 118.82
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 181 | 118.7
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:191 | T:77&78 | 174 | 181 | 118.68
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 118.57
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:192 | T:77&78 | 174 | 181 | 118.54
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 181 | 118.28
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 181 | 118.28
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | TB:2/1:PK3 | T:77&78 | 174 | 181 | 118.23
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 118.17
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - HOMERCTY | T:77&78 | 174 | 181 | 118.09
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 174 | 181 | 117.13
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV | T:77&78 | 174 | 181 | 117.05
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 174 | 181 | 116.8
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 174 | 181 | 116.44
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 174 | 181 | 116.34
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 174 | 181 | 116.04
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 181 | 115.84
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:38 | T:77&78 | 174 | 181 | 115.83
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | T:79&80 | 174 | 181 | 115.8
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 174 | 181 | 115.62
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 174 | 181 | 115.56
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182S | T:79&80 | 174 | 181 | 115.47
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 181 | 115.38
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 115.32
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:195 | T:77&78 | 174 | 181 | 114.91
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 114.5
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 174 | 181 | 114.4
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 174 | 181 | 114.4
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 174 | 181 | 114.4
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:191 | T:77&78 | 174 | 181 | 114.35
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:192 | T:77&78 | 174 | 181 | 114.26
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 174 | 181 | 114.23
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 181 | 114.09
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 174 | 181 | 114.06
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 181 | 113.68
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 181 | 113.68
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - HOMERCTY | T:77&78 | 174 | 181 | 113.56
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:101 | T:77&78 | 174 | 181 | 113.19
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:102 | T:77&78 | 174 | 181 | 112.98
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:120 | T:77&78 | 174 | 181 | 112.82
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 174 | 181 | 112.6
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:133 | T:77&78 | 174 | 181 | 112.56
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV | T:77&78 | 174 | 181 | 112.53
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:130 | T:77&78 | 174 | 181 | 112.34
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:BLISS1 | T:77&78 | 174 | 181 | 112.29
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | TB:2/1:PK3 | T:77&78 | 174 | 181 | 112.21
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 174 | 181 | 112.13
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 174 | 181 | 112.1
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:129 | T:77&78 | 174 | 181 | 112.1
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:INDEK-OL | T:77&78 | 174 | 181 | 112.08
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 174 | 181 | 112.04
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 174 | 181 | 111.74
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 174 | 181 | 111.56
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 181 | 111.47
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - KINTIGH 345 | T:77&78 | 174 | 181 | 111.43
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 174 | 181 | 111.36
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 174 | 181 | 111.31
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 111.16
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:180 | T:79&80 | 174 | 181 | 111.14
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 174 | 181 | 111.12
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:38 | T:77&78 | 174 | 181 | 111.04
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 174 | 181 | 111.04
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 181 | 110.7
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 110.54
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 174 | 181 | 110.5
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 174 | 181 | 110.5
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 174 | 181 | 110.5
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 174 | 181 | 110.5
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | T:79&80 | 174 | 181 | 110.36
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182S | T:79&80 | 174 | 181 | 109.97
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 174 | 181 | 109.94
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 174 | 181 | 109.94
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 174 | 181 | 109.94
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 174 | 181 | 109.34
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:101 | T:77&78 | 174 | 181 | 108.22
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:102 | T:77&78 | 174 | 181 | 108.03
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:120 | T:77&78 | 174 | 181 | 107.95
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:133 | T:77&78 | 174 | 181 | 107.83
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:BLISS1 | T:77&78 | 174 | 181 | 107.77
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:130 | T:77&78 | 174 | 181 | 107.64
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 107.57
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 174 | 181 | 107.53
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:INDEK-OL | T:77&78 | 174 | 181 | 107.51
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:129 | T:77&78 | 174 | 181 | 107.33
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | First:Lancaster_926B | T:77&78 | 174 | 181 | 107.32
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | STONYCR - WTHRS 230 | T:77&78 | 174 | 181 | 107.24
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - KINTIGH 345 | T:77&78 | 174 | 181 | 107.01
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | GEN:115:GINNA | T:77&78 | 174 | 181 | 106.99
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:GINNA | T:77&78 | 174 | 181 | 106.98
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:100 | T:77&78 | 174 | 181 | 106.97
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 174 | 181 | 106.94
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 174 | 181 | 106.8
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 174 | 181 | 106.78
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 174 | 181 | 106.75
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:926 NY | T:77&78 | 174 | 181 | 106.73
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 174 | 181 | 106.63
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:908 NY | T:77&78 | 174 | 181 | 106.57
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:195 | T:79&80 | 174 | 181 | 106.43
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 174 | 181 | 106.03
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 174 | 181 | 106.03
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 174 | 181 | 106.03
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 174 | 181 | 106.03
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 174 | 181 | 105.98
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 105.96
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 174 | 181 | 105.93
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 105.93
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | TB:3/2:FV | T:77&78 | 174 | 181 | 105.89
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - FARMVLY | T:77&78 | 174 | 181 | 105.89
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 174 | 181 | 105.8
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 174 | 181 | 105.62
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:180 | T:79&80 | 174 | 181 | 105.59
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 174 | 181 | 105.48
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | TB:2/1:PK3 | T:79&80 | 174 | 181 | 105.46
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:191 | T:79&80 | 174 | 181 | 105.45
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | First:Lancaster_926A | T:77&78 | 174 | 181 | 105.45
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | CAP:115:GV1 | T:77&78 | 174 | 181 | 105.31
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | CAP:115:GV2 | T:77&78 | 174 | 181 | 105.31
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:192 | T:79&80 | 174 | 181 | 105.31
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | T:79&80 | 174 | 181 | 105.26
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | WTHRS - MEYER 230 | T:77&78 | 174 | 181 | 105.21
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | GEN:345:SOMERSET | T:77&78 | 174 | 181 | 105.14
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | GEN:KINTIGH | T:77&78 | 174 | 181 | 105.14
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - HOMERCTY | T:79&80 | 174 | 181 | 104.93
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 104.83
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 174 | 181 | 104.77
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 104.5
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 174 | 181 | 104.11
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 174 | 181 | 104.04
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.82
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 174 | 181 | 103.74
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 174 | 181 | 103.67
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV-HC | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.63
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 174 | 181 | 103.62
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 174 | 181 | 103.57
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 174 | 181 | 103.51
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 174 | 181 | 103.5
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 174 | 181 | 103.48
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 174 | 181 | 103.45
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.4
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:FV-5M_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.4
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.15
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:79&80 | 174 | 181 | 103.08
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV-HC | T:79&80 | 174 | 181 | 102.92
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | STONYCR - WTHRS 230 | T:77&78 | 174 | 181 | 102.79
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-SR_37&W-F_171 | T:79&80 | 174 | 181 | 102.69
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:FV-5M_37&W-F_171 | T:79&80 | 174 | 181 | 102.69
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:39 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.68
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 174 | 181 | 102.61
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:NIAG. 7 | T:77&78 | 174 | 181 | 102.61
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:926 NY | T:77&78 | 174 | 181 | 102.6
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:NIAG. 11 | T:77&78 | 174 | 181 | 102.6
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:NIAG. 12 | T:77&78 | 174 | 181 | 102.6
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:NIAG. 13 | T:77&78 | 174 | 181 | 102.6
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:NIAG. 8 | T:77&78 | 174 | 181 | 102.6
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:NIAG. 9 | T:77&78 | 174 | 181 | 102.6
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:NIAG. 10 | T:77&78 | 174 | 181 | 102.59
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:NIAG. 4 | T:77&78 | 174 | 181 | 102.59
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:NIAG. 5 | T:77&78 | 174 | 181 | 102.59
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:NIAG. 6 | T:77&78 | 174 | 181 | 102.59
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | GEN:115:GINNA | T:77&78 | 174 | 181 | 102.48
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.47
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:GINNA | T:77&78 | 174 | 181 | 102.46
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:38 | T:79&80 | 174 | 181 | 102.39
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.39
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | TB:2/1:ROB | T:77&78 | 174 | 181 | 102.36
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 174 | 181 | 102.26
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HCWC/NWES | T:77&78 | 174 | 181 | 102.25
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:MBWC/NWES | T:77&78 | 174 | 181 | 102.25
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - 5MILE 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.2
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - ELM 70 230 | T:79&80 | 174 | 181 | 102.19
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | TB:2/1:NI1 | T:77&78 | 174 | 181 | 102.18
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAGARA 230/115 1TR | T:77&78 | 174 | 181 | 102.18
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | B:Hunt68 | 174 | 181 | 102.16
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 174 | 181 | 102.14
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | T:77&80 | 174 | 181 | 102.13
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182S | B:Hunt68 | 174 | 181 | 102
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | LN:115:180 | 174 | 181 | 101.94
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:39 | T:79&80 | 174 | 181 | 101.92
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182S | T:77&80 | 174 | 181 | 101.88
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:100 | T:77&78 | 174 | 181 | 101.87
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:180 | LN:115:182N | 174 | 181 | 101.87
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.84
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:345:37S-FM-FV | T:79&80 | 174 | 181 | 101.78
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.74
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:195 | T:79&80 | 174 | 181 | 101.74
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.7
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:101 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.62
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.58
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - 5MILE 345 | T:79&80 | 174 | 181 | 101.58
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | SB:HUNT230_R1502 | 174 | 181 | 101.54
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_NEW | 174 | 181 | 101.53
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:908 NY | T:77&78 | 174 | 181 | 101.48
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:102 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.41
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182S | SB:HUNT230_R1502 | 174 | 181 | 101.41
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | SB:HUNT230_R1402 | 174 | 181 | 101.34
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | T:78&79 | 174 | 181 | 101.34
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | First:Lancaster_926A | T:77&78 | 174 | 181 | 101.28
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.27
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:120 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.26
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | TB:3/2:FV | T:77&78 | 174 | 181 | 101.23
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - FARMVLY | T:77&78 | 174 | 181 | 101.23
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182S | SB:HUNT230_R1402 | 174 | 181 | 101.2
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182S | T:78&79 | 174 | 181 | 101.2
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | PACKARD 230/115 3TR | T:77&78 | 174 | 181 | 101.19
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:191 | T:79&80 | 174 | 181 | 101.13
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:5M-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.13
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:101 | T:79&80 | 174 | 181 | 101.08
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:192 | T:79&80 | 174 | 181 | 101.03
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:102 | T:79&80 | 174 | 181 | 100.87
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:180 | LN:115:182S | 174 | 181 | 100.86
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182S | LN:115:180 | 174 | 181 | 100.83
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 174 | 181 | 100.8
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | GEN:345:SOMERSET | T:77&78 | 174 | 181 | 100.77
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | GEN:KINTIGH | T:77&78 | 174 | 181 | 100.77
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | CAP:115:GV1 | T:77&78 | 174 | 181 | 100.75
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | CAP:115:GV2 | T:77&78 | 174 | 181 | 100.75
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | WTHRS - MEYER 230 | T:77&78 | 174 | 181 | 100.75
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | First:Lancaster_STOL_HOMER_345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.75
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 5 MILE - STOLLE 37A 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.75
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HOMERCTY - STOLLRD 37 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.75
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:BLISS1 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.73
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:120 | T:79&80 | 174 | 181 | 100.72
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HC-FV_37&W-F_171 | T:79&80 | 174 | 181 | 100.68
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.66
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:HCMB/NWES | T:77&78 | 174 | 181 | 100.6
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | R:5M-SR_37&W-F_171 | T:79&80 | 174 | 181 | 100.59
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:INDEK-OL | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.53
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.46
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 174 | 181 | 100.44
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | FARMVLY - HOMERCTY | T:79&80 | 174 | 181 | 100.39
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.33
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.32
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.23
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | First:Lancaster_STOL_HOMER_345 | T:79&80 | 174 | 181 | 100.21
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | 5 MILE - STOLLE 37A 345 | T:79&80 | 174 | 181 | 100.21
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | HOMERCTY - STOLLRD 37 345 | T:79&80 | 174 | 181 | 100.21
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:705 NY | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.13
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | First:Lancaster_705 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.13
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:54/921 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.11
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | G:BLISS1 | T:79&80 | 174 | 181 | 100.11
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 174 | 181 | 100.08
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.06
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | LN:115:182N | SB:HUNT230_NEW | 174 | 181 | 100.01
| 135442 ECWA-181 115 135495 YNG-181 115 1 Max |  |  |  |  | 149.57
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 153.31
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 150.57
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 138.36
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 133.92
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | T:77&78 | 174 | 181 | 130.1
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 174 | 181 | 127.1
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:180 | T:77&78 | 174 | 181 | 126.69
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | T:77&78 | 174 | 181 | 123.9
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 174 | 181 | 122.85
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 122.69
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:180 | T:77&78 | 174 | 181 | 120.26
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 174 | 181 | 119
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:195 | T:77&78 | 174 | 181 | 118.91
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 118.86
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:191 | T:77&78 | 174 | 181 | 117.77
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:192 | T:77&78 | 174 | 181 | 117.62
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | TB:2/1:PK3 | T:77&78 | 174 | 181 | 117.25
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 117.13
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 174 | 181 | 116.05
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 174 | 181 | 114.74
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:38 | T:77&78 | 174 | 181 | 114.51
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 174 | 181 | 114.34
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 114.26
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 174 | 181 | 114.2
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | First:Lancaster_922 | T:77&78 | 174 | 181 | 113.75
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 174 | 181 | 113.51
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:195 | T:77&78 | 174 | 181 | 113.49
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 174 | 181 | 113.19
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 113.09
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:191 | T:77&78 | 174 | 181 | 112.81
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 174 | 181 | 112.72
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:192 | T:77&78 | 174 | 181 | 112.69
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 181 | 112.62
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 181 | 112.34
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 181 | 112.34
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 174 | 181 | 112.21
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | FARMVLY - HOMERCTY | T:77&78 | 174 | 181 | 112.04
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:345:37S-FM-FV | T:77&78 | 174 | 181 | 111.28
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:101 | T:77&78 | 174 | 181 | 111.13
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | T:79&80 | 174 | 181 | 110.89
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:102 | T:77&78 | 174 | 181 | 110.88
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 174 | 181 | 110.77
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:120 | T:77&78 | 174 | 181 | 110.68
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:133 | T:77&78 | 174 | 181 | 110.66
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:130 | T:77&78 | 174 | 181 | 110.47
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 181 | 110.42
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | TB:2/1:PK3 | T:77&78 | 174 | 181 | 110.37
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:129 | T:77&78 | 174 | 181 | 110.15
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 174 | 181 | 109.77
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | G:BLISS1 | T:77&78 | 174 | 181 | 109.77
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 174 | 181 | 109.15
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | G:INDEK-OL | T:77&78 | 174 | 181 | 109.12
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 174 | 181 | 109.1
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 181 | 109.06
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:38 | T:77&78 | 174 | 181 | 108.95
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 108.7
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 174 | 181 | 108.68
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAG - KINTIGH 345 | T:77&78 | 174 | 181 | 108.64
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 108.56
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 174 | 181 | 108.23
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | First:Lancaster_922 | T:77&78 | 174 | 181 | 108.11
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 174 | 181 | 107.67
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 174 | 181 | 107.67
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 174 | 181 | 107.67
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 174 | 181 | 107.67
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 174 | 181 | 107.54
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 174 | 181 | 107.46
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 181 | 107.33
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:180 | T:79&80 | 174 | 181 | 107.26
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 174 | 181 | 107.23
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 174 | 181 | 107.13
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 181 | 107.03
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 181 | 107.03
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | FARMVLY - HOMERCTY | T:77&78 | 174 | 181 | 106.79
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 174 | 181 | 106.14
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 174 | 181 | 106.02
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:345:37S-FM-FV | T:77&78 | 174 | 181 | 105.92
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:101 | T:77&78 | 174 | 181 | 105.38
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 181 | 105.24
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:133 | T:77&78 | 174 | 181 | 105.21
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:102 | T:77&78 | 174 | 181 | 105.15
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:120 | T:77&78 | 174 | 181 | 105.03
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:130 | T:77&78 | 174 | 181 | 105.03
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:129 | T:77&78 | 174 | 181 | 104.69
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 104.69
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | T:79&80 | 174 | 181 | 104.54
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | G:BLISS1 | T:77&78 | 174 | 181 | 104.54
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | TB:2/1:MEYER | T:77&78 | 174 | 181 | 104.37
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | TB:2/1:ROB | T:77&78 | 174 | 181 | 104.2
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | GEN:115:GINNA | T:77&78 | 174 | 181 | 103.96
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 174 | 181 | 103.95
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | G:GINNA | T:77&78 | 174 | 181 | 103.94
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 174 | 181 | 103.93
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | G:INDEK-OL | T:77&78 | 174 | 181 | 103.87
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 174 | 181 | 103.86
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 181 | 103.58
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:100 | T:77&78 | 174 | 181 | 103.58
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAG - KINTIGH 345 | T:77&78 | 174 | 181 | 103.54
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 174 | 181 | 103.45
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:908 NY | T:77&78 | 174 | 181 | 103.09
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | STONYCR - WTHRS 230 | T:77&78 | 174 | 181 | 103.02
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | CAP:115:GV1 | T:77&78 | 174 | 181 | 102.67
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | CAP:115:GV2 | T:77&78 | 174 | 181 | 102.67
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 174 | 181 | 102.5
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 174 | 181 | 102.5
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 174 | 181 | 102.5
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 174 | 181 | 102.5
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.35
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.26
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | GEN:345:SOMERSET | T:77&78 | 174 | 181 | 102.01
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | GEN:KINTIGH | T:77&78 | 174 | 181 | 102.01
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 174 | 181 | 101.94
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 174 | 181 | 101.92
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 174 | 181 | 101.75
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:195 | T:79&80 | 174 | 181 | 101.44
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.16
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.08
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.92
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:180 | T:79&80 | 174 | 181 | 100.65
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 174 | 181 | 100.63
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | TB:2/1:PK3 | T:79&80 | 174 | 181 | 100.32
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:191 | T:79&80 | 174 | 181 | 100.3
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 174 | 181 | 100.24
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | R:HCWC/NWES | T:77&78 | 174 | 181 | 100.24
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | R:MBWC/NWES | T:77&78 | 174 | 181 | 100.24
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | LN:115:192 | T:79&80 | 174 | 181 | 100.14
| 135443 ECWA-182 115 135459 NI.B-182 115 1 Max |  |  |  |  | 153.31
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 153.65
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 150.87
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 138.79
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 134.32
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:181/922 | T:77&78 | 174 | 181 | 129.59
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 174 | 181 | 127.43
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:180 | T:77&78 | 174 | 181 | 127.04
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:181/922 | T:77&78 | 174 | 181 | 123.39
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 174 | 181 | 123.17
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 122.97
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:180 | T:77&78 | 174 | 181 | 120.56
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 174 | 181 | 119.23
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:195 | T:77&78 | 174 | 181 | 119.14
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 119.11
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:191 | T:77&78 | 174 | 181 | 117.99
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:192 | T:77&78 | 174 | 181 | 117.83
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | TB:2/1:PK3 | T:77&78 | 174 | 181 | 117.47
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 117.35
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 174 | 181 | 116.2
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | First:Lancaster_922 | T:77&78 | 174 | 181 | 115.74
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 174 | 181 | 114.94
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:38 | T:77&78 | 174 | 181 | 114.71
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 174 | 181 | 114.49
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 114.47
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 174 | 181 | 114.38
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:195 | T:77&78 | 174 | 181 | 113.68
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 174 | 181 | 113.65
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 113.28
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 174 | 181 | 113.27
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:191 | T:77&78 | 174 | 181 | 112.99
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:192 | T:77&78 | 174 | 181 | 112.87
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 174 | 181 | 112.86
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 181 | 112.65
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 181 | 112.37
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 181 | 112.37
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | FARMVLY - HOMERCTY | T:77&78 | 174 | 181 | 112.08
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 174 | 181 | 111.71
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:345:37S-FM-FV | T:77&78 | 174 | 181 | 111.36
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:101 | T:77&78 | 174 | 181 | 111.3
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:102 | T:77&78 | 174 | 181 | 111.04
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 174 | 181 | 110.88
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:120 | T:77&78 | 174 | 181 | 110.84
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:133 | T:77&78 | 174 | 181 | 110.83
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:130 | T:77&78 | 174 | 181 | 110.64
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | TB:2/1:PK3 | T:77&78 | 174 | 181 | 110.54
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 181 | 110.47
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:181/922 | T:79&80 | 174 | 181 | 110.39
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:129 | T:77&78 | 174 | 181 | 110.32
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | First:Lancaster_922 | T:77&78 | 174 | 181 | 109.96
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 174 | 181 | 109.92
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | G:BLISS1 | T:77&78 | 174 | 181 | 109.92
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 174 | 181 | 109.28
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | G:INDEK-OL | T:77&78 | 174 | 181 | 109.25
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 174 | 181 | 109.21
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 181 | 109.12
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:38 | T:77&78 | 174 | 181 | 109.1
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 108.86
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 174 | 181 | 108.85
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAG - KINTIGH 345 | T:77&78 | 174 | 181 | 108.78
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 108.7
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 174 | 181 | 108.33
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 174 | 181 | 107.8
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 174 | 181 | 107.8
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 174 | 181 | 107.8
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 174 | 181 | 107.8
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 174 | 181 | 107.58
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 174 | 181 | 107.56
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:180 | T:79&80 | 174 | 181 | 107.41
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 181 | 107.32
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 174 | 181 | 107.3
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 174 | 181 | 107.19
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 181 | 107.03
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 181 | 107.03
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | FARMVLY - HOMERCTY | T:77&78 | 174 | 181 | 106.79
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 174 | 181 | 106.13
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:345:37S-FM-FV | T:77&78 | 174 | 181 | 105.96
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 174 | 181 | 105.63
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:101 | T:77&78 | 174 | 181 | 105.5
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:133 | T:77&78 | 174 | 181 | 105.34
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:102 | T:77&78 | 174 | 181 | 105.27
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 181 | 105.26
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:130 | T:77&78 | 174 | 181 | 105.16
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:120 | T:77&78 | 174 | 181 | 105.15
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:129 | T:77&78 | 174 | 181 | 104.82
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 104.82
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | G:BLISS1 | T:77&78 | 174 | 181 | 104.65
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | TB:2/1:MEYER | T:77&78 | 174 | 181 | 104.48
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | TB:2/1:ROB | T:77&78 | 174 | 181 | 104.31
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | GEN:115:GINNA | T:77&78 | 174 | 181 | 104.07
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | G:GINNA | T:77&78 | 174 | 181 | 104.06
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:181/922 | T:79&80 | 174 | 181 | 104.04
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 174 | 181 | 104.04
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 174 | 181 | 103.99
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 174 | 181 | 103.99
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | G:INDEK-OL | T:77&78 | 174 | 181 | 103.97
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:100 | T:77&78 | 174 | 181 | 103.69
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAG - KINTIGH 345 | T:77&78 | 174 | 181 | 103.64
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 181 | 103.6
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 174 | 181 | 103.58
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:908 NY | T:77&78 | 174 | 181 | 103.19
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | STONYCR - WTHRS 230 | T:77&78 | 174 | 181 | 103.1
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | CAP:115:GV1 | T:77&78 | 174 | 181 | 102.8
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | CAP:115:GV2 | T:77&78 | 174 | 181 | 102.8
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 174 | 181 | 102.59
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 174 | 181 | 102.59
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 174 | 181 | 102.59
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 174 | 181 | 102.59
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.47
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.31
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | GEN:345:SOMERSET | T:77&78 | 174 | 181 | 102.11
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | GEN:KINTIGH | T:77&78 | 174 | 181 | 102.11
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 174 | 181 | 101.97
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 174 | 181 | 101.94
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 174 | 181 | 101.84
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:195 | T:79&80 | 174 | 181 | 101.48
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.2
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.12
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.96
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 174 | 181 | 100.78
Dispatch 1 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:180 | T:79&80 | 174 | 181 | 100.74
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 174 | 181 | 100.39
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | R:HCWC/NWES | T:77&78 | 174 | 181 | 100.39
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | R:MBWC/NWES | T:77&78 | 174 | 181 | 100.39
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | TB:2/1:PK3 | T:79&80 | 174 | 181 | 100.35
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:191 | T:79&80 | 174 | 181 | 100.32
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | LN:115:192 | T:79&80 | 174 | 181 | 100.16
| 135443 ECWA-182 115 135496 YNG-182 115 1 Max |  |  |  |  | 153.65
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:141 | T:73&74 | 88 | 101 | 122.26
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:141 | T:73&74 | 88 | 101 | 121.48
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:141 | SB:DUNK230_R1312 | 88 | 101 | 121.06
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:141 | SB:DUNK230_R1312 | 88 | 101 | 120.56
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 110.4
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 109.74
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 109.36
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 109.36
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 108.69
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 108.69
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:149 | T:73&74 | 88 | 101 | 107.82
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:149 | T:73&74 | 88 | 101 | 107.19
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 106.85
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 106.22
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 106.08
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 101 | 105.48
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 105.42
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | LFYTE - CLARKCRNS 36A 345 | T:73&74 | 88 | 101 | 105.05
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:73&74 | 88 | 101 | 104.96
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 101 | 104.79
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | LFYTE - CLARKCRNS 36A 345 | T:73&74 | 88 | 101 | 104.44
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:73&74 | 88 | 101 | 104.36
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:345:37S-FM-FV-HC | T:73&74 | 88 | 101 | 104.17
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | MEYER - CANDQUA 60 230 | T:73&74 | 88 | 101 | 103.41
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | HILLSIDE 230/115 4TR | T:73&74 | 88 | 101 | 103.32
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:345:37S-FM-FV-HC | T:73&74 | 88 | 101 | 103.11
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | SOMERSET - NEWROCH 1 345 | T:73&74 | 88 | 101 | 103.02
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | MEYER - CANDQUA 60 230 | T:73&74 | 88 | 101 | 102.77
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | HILLSIDE 230/115 4TR | T:73&74 | 88 | 101 | 102.75
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | 4 MILE - ERIE SE 230 | T:73&74 | 88 | 101 | 102.64
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:167 | T:73&74 | 88 | 101 | 102.6
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | SOMERSET - NEWROCH 1 345 | T:73&74 | 88 | 101 | 102.57
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | SHLDON - STONYCR 230 | T:73&74 | 88 | 101 | 102.57
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | G:JAMESGN7 | T:73&74 | 88 | 101 | 102.47
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | 4 MILE - ERIE SE 230 | T:73&74 | 88 | 101 | 102.07
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:167 | T:73&74 | 88 | 101 | 101.95
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | SHLDON - STONYCR 230 | T:73&74 | 88 | 101 | 101.91
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | G:JAMESGN7 | T:73&74 | 88 | 101 | 101.84
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | STNYRDG - HILLSIDE 68B 230 | T:73&74 | 88 | 101 | 101.38
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:153 | T:73&74 | 88 | 101 | 100.92
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | STNYRDG - HILLSIDE 68B 230 | T:73&74 | 88 | 101 | 100.75
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | R:5M-SR_37&W-F_171 | T:73&74 | 88 | 101 | 100.74
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:154 | T:73&74 | 88 | 101 | 100.64
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | First:Lancaster_STOL_HOMER_345 | T:73&74 | 88 | 101 | 100.3
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | 5 MILE - STOLLE 37A 345 | T:73&74 | 88 | 101 | 100.3
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | HOMERCTY - STOLLRD 37 345 | T:73&74 | 88 | 101 | 100.29
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:153 | T:73&74 | 88 | 101 | 100.28
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | G:INDEK-OL | T:73&74 | 88 | 101 | 100.22
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:705 NY | T:73&74 | 88 | 101 | 100.11
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | First:Lancaster_705 | T:73&74 | 88 | 101 | 100.11
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | LN:115:154 | T:73&74 | 88 | 101 | 100
| 135445 FORD-142 115 135484 S55-142 115 1 Max |  |  |  |  | 122.26
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 163.45
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 160.81
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | T:77&78 | 174 | 181 | 145.05
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 144.35
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 139.82
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | T:77&78 | 174 | 181 | 138.78
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 174 | 181 | 133.19
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:180 | T:77&78 | 174 | 181 | 132.54
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 128.92
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 174 | 181 | 128.84
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 174 | 181 | 126.92
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:180 | T:77&78 | 174 | 181 | 126.18
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | T:79&80 | 174 | 181 | 125.66
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 174 | 181 | 125.35
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 125.18
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:195 | T:77&78 | 174 | 181 | 125.06
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:191 | T:77&78 | 174 | 181 | 123.94
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:192 | T:77&78 | 174 | 181 | 123.79
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | TB:2/1:PK3 | T:77&78 | 174 | 181 | 123.42
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 123.36
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 174 | 181 | 122.66
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 174 | 181 | 121.2
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 174 | 181 | 120.93
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 174 | 181 | 120.83
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:38 | T:77&78 | 174 | 181 | 120.72
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 174 | 181 | 120.61
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 174 | 181 | 120.54
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 120.43
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 174 | 181 | 119.98
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:195 | T:77&78 | 174 | 181 | 119.66
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 181 | 119.39
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 181 | 119.38
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 181 | 119.38
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | T:79&80 | 174 | 181 | 119.32
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 174 | 181 | 119.31
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 174 | 181 | 119.17
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:191 | T:77&78 | 174 | 181 | 119
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:192 | T:77&78 | 174 | 181 | 118.89
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | FARMVLY - HOMERCTY | T:77&78 | 174 | 181 | 118.74
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:345:37S-FM-FV | T:77&78 | 174 | 181 | 118.57
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 174 | 181 | 117.41
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:101 | T:77&78 | 174 | 181 | 117.41
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 181 | 117.23
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:102 | T:77&78 | 174 | 181 | 117.15
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:120 | T:77&78 | 174 | 181 | 116.95
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:133 | T:77&78 | 174 | 181 | 116.93
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:130 | T:77&78 | 174 | 181 | 116.71
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | TB:2/1:PK3 | T:77&78 | 174 | 181 | 116.57
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 181 | 116.44
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:129 | T:77&78 | 174 | 181 | 116.39
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 174 | 181 | 116.13
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:BLISS1 | T:77&78 | 174 | 181 | 116.07
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | First:Lancaster_922 | T:77&78 | 174 | 181 | 116.04
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 174 | 181 | 115.74
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 174 | 181 | 115.57
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 174 | 181 | 115.57
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 174 | 181 | 115.57
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 174 | 181 | 115.55
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:INDEK-OL | T:77&78 | 174 | 181 | 115.46
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:38 | T:77&78 | 174 | 181 | 115.22
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - KINTIGH 345 | T:77&78 | 174 | 181 | 115.01
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:39 | T:77&78 | 174 | 181 | 114.93
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 174 | 181 | 114.89
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 114.86
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 174 | 181 | 114.83
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 174 | 181 | 114.74
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 174 | 181 | 114.16
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 174 | 181 | 114.12
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 174 | 181 | 114.06
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 174 | 181 | 114.04
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 174 | 181 | 114.04
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 174 | 181 | 114.01
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 174 | 181 | 114.01
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 174 | 181 | 114.01
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 174 | 181 | 114.01
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 174 | 181 | 113.95
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | FARMVLY - HOMERCTY | T:77&78 | 174 | 181 | 113.52
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:180 | T:79&80 | 174 | 181 | 113.49
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:345:37S-FM-FV | T:77&78 | 174 | 181 | 113.22
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 174 | 181 | 112.43
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 174 | 181 | 112.08
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:101 | T:77&78 | 174 | 181 | 111.71
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:133 | T:77&78 | 174 | 181 | 111.51
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:102 | T:77&78 | 174 | 181 | 111.48
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:120 | T:77&78 | 174 | 181 | 111.37
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:130 | T:77&78 | 174 | 181 | 111.32
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 110.97
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:129 | T:77&78 | 174 | 181 | 110.95
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 174 | 181 | 110.95
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:BLISS1 | T:77&78 | 174 | 181 | 110.9
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | TB:2/1:MEYER | T:77&78 | 174 | 181 | 110.72
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | First:Lancaster_922 | T:77&78 | 174 | 181 | 110.68
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | TB:2/1:ROB | T:77&78 | 174 | 181 | 110.56
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 174 | 181 | 110.45
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 174 | 181 | 110.4
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | GEN:115:GINNA | T:77&78 | 174 | 181 | 110.33
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:GINNA | T:77&78 | 174 | 181 | 110.3
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:INDEK-OL | T:77&78 | 174 | 181 | 110.25
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 174 | 181 | 110.24
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 174 | 181 | 110.24
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 174 | 181 | 110.23
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 174 | 181 | 110.12
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - KINTIGH 345 | T:77&78 | 174 | 181 | 109.95
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:100 | T:77&78 | 174 | 181 | 109.95
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:908 NY | T:77&78 | 174 | 181 | 109.46
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | STONYCR - WTHRS 230 | T:77&78 | 174 | 181 | 109.44
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 174 | 181 | 108.92
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 174 | 181 | 108.92
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | CAP:115:GV1 | T:77&78 | 174 | 181 | 108.92
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | CAP:115:GV2 | T:77&78 | 174 | 181 | 108.92
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 174 | 181 | 108.89
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 174 | 181 | 108.89
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 174 | 181 | 108.89
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 174 | 181 | 108.89
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 174 | 181 | 108.72
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 174 | 181 | 108.6
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | B:Hunt68 | 174 | 181 | 108.6
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | T:77&80 | 174 | 181 | 108.57
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | GEN:345:SOMERSET | T:77&78 | 174 | 181 | 108.36
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | GEN:KINTIGH | T:77&78 | 174 | 181 | 108.36
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 174 | 181 | 108.16
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:195 | T:79&80 | 174 | 181 | 107.98
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | SB:HUNT230_R1502 | 174 | 181 | 107.95
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | SB:HUNT230_R1402 | 174 | 181 | 107.69
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | T:78&79 | 174 | 181 | 107.68
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 174 | 181 | 107.63
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 174 | 181 | 107.57
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 174 | 181 | 107.42
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:180 | T:79&80 | 174 | 181 | 107
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:191 | T:79&80 | 174 | 181 | 106.87
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | TB:2/1:PK3 | T:79&80 | 174 | 181 | 106.86
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 174 | 181 | 106.84
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:192 | T:79&80 | 174 | 181 | 106.71
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 174 | 181 | 106.42
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HCWC/NWES | T:77&78 | 174 | 181 | 106.42
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:MBWC/NWES | T:77&78 | 174 | 181 | 106.42
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 106.36
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | LN:115:180 | 174 | 181 | 106.2
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | WTHRS - MEYER 230 | T:77&78 | 174 | 181 | 106.16
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:180 | LN:115:181/922 | 174 | 181 | 106.05
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | SB:HUNT230_NEW | 174 | 181 | 106.03
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 174 | 181 | 105.73
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 174 | 181 | 105.66
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 174 | 181 | 105.65
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 174 | 181 | 105.63
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | TB:2/1:MEYER | T:77&78 | 174 | 181 | 105.62
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | First:Lockport_907 | T:77&78 | 174 | 181 | 105.61
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:907 NY | T:77&78 | 174 | 181 | 105.58
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 174 | 181 | 105.57
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 174 | 181 | 105.56
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 174 | 181 | 105.54
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 174 | 181 | 105.49
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | B:Hunt67 | 174 | 181 | 105.47
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 11 | T:77&78 | 174 | 181 | 105.37
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 12 | T:77&78 | 174 | 181 | 105.37
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 13 | T:77&78 | 174 | 181 | 105.37
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 10 | T:77&78 | 174 | 181 | 105.36
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 8 | T:77&78 | 174 | 181 | 105.36
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 9 | T:77&78 | 174 | 181 | 105.36
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 174 | 181 | 105.29
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 105.21
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | GEN:115:GINNA | T:77&78 | 174 | 181 | 105.2
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:GINNA | T:77&78 | 174 | 181 | 105.18
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 174 | 181 | 105.17
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | SB:GARD230_T7-12 | 174 | 181 | 105.16
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 7 | T:77&78 | 174 | 181 | 105.11
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 4 | T:77&78 | 174 | 181 | 105.08
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 5 | T:77&78 | 174 | 181 | 105.08
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 6 | T:77&78 | 174 | 181 | 105.08
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 174 | 181 | 104.99
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | SB:HUNT230_R1302 | 174 | 181 | 104.9
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | SB:HUNT230_R1202 | 174 | 181 | 104.88
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HCMB/NWES | T:77&78 | 174 | 181 | 104.88
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 174 | 181 | 104.8
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 174 | 181 | 104.73
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 104.71
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | TB:2/1:ROB | T:77&78 | 174 | 181 | 104.68
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | TB:2/1:NI1 | T:77&78 | 174 | 181 | 104.48
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAGARA 230/115 1TR | T:77&78 | 174 | 181 | 104.48
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | STONYCR - WTHRS 230 | T:77&78 | 174 | 181 | 104.39
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 174 | 181 | 104.34
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:181/922 | 174 | 181 | 104.18
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:181/922 | 174 | 181 | 104.11
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:100 | T:77&78 | 174 | 181 | 104.08
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:39 | DCT:230:79+80+ELM1-2 | 174 | 181 | 104.07
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.95
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | S:PA_HNTL77 | 174 | 181 | 103.8
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | CAP:115:GV1 | T:77&78 | 174 | 181 | 103.78
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | CAP:115:GV2 | T:77&78 | 174 | 181 | 103.78
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | HUNTLEY - PACKARD 78 230 | 174 | 181 | 103.7
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | S:PA_HNTL78 | 174 | 181 | 103.7
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 174 | 181 | 103.66
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | HUNTLEY - PACKARD 77 230 | 174 | 181 | 103.64
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:908 NY | T:77&78 | 174 | 181 | 103.6
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.58
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 174 | 181 | 103.5
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | B:STOLE230 | 174 | 181 | 103.43
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.37
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | GEN:345:SOMERSET | T:77&78 | 174 | 181 | 103.34
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | GEN:KINTIGH | T:77&78 | 174 | 181 | 103.34
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | PACKARD 230/115 3TR | T:77&78 | 174 | 181 | 103.34
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:38 | T:79&80 | 174 | 181 | 103.28
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - ELM 70 230 | T:79&80 | 174 | 181 | 103.1
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 174 | 181 | 103.05
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:39 | T:79&80 | 174 | 181 | 103.02
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:79&80 | 174 | 181 | 102.92
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.86
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.75
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:181/922 | 174 | 181 | 102.75
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:345:37S-FM-FV-HC | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.66
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:181/922 | 174 | 181 | 102.62
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:195 | T:79&80 | 174 | 181 | 102.58
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | STOLLRD - GARDENVILL 66 230 | 174 | 181 | 102.57
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-FV_37&W-F_171 | T:79&80 | 174 | 181 | 102.44
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:101 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.42
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | ROBINSON - STOLLRD 65 230 | 174 | 181 | 102.34
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:102 | DCT:230:79+80+ELM1-2 | 174 | 181 | 102.17
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_NEW | 174 | 181 | 102.13
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | FARMVLY - HOMERCTY | T:79&80 | 174 | 181 | 102.11
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:120 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.98
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 7 | T:77&78 | 174 | 181 | 101.96
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 4 | T:77&78 | 174 | 181 | 101.94
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 5 | T:77&78 | 174 | 181 | 101.94
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:NIAG. 6 | T:77&78 | 174 | 181 | 101.94
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:191 | T:79&80 | 174 | 181 | 101.88
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.79
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:FV-5M_37&W-F_171 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.79
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 174 | 181 | 101.78
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:192 | T:79&80 | 174 | 181 | 101.77
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:345:37S-FM-FV-HC | T:79&80 | 174 | 181 | 101.75
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:101 | T:79&80 | 174 | 181 | 101.65
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.54
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.45
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:102 | T:79&80 | 174 | 181 | 101.4
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HCWC/NWES | T:77&78 | 174 | 181 | 101.36
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:MBWC/NWES | T:77&78 | 174 | 181 | 101.36
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 174 | 181 | 101.35
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.33
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:345:37S-FM-FV | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.27
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | T:77&80 | 174 | 181 | 101.24
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | B:Hunt68 | 174 | 181 | 101.21
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:120 | T:79&80 | 174 | 181 | 101.21
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.13
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | WTHRS - MEYER 230 | T:77&78 | 174 | 181 | 101.1
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:BLISS1 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.1
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 174 | 181 | 101.05
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | SB:PA230_R3430 | 174 | 181 | 100.97
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 174 | 181 | 100.96
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-SR_37&W-F_171 | T:79&80 | 174 | 181 | 100.88
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:FV-5M_37&W-F_171 | T:79&80 | 174 | 181 | 100.88
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | FARMVLY - 5MILE 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.76
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | First:Lancaster_922 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.72
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | SB:HUNT230_R1502 | 174 | 181 | 100.56
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:133 | T:79&80 | 174 | 181 | 100.54
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:INDEK-OL | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.5
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:345:37S-FM-FV | T:79&80 | 174 | 181 | 100.45
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | SB:GARD230_R823 | 174 | 181 | 100.4
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 174 | 181 | 100.38
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 174 | 181 | 100.38
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 174 | 181 | 100.38
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | SB:HUNT230_R1402 | 174 | 181 | 100.33
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | T:78&79 | 174 | 181 | 100.33
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 174 | 181 | 100.33
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:130 | T:79&80 | 174 | 181 | 100.33
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 174 | 181 | 100.31
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 174 | 181 | 100.3
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 174 | 181 | 100.24
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | G:BLISS1 | T:79&80 | 174 | 181 | 100.23
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 174 | 181 | 100.1
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:129 | T:79&80 | 174 | 181 | 100.07
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | TB:2/1:PK3 | T:79&80 | 174 | 181 | 100.05
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 174 | 181 | 100.04
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | LN:115:181/922 | SB:GARD230_R833 | 174 | 181 | 100.02
| 135449 GR.I-182 115 135459 NI.B-182 115 1 Max |  |  |  |  | 163.45
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 200 | 208 | NConv
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 200 | 208 | NConv
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 200 | 208 | NConv
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 200 | 208 | NConv
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 200 | 208 | NConv
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 200 | 208 | NConv
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 200 | 208 | NConv
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 200 | 208 | NConv
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 200 | 208 | NConv
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 200 | 208 | NConv
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 208 | 157.64
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 208 | 155.02
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | T:77&78 | 200 | 208 | 137.38
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 200 | 208 | 136.85
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 200 | 208 | 132.72
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | T:77&78 | 200 | 208 | 131.81
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 200 | 208 | 127.03
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:180 | T:77&78 | 200 | 208 | 126.19
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 200 | 208 | 123.22
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 200 | 208 | 123.05
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 200 | 208 | 121.39
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:180 | T:77&78 | 200 | 208 | 120.54
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | T:79&80 | 200 | 208 | 120.32
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 200 | 208 | 120.11
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 200 | 208 | 119.94
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:195 | T:77&78 | 200 | 208 | 119.54
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:191 | T:77&78 | 200 | 208 | 118.55
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:192 | T:77&78 | 200 | 208 | 118.42
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 200 | 208 | 118.17
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | TB:2/1:PK3 | T:77&78 | 200 | 208 | 118.12
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 200 | 208 | 117.93
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 200 | 208 | 116.64
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 200 | 208 | 116.47
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 200 | 208 | 116.42
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 200 | 208 | 116.02
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:38 | T:77&78 | 200 | 208 | 115.82
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 200 | 208 | 115.73
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:39 | T:77&78 | 200 | 208 | 115.54
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 200 | 208 | 115.31
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 200 | 208 | 115.1
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 200 | 208 | 115.1
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 200 | 208 | 114.84
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:195 | T:77&78 | 200 | 208 | 114.73
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | T:79&80 | 200 | 208 | 114.72
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV | T:77&78 | 200 | 208 | 114.71
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 200 | 208 | 114.57
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 200 | 208 | 114.55
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | FARMVLY - HOMERCTY | T:77&78 | 200 | 208 | 114.2
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:191 | T:77&78 | 200 | 208 | 114.16
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:192 | T:77&78 | 200 | 208 | 114.07
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 200 | 208 | 113.27
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 200 | 208 | 113.04
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:101 | T:77&78 | 200 | 208 | 112.89
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 200 | 208 | 112.87
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:102 | T:77&78 | 200 | 208 | 112.67
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:133 | T:77&78 | 200 | 208 | 112.5
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:120 | T:77&78 | 200 | 208 | 112.48
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:130 | T:77&78 | 200 | 208 | 112.28
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | TB:2/1:PK3 | T:77&78 | 200 | 208 | 112.02
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 200 | 208 | 112
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 200 | 208 | 112
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 200 | 208 | 112
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:129 | T:77&78 | 200 | 208 | 111.99
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 200 | 208 | 111.83
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 200 | 208 | 111.79
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:BLISS1 | T:77&78 | 200 | 208 | 111.71
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | First:Lancaster_922 | T:77&78 | 200 | 208 | 111.68
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 200 | 208 | 111.44
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 200 | 208 | 111.32
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:INDEK-OL | T:77&78 | 200 | 208 | 111.18
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:38 | T:77&78 | 200 | 208 | 110.93
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 110.71
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:39 | T:77&78 | 200 | 208 | 110.66
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 200 | 208 | 110.64
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 200 | 208 | 110.55
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 200 | 208 | 110.49
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 200 | 208 | 110.41
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 200 | 208 | 110.29
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 200 | 208 | 110.29
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 200 | 208 | 110.12
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 200 | 208 | 109.91
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 200 | 208 | 109.91
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 200 | 208 | 109.91
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV | T:77&78 | 200 | 208 | 109.9
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 200 | 208 | 109.9
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 200 | 208 | 109.9
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | FARMVLY - HOMERCTY | T:77&78 | 200 | 208 | 109.55
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:180 | T:79&80 | 200 | 208 | 109.4
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 200 | 208 | 108.61
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 200 | 208 | 108.43
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 200 | 208 | 107.92
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:101 | T:77&78 | 200 | 208 | 107.83
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:133 | T:77&78 | 200 | 208 | 107.68
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:102 | T:77&78 | 200 | 208 | 107.63
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:120 | T:77&78 | 200 | 208 | 107.54
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:130 | T:77&78 | 200 | 208 | 107.5
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 200 | 208 | 107.22
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 200 | 208 | 107.22
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 200 | 208 | 107.22
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 107.2
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:129 | T:77&78 | 200 | 208 | 107.13
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:BLISS1 | T:77&78 | 200 | 208 | 107.13
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | First:Lancaster_922 | T:77&78 | 200 | 208 | 106.93
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | TB:2/1:ROB | T:77&78 | 200 | 208 | 106.88
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 200 | 208 | 106.82
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 200 | 208 | 106.75
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | GEN:115:GINNA | T:77&78 | 200 | 208 | 106.67
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:GINNA | T:77&78 | 200 | 208 | 106.65
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:INDEK-OL | T:77&78 | 200 | 208 | 106.54
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 200 | 208 | 106.4
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:100 | T:77&78 | 200 | 208 | 106.33
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:908 NY | T:77&78 | 200 | 208 | 105.92
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | STONYCR - WTHRS 230 | T:77&78 | 200 | 208 | 105.86
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 200 | 208 | 105.85
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 200 | 208 | 105.84
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 200 | 208 | 105.37
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 200 | 208 | 105.37
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 200 | 208 | 105.37
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 200 | 208 | 105.37
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | CAP:115:GV1 | T:77&78 | 200 | 208 | 105.35
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | CAP:115:GV2 | T:77&78 | 200 | 208 | 105.35
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | T:77&80 | 200 | 208 | 105.33
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | B:Hunt68 | 200 | 208 | 105.32
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 200 | 208 | 105.17
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 200 | 208 | 105.04
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | GEN:345:SOMERSET | T:77&78 | 200 | 208 | 104.9
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | GEN:KINTIGH | T:77&78 | 200 | 208 | 104.9
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 200 | 208 | 104.78
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_R1502 | 200 | 208 | 104.59
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:195 | T:79&80 | 200 | 208 | 104.56
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_R1402 | 200 | 208 | 104.36
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | T:78&79 | 200 | 208 | 104.36
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 200 | 208 | 104.22
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 200 | 208 | 104.17
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 200 | 208 | 104.03
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:180 | T:79&80 | 200 | 208 | 103.68
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | TB:2/1:PK3 | T:79&80 | 200 | 208 | 103.59
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:191 | T:79&80 | 200 | 208 | 103.59
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 200 | 208 | 103.52
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:192 | T:79&80 | 200 | 208 | 103.45
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 103.4
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 200 | 208 | 103.14
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:HCWC/NWES | T:77&78 | 200 | 208 | 103.13
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:MBWC/NWES | T:77&78 | 200 | 208 | 103.13
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | WTHRS - MEYER 230 | T:77&78 | 200 | 208 | 103.04
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_NEW | 200 | 208 | 102.91
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | LN:115:180 | 200 | 208 | 102.9
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:180 | LN:115:181/922 | 200 | 208 | 102.77
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 200 | 208 | 102.61
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 200 | 208 | 102.53
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | B:Hunt67 | 200 | 208 | 102.51
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 102.44
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 200 | 208 | 102.36
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 200 | 208 | 102.28
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 200 | 208 | 102.25
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 200 | 208 | 102.24
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:NIAG. 11 | T:77&78 | 200 | 208 | 102.19
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:NIAG. 12 | T:77&78 | 200 | 208 | 102.19
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:NIAG. 13 | T:77&78 | 200 | 208 | 102.19
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:NIAG. 8 | T:77&78 | 200 | 208 | 102.19
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:NIAG. 9 | T:77&78 | 200 | 208 | 102.19
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:NIAG. 10 | T:77&78 | 200 | 208 | 102.18
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 200 | 208 | 102.18
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | GEN:115:GINNA | T:77&78 | 200 | 208 | 102.17
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 200 | 208 | 102.17
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:GINNA | T:77&78 | 200 | 208 | 102.15
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:NIAG. 7 | T:77&78 | 200 | 208 | 102.15
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:NIAG. 4 | T:77&78 | 200 | 208 | 102.13
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:NIAG. 5 | T:77&78 | 200 | 208 | 102.13
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | G:NIAG. 6 | T:77&78 | 200 | 208 | 102.13
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 200 | 208 | 102.12
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:GARD230_T7-12 | 200 | 208 | 102.08
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 200 | 208 | 102.05
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 200 | 208 | 102.04
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_R1302 | 200 | 208 | 101.86
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 200 | 208 | 101.85
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_R1202 | 200 | 208 | 101.83
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 101.83
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:HCMB/NWES | T:77&78 | 200 | 208 | 101.77
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | TB:2/1:ROB | T:77&78 | 200 | 208 | 101.67
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 200 | 208 | 101.65
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | TB:2/1:NI1 | T:77&78 | 200 | 208 | 101.53
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAGARA 230/115 1TR | T:77&78 | 200 | 208 | 101.53
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 200 | 208 | 101.38
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | STONYCR - WTHRS 230 | T:77&78 | 200 | 208 | 101.37
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:181/922 | 200 | 208 | 101.23
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:181/922 | 200 | 208 | 101.17
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 101.14
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:100 | T:77&78 | 200 | 208 | 101.13
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:39 | DCT:230:79+80+ELM1-2 | 200 | 208 | 101.13
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 200 | 208 | 100.94
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 200 | 208 | 100.94
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | S:PA_HNTL77 | 200 | 208 | 100.91
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | CAP:115:GV1 | T:77&78 | 200 | 208 | 100.81
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | CAP:115:GV2 | T:77&78 | 200 | 208 | 100.81
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | S:PA_HNTL78 | 200 | 208 | 100.8
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | HUNTLEY - PACKARD 78 230 | 200 | 208 | 100.8
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:908 NY | T:77&78 | 200 | 208 | 100.74
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | HUNTLEY - PACKARD 77 230 | 200 | 208 | 100.74
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 200 | 208 | 100.67
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 200 | 208 | 100.65
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | GEN:345:SOMERSET | T:77&78 | 200 | 208 | 100.6
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | GEN:KINTIGH | T:77&78 | 200 | 208 | 100.6
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | PACKARD 230/115 3TR | T:77&78 | 200 | 208 | 100.58
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:181/922 | B:STOLE230 | 200 | 208 | 100.53
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV-HC | DCT:230:79+80+ELM1-2 | 200 | 208 | 100.52
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:38 | T:79&80 | 200 | 208 | 100.49
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | HUNTLEY - ELM 70 230 | T:79&80 | 200 | 208 | 100.48
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 200 | 208 | 100.34
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:79&80 | 200 | 208 | 100.26
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:39 | T:79&80 | 200 | 208 | 100.25
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 200 | 208 | 100.02
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:181/922 | 200 | 208 | 100
| 135449 GR.I-182 115 135538 LONG-182 115 1 Max |  |  |  |  | 157.64
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 160 | 206 | NConv
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 160 | 206 | NConv
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 160 | 206 | NConv
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 160 | 206 | NConv
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 160 | 206 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 160 | 206 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 160 | 206 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 160 | 206 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 160 | 206 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 160 | 206 | 139.65
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 160 | 206 | 135.82
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 160 | 206 | 125
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 160 | 206 | 119.7
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:182S | T:77&78 | 160 | 206 | 114.21
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:182N | T:77&78 | 160 | 206 | 114.15
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 160 | 206 | 113.83
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:181/922 | T:77&78 | 160 | 206 | 113.48
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 111.68
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 160 | 206 | 108.56
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 160 | 206 | 108.53
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:182N | T:77&78 | 160 | 206 | 107.44
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:182S | T:77&78 | 160 | 206 | 107.37
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 106.96
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:181/922 | T:77&78 | 160 | 206 | 106.87
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 106.81
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:192 | T:77&78 | 160 | 206 | 106.71
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:191 | T:77&78 | 160 | 206 | 106.5
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 160 | 206 | 104.8
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 160 | 206 | 104.32
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:38 | T:77&78 | 160 | 206 | 104.31
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:39 | T:77&78 | 160 | 206 | 104.08
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:195 | T:77&78 | 160 | 206 | 103.85
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 160 | 206 | 103.52
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 160 | 206 | 103.45
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | First:Lancaster_922 | T:77&78 | 160 | 206 | 103.43
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 160 | 206 | 103.42
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 160 | 206 | 103.35
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | TB:2/1:PK3 | T:77&78 | 160 | 206 | 103.18
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 160 | 206 | 102.66
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 160 | 206 | 102.63
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 160 | 206 | 102.47
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 160 | 206 | 102.47
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | FARMVLY - HOMERCTY | T:77&78 | 160 | 206 | 102.1
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 160 | 206 | 101.88
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:101 | T:77&78 | 160 | 206 | 101.78
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:345:37S-FM-FV | T:77&78 | 160 | 206 | 101.71
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:102 | T:77&78 | 160 | 206 | 101.53
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:120 | T:77&78 | 160 | 206 | 101.32
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 160 | 206 | 100.75
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:133 | T:77&78 | 160 | 206 | 100.52
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:130 | T:77&78 | 160 | 206 | 100.35
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | LN:115:129 | T:77&78 | 160 | 206 | 100.1
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | G:BLISS1 | T:77&78 | 160 | 206 | 100.04
| 135450 GRDNVL1 115 135453 LONG-180 115 1 Max |  |  |  |  | 139.65
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 120.54
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 119.78
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | LN:115:142 | SB:DUNK230_R1312 | 88 | 101 | 119.55
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | LN:115:142 | SB:DUNK230_R1312 | 88 | 101 | 119.07
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 108.11
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 107.48
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 106.99
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 106.99
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 106.34
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 106.34
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 104.66
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 104.04
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 103.9
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 101 | 103.32
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 103.26
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | LFYTE - CLARKCRNS 36A 345 | T:73&74 | 88 | 101 | 102.91
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:73&74 | 88 | 101 | 102.82
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 101 | 102.66
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | LFYTE - CLARKCRNS 36A 345 | T:73&74 | 88 | 101 | 102.32
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:73&74 | 88 | 101 | 102.23
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | LN:345:37S-FM-FV-HC | T:73&74 | 88 | 101 | 102.15
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | MEYER - CANDQUA 60 230 | T:73&74 | 88 | 101 | 101.3
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | HILLSIDE 230/115 4TR | T:73&74 | 88 | 101 | 101.22
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | LN:345:37S-FM-FV-HC | T:73&74 | 88 | 101 | 101.12
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | SOMERSET - NEWROCH 1 345 | T:73&74 | 88 | 101 | 100.93
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | MEYER - CANDQUA 60 230 | T:73&74 | 88 | 101 | 100.68
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | LN:115:167 | T:73&74 | 88 | 101 | 100.68
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | HILLSIDE 230/115 4TR | T:73&74 | 88 | 101 | 100.66
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | SOMERSET - NEWROCH 1 345 | T:73&74 | 88 | 101 | 100.5
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | 4 MILE - ERIE SE 230 | T:73&74 | 88 | 101 | 100.48
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | SHLDON - STONYCR 230 | T:73&74 | 88 | 101 | 100.48
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | G:JAMESGN7 | T:73&74 | 88 | 101 | 100.36
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | LN:115:167 | T:73&74 | 88 | 101 | 100.04
| 135450 GRDNVL1 115 135475 S139-141 115 1 Max |  |  |  |  | 120.54
Dispatch 2 | 135450 GRDNVL1 115 135503 DALE-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 129 | 181 | 105.59
Dispatch 1 | 135450 GRDNVL1 115 135503 DALE-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 129 | 181 | 105.05
| 135450 GRDNVL1 115 135503 DALE-38 115 1 Max |  |  |  |  | 105.59
Dispatch 2 | 135450 GRDNVL1 115 135504 DALE-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 129 | 181 | 109.2
Dispatch 1 | 135450 GRDNVL1 115 135504 DALE-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 129 | 181 | 108.71
| 135450 GRDNVL1 115 135504 DALE-39 115 1 Max |  |  |  |  | 109.2
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 145 | 151 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 151 | 163.03
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 145 | 151 | 163.02
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:39 | T:77&78 | 145 | 151 | 141.9
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 151 | 141.12
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 145 | 151 | 138.31
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:39 | T:77&78 | 145 | 151 | 136.34
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 123.17
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 145 | 151 | 122.03
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 121.19
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 145 | 151 | 119.28
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 145 | 151 | 118.98
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:39 | DCT:230:79+80+ELM1-2 | 145 | 151 | 118.27
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:180 | T:77&78 | 145 | 151 | 118.02
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:182N | T:77&78 | 145 | 151 | 117.46
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:39 | T:79&80 | 145 | 151 | 116.84
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 145 | 151 | 116.45
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 116.33
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:181/922 | T:77&78 | 145 | 151 | 116.02
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:182S | T:77&78 | 145 | 151 | 115.98
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 145 | 151 | 113.66
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 145 | 151 | 113.04
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:180 | T:77&78 | 145 | 151 | 113.01
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:182N | T:77&78 | 145 | 151 | 112.79
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:39 | DCT:230:79+80+ELM1-2 | 145 | 151 | 112.76
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 145 | 151 | 112.4
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:181/922 | T:77&78 | 145 | 151 | 111.44
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 145 | 151 | 111.25
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:182S | T:77&78 | 145 | 151 | 111.18
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:39 | T:79&80 | 145 | 151 | 110.97
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 145 | 151 | 110.7
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 145 | 151 | 110.68
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 145 | 151 | 110.68
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 145 | 151 | 110.58
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 145 | 151 | 110.29
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:345:37S-FM-FV | T:77&78 | 145 | 151 | 109.96
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 145 | 151 | 109.89
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | FARMVLY - HOMERCTY | T:77&78 | 145 | 151 | 109.78
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 145 | 151 | 109
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 145 | 151 | 108.18
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 145 | 151 | 108.01
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | First:Lancaster_922 | T:77&78 | 145 | 151 | 107.46
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 145 | 151 | 107.42
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 145 | 151 | 107.16
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 145 | 151 | 106.91
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 145 | 151 | 106.65
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 145 | 151 | 106.65
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | G:BLISS1 | T:77&78 | 145 | 151 | 106.51
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 145 | 151 | 106.46
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 145 | 151 | 106.35
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 145 | 151 | 106.35
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 145 | 151 | 106.35
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 145 | 151 | 106.19
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:345:37S-FM-FV | T:77&78 | 145 | 151 | 106.13
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 145 | 151 | 105.93
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | CAP:115:HUN | T:77&78 | 145 | 151 | 105.91
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | PACKARD 230/115 3TR | T:77&78 | 145 | 151 | 105.75
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | G:INDEK-OL | T:77&78 | 145 | 151 | 105.75
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | FARMVLY - HOMERCTY | T:77&78 | 145 | 151 | 105.68
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 145 | 151 | 105.35
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 145 | 151 | 105.02
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | G:JAMESGN7 | T:77&78 | 145 | 151 | 104.95
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:4 | T:77&78 | 145 | 151 | 104.63
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:969 | T:77&78 | 145 | 151 | 104.59
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 145 | 151 | 104.3
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 145 | 151 | 104.19
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 145 | 151 | 104.07
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 145 | 151 | 103.85
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 145 | 151 | 103.85
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 145 | 151 | 103.85
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 145 | 151 | 103.85
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 145 | 151 | 103.44
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | First:Lancaster_922 | T:77&78 | 145 | 151 | 103.06
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 145 | 151 | 102.57
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 145 | 151 | 102.57
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 145 | 151 | 102.57
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | PACKARD 230/115 3TR | T:77&78 | 145 | 151 | 102.38
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | G:BLISS1 | T:77&78 | 145 | 151 | 102.38
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | CAP:115:HUN | T:77&78 | 145 | 151 | 101.9
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 145 | 151 | 101.81
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | G:INDEK-OL | T:77&78 | 145 | 151 | 101.55
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 145 | 151 | 101.43
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | TB:2/1:NI1 | T:77&78 | 145 | 151 | 101.29
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | NIAGARA 230/115 1TR | T:77&78 | 145 | 151 | 101.29
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | STOLLRD - SHLDON 67 230 | T:77&78 | 145 | 151 | 100.94
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | G:JAMESGN7 | T:77&78 | 145 | 151 | 100.74
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | TB:2/1:PK4 | T:77&78 | 145 | 151 | 100.56
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | PACKARD 230/115 4TR | T:77&78 | 145 | 151 | 100.56
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:4 | T:77&78 | 145 | 151 | 100.53
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:969 | T:77&78 | 145 | 151 | 100.48
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 145 | 151 | 100.41
Dispatch 1 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 145 | 151 | 100.39
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:160 | T:77&78 | 145 | 151 | 100.34
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | LN:115:36 | T:77&78 | 145 | 151 | 100.17
Dispatch 2 | 135451 HUNTLEY1 115 135472 S129-38 115 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 145 | 151 | 100.11
| 135451 HUNTLEY1 115 135472 S129-38 115 1 Max |  |  |  |  | 163.03
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 168 | 181 | NConv
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 168 | 181 | NConv
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 168 | 181 | NConv
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 168 | 181 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 168 | 181 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 168 | 181 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:77&78 | 168 | 181 | 153.38
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:77&78 | 168 | 181 | 147.31
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | T:77&78 | 168 | 181 | 140.93
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 168 | 181 | 138.63
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:79&80 | 168 | 181 | 137.54
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:NIAW230_2014 | 168 | 181 | 136.37
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 168 | 181 | 135.85
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | T:77&78 | 168 | 181 | 135.32
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 168 | 181 | 133.81
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAGARA 230/115 2TR | 168 | 181 | 133.46
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | TB:2/1:NI2 | 168 | 181 | 133.46
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | LN:115:133 | 168 | 181 | 133.32
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | LN:115:133 | 168 | 181 | 133.32
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 168 | 181 | 132.55
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:79&80 | 168 | 181 | 131.22
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 181 | 130.28
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:PA230_R3430 | 168 | 181 | 128.74
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 181 | 127.67
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 168 | 181 | 127.36
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:133 | 168 | 181 | 126.63
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:61&64 | 168 | 181 | 126.4
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | T:79&80 | 168 | 181 | 126.36
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 125.82
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | LN:115:133 | 168 | 181 | 125.23
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:ROBI230 | 168 | 181 | 125
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 168 | 181 | 124.32
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:PA230_R3230 | 168 | 181 | 123.96
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:PA230_R506 | 168 | 181 | 123.76
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:NIAW230_2014 | 168 | 181 | 123.73
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:HUNT230_R1502 | 168 | 181 | 123.66
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:Hunt68 | 168 | 181 | 123.6
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:77&80 | 168 | 181 | 123.42
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:HUNT230_R1402 | 168 | 181 | 123.42
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:78&79 | 168 | 181 | 123.41
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:PACKT4 | 168 | 181 | 123.3
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 181 | 123.18
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:255_345B302 | 168 | 181 | 122.69
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:133 | 168 | 181 | 122.65
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:NIAG345_3108 | 168 | 181 | 122.53
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAG - NEWROCH 1 345 | 168 | 181 | 122.5
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:HUNT230_NEW | 168 | 181 | 122.03
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 168 | 181 | 121.76
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | PACKARD 230/115 4TR | 168 | 181 | 121.73
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | TB:2/1:PK4 | 168 | 181 | 121.73
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:PK4 | LN:115:133 | 168 | 181 | 121.57
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 4TR | LN:115:133 | 168 | 181 | 121.57
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 168 | 181 | 121.51
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:HUNT230_R1302 | 168 | 181 | 121.36
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:HUNT230_R1202 | 168 | 181 | 121.32
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:Hunt67 | 168 | 181 | 121.26
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 121.19
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | NIAGARA 230/115 2TR | 168 | 181 | 121.13
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | TB:2/1:NI2 | 168 | 181 | 121.13
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | LN:115:129 | 168 | 181 | 120.95
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | LN:115:129 | 168 | 181 | 120.95
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:133 | 168 | 181 | 120.93
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:255_345B202 | 168 | 181 | 120.91
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:133 | 168 | 181 | 120.87
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SOMERSET - NEWROCH 1 345 | 168 | 181 | 120.84
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 168 | 181 | 120.6
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | T:79&80 | 168 | 181 | 120.56
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | S:PA_HNTL77 | 168 | 181 | 120.43
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | HUNTLEY - PACKARD 78 230 | 168 | 181 | 120.33
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | S:PA_HNTL78 | 168 | 181 | 120.33
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | HUNTLEY - PACKARD 77 230 | 168 | 181 | 120.27
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:133 | 168 | 181 | 119.82
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:61&64 | 168 | 181 | 119.55
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 181 | 119.46
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | Base Case | 168 | 181 | 119.38
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 119.15
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 168 | 181 | 119.14
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 118.89
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:908 NY | 168 | 181 | 118.89
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:908 NY | LN:115:133 | 168 | 181 | 118.81
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:ROBI230 | 168 | 181 | 118.4
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 168 | 181 | 117.72
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:100 | 168 | 181 | 117.66
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:100 | LN:115:133 | 168 | 181 | 117.57
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:PA230_R3230 | 168 | 181 | 117.53
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | LN:115:133 | 168 | 181 | 117.49
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:GARD230_R823 | 168 | 181 | 117.11
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:GARD230_R833 | 168 | 181 | 117.01
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:133 | 168 | 181 | 116.95
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:133 | 168 | 181 | 116.94
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:GARD230_T7-12 | 168 | 181 | 116.89
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:PA230_R3430 | 168 | 181 | 116.85
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:GARD72&79 | 168 | 181 | 116.85
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | S:HNT_GRD80 | 168 | 181 | 116.76
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 168 | 181 | 116.75
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | HUNTLEY - GARDENVILL 79 230 | 168 | 181 | 116.67
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | HUNTLEY - GARDENVILL 80 230 | 168 | 181 | 116.66
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | TB:2/1:ROB | 168 | 181 | 116.5
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:GARD230_R873 | 168 | 181 | 116.38
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:ROB | LN:115:133 | 168 | 181 | 116.36
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:HUNT230_R1502 | 168 | 181 | 116.21
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:Hunt68 | 168 | 181 | 116.19
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:77&80 | 168 | 181 | 116.04
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:GARD73&80 | 168 | 181 | 116.03
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:HUNT230_R1402 | 168 | 181 | 116.01
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:78&79 | 168 | 181 | 116.01
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:129 | 168 | 181 | 115.88
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | T:61&64 | 168 | 181 | 115.66
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:133 | 168 | 181 | 115.26
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:STOLE230 | 168 | 181 | 115.19
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI1 | T:77&78 | 168 | 181 | 115.18
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | G:LOCKPORT | 168 | 181 | 115.18
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 1TR | T:77&78 | 168 | 181 | 115.18
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | LN:115:129 | 168 | 181 | 115.15
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 115.14
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:133 | 168 | 181 | 115.04
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:101 | 168 | 181 | 115.03
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:133 | 168 | 181 | 115
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:255_345B302 | 168 | 181 | 114.95
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | STOLLRD - GARDENVILL 66 230 | 168 | 181 | 114.95
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:LOCKPORT | LN:115:133 | 168 | 181 | 114.88
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:101 | LN:115:133 | 168 | 181 | 114.85
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:NIAG345_3108 | 168 | 181 | 114.81
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAGARA 230/115 1TR | 168 | 181 | 114.8
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | TB:2/1:NI1 | 168 | 181 | 114.8
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI1 | LN:115:133 | 168 | 181 | 114.79
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 1TR | LN:115:133 | 168 | 181 | 114.79
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | ROBINSON - STOLLRD 65 230 | 168 | 181 | 114.78
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:102 | 168 | 181 | 114.77
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAG - NEWROCH 1 345 | 168 | 181 | 114.74
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI1 | T:77&78 | 168 | 181 | 114.73
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 1TR | T:77&78 | 168 | 181 | 114.73
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:102 | LN:115:133 | 168 | 181 | 114.59
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:907 NY | 168 | 181 | 114.57
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | First:Lockport_907 | 168 | 181 | 114.54
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:HUNT230_NEW | 168 | 181 | 114.48
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | FARMVLY - HOMERCTY | 168 | 181 | 114.48
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:907 NY | LN:115:133 | 168 | 181 | 114.46
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | R:HC-FV_37&W-F_171 | 168 | 181 | 114.43
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:120 | 168 | 181 | 114.42
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | First:Lockport_907 | LN:115:133 | 168 | 181 | 114.4
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:ROBI230 | 168 | 181 | 114.36
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:120 | LN:115:133 | 168 | 181 | 114.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:37 | 168 | 181 | 114.15
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:37 | LN:115:133 | 168 | 181 | 113.98
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:DUPONT46 | LN:115:133 | 168 | 181 | 113.96
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:ROCH_2T8082 | 168 | 181 | 113.88
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:36 | 168 | 181 | 113.87
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:Hunt67 | 168 | 181 | 113.73
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - KINTIGH 345 | LN:115:133 | 168 | 181 | 113.71
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:36 | LN:115:133 | 168 | 181 | 113.69
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | PACKARD 230/115 3TR | 168 | 181 | 113.64
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | B:Hunt68 | 168 | 181 | 113.62
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 3TR | LN:115:133 | 168 | 181 | 113.58
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 3TR | T:77&78 | 168 | 181 | 113.58
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:ROCH_34XC | 168 | 181 | 113.56
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:40&41 | 168 | 181 | 113.55
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:HUNT230_R1502 | 168 | 181 | 113.52
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:HUNT230_R1202 | 168 | 181 | 113.5
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:HUNT230_R1302 | 168 | 181 | 113.47
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | T:77&80 | 168 | 181 | 113.47
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:NIAG345_3308 | 168 | 181 | 113.47
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:PA230_R3230 | 168 | 181 | 113.43
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:PACKT3 | 168 | 181 | 113.39
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAG - KINTIGH 345 | 168 | 181 | 113.36
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:133 | 168 | 181 | 113.34
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:908 NY | T:77&78 | 168 | 181 | 113.31
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | T:78&79 | 168 | 181 | 113.29
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:HUNT230_R1402 | 168 | 181 | 113.29
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:KINT_39-B112 | 168 | 181 | 113.2
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:KINT_B1-3812 | 168 | 181 | 113.13
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:ROCH_3414 | 168 | 181 | 113.11
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:ROCH_3514 | 168 | 181 | 113.1
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:255_345B202 | 168 | 181 | 113.08
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SOMERSET - NEWROCH 1 345 | 168 | 181 | 113.01
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:133 | 168 | 181 | 112.99
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:133 | 168 | 181 | 112.95
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:133 | 168 | 181 | 112.92
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 4 | LN:115:133 | 168 | 181 | 112.91
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 5 | LN:115:133 | 168 | 181 | 112.91
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 6 | LN:115:133 | 168 | 181 | 112.91
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 7 | LN:115:133 | 168 | 181 | 112.9
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:5MILE_B | 168 | 181 | 112.8
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:LAFA_ELB | 168 | 181 | 112.8
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-FV_37&W-F_171 | LN:115:133 | 168 | 181 | 112.79
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:182N | LN:115:133 | 168 | 181 | 112.77
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | FARMVLY - HOMERCTY | LN:115:133 | 168 | 181 | 112.77
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:129 | 168 | 181 | 112.73
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:255_345B302 | 168 | 181 | 112.72
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 112.7
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 112.64
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:NIAG345_3108 | 168 | 181 | 112.55
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | NIAG - NEWROCH 1 345 | 168 | 181 | 112.52
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:100 | T:77&78 | 168 | 181 | 112.47
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | S:PA_HNTL77 | 168 | 181 | 112.44
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | HUNTLEY - PACKARD 78 230 | 168 | 181 | 112.33
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | S:PA_HNTL78 | 168 | 181 | 112.33
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:PA230_R506 | 168 | 181 | 112.29
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | HUNTLEY - PACKARD 77 230 | 168 | 181 | 112.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:182N | T:77&78 | 168 | 181 | 112.16
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:NIAW230_2014 | 168 | 181 | 112
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:HUNT230_NEW | 168 | 181 | 111.98
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | B:PACKT4 | 168 | 181 | 111.87
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:180 | T:77&78 | 168 | 181 | 111.86
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:182S | T:77&78 | 168 | 181 | 111.79
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:PA230_R3430 | 168 | 181 | 111.64
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:908 NY | 168 | 181 | 111.64
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:908 NY | LN:115:133 | 168 | 181 | 111.58
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:ROB | T:77&78 | 168 | 181 | 111.55
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:181/922 | T:77&78 | 168 | 181 | 111.53
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 168 | 181 | 111.48
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 168 | 181 | 111.41
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - KINTIGH 345 | T:77&78 | 168 | 181 | 111.4
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | B:Hunt67 | 168 | 181 | 111.35
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 168 | 181 | 111.11
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:HUNT230_R1302 | 168 | 181 | 111.1
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:255_345B202 | 168 | 181 | 111.06
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:HUNT230_R1202 | 168 | 181 | 111.06
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 168 | 181 | 111.06
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 3TR | T:77&78 | 168 | 181 | 111.04
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SOMERSET - NEWROCH 1 345 | 168 | 181 | 110.99
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 168 | 181 | 110.93
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 168 | 181 | 110.93
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 168 | 181 | 110.92
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:LOCKPORT | T:77&78 | 168 | 181 | 110.81
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | FARMVLY - HOMERCTY | T:77&78 | 168 | 181 | 110.76
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:101 | T:77&78 | 168 | 181 | 110.72
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:129 | 168 | 181 | 110.71
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:129 | 168 | 181 | 110.66
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:DUPONT46 | T:77&78 | 168 | 181 | 110.59
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:102 | T:77&78 | 168 | 181 | 110.55
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:100 | 168 | 181 | 110.52
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:100 | LN:115:133 | 168 | 181 | 110.46
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 110.44
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | TB:2/1:PK4 | 168 | 181 | 110.43
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | PACKARD 230/115 4TR | 168 | 181 | 110.43
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 168 | 181 | 110.4
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:120 | T:77&78 | 168 | 181 | 110.38
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | Base Case | 168 | 181 | 110.29
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:PK4 | LN:115:129 | 168 | 181 | 110.29
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 4TR | LN:115:129 | 168 | 181 | 110.29
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:907 NY | T:77&78 | 168 | 181 | 110.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | S:PA_HNTL77 | 168 | 181 | 110.26
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | First:Lockport_907 | T:77&78 | 168 | 181 | 110.23
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | HUNTLEY - PACKARD 78 230 | 168 | 181 | 110.16
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | S:PA_HNTL78 | 168 | 181 | 110.16
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI1 | LN:115:133 | 168 | 181 | 110.14
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 1TR | LN:115:133 | 168 | 181 | 110.14
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:345:37S-FM-FV | T:77&78 | 168 | 181 | 110.13
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | HUNTLEY - PACKARD 77 230 | 168 | 181 | 110.12
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:37 | T:77&78 | 168 | 181 | 110
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 109.97
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAGARA 230/115 1TR | 168 | 181 | 109.96
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | TB:2/1:NI1 | 168 | 181 | 109.96
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 168 | 181 | 109.91
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:908 NY | T:77&78 | 168 | 181 | 109.86
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | T:77&78 | 168 | 181 | 109.84
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:36 | T:77&78 | 168 | 181 | 109.84
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | T:77&78 | 168 | 181 | 109.84
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:129 | 168 | 181 | 109.64
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:GARD230_R823 | 168 | 181 | 109.52
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | T:61&64 | 168 | 181 | 109.37
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | TB:2/1:ROB | 168 | 181 | 109.35
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | Base Case | 168 | 181 | 109.31
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:ROB | LN:115:133 | 168 | 181 | 109.25
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:GARD230_R833 | 168 | 181 | 109.19
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:100 | T:77&78 | 168 | 181 | 109.15
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 109.09
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 109.09
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 168 | 181 | 109.06
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:133 | 168 | 181 | 108.93
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:133 | 168 | 181 | 108.92
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:GARD72&79 | 168 | 181 | 108.84
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:GARD230_T7-12 | 168 | 181 | 108.83
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | LN:115:908 NY | 168 | 181 | 108.81
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 108.77
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:114 | 168 | 181 | 108.75
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:908 NY | LN:115:129 | 168 | 181 | 108.74
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:113 | 168 | 181 | 108.71
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | S:HNT_GRD80 | 168 | 181 | 108.7
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:111 | 168 | 181 | 108.68
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | HUNTLEY - GARDENVILL 79 230 | 168 | 181 | 108.6
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | DUNKIRK - SRIPL 68 230 | 168 | 181 | 108.6
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:SRIPLEY | 168 | 181 | 108.6
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | HUNTLEY - GARDENVILL 80 230 | 168 | 181 | 108.59
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 168 | 181 | 108.59
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 168 | 181 | 108.59
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 168 | 181 | 108.59
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 168 | 181 | 108.59
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | R:EESR/NWES | 168 | 181 | 108.57
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SRIPL - ERIE E 69 230 | 168 | 181 | 108.57
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:113 | LN:115:133 | 168 | 181 | 108.55
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:111 | LN:115:133 | 168 | 181 | 108.47
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:GARD230_R873 | 168 | 181 | 108.32
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | B:PACKT4 | 168 | 181 | 108.32
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | B:PACKT4 | 168 | 181 | 108.32
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:ROBI230 | 168 | 181 | 108.3
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | SB:PA230_R506 | 168 | 181 | 108.29
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | SB:PA230_R506 | 168 | 181 | 108.29
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:119 | 168 | 181 | 108.28
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:PK4 | TB:2/1:NI2 | 168 | 181 | 108.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:PK4 | NIAGARA 230/115 2TR | 168 | 181 | 108.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | PACKARD 230/115 4TR | 168 | 181 | 108.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | TB:2/1:PK4 | 168 | 181 | 108.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | PACKARD 230/115 4TR | 168 | 181 | 108.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | TB:2/1:PK4 | 168 | 181 | 108.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 4TR | TB:2/1:NI2 | 168 | 181 | 108.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 4TR | NIAGARA 230/115 2TR | 168 | 181 | 108.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | SB:PA230_R3430 | 168 | 181 | 108.26
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | SB:PA230_R3430 | 168 | 181 | 108.26
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:ROB | T:77&78 | 168 | 181 | 108.22
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:119 | LN:115:133 | 168 | 181 | 108.17
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:PK4 | SB:NIAW230_2014 | 168 | 181 | 108.16
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 4TR | SB:NIAW230_2014 | 168 | 181 | 108.16
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 168 | 181 | 108.11
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 168 | 181 | 108.09
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 11 | LN:115:133 | 168 | 181 | 108.09
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 12 | LN:115:133 | 168 | 181 | 108.09
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 13 | LN:115:133 | 168 | 181 | 108.09
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 8 | LN:115:133 | 168 | 181 | 108.09
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 9 | LN:115:133 | 168 | 181 | 108.09
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 10 | LN:115:133 | 168 | 181 | 108.08
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 168 | 181 | 108.02
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | R:DKSR/WRFL | 168 | 181 | 108
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | R:EESR/WRFL | 168 | 181 | 107.96
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | R:EESR/WF/NWES | 168 | 181 | 107.96
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:GARD73&80 | 168 | 181 | 107.95
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:MEYER | 168 | 181 | 107.94
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-WC_30&W-F_171 | LN:115:133 | 168 | 181 | 107.94
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | WTHRS - MEYER 230 | 168 | 181 | 107.93
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | WTRCR - MAINSBRG 30A 345 | LN:115:133 | 168 | 181 | 107.92
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HCWC/NWES | LN:115:133 | 168 | 181 | 107.92
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:MBWC/NWES | LN:115:133 | 168 | 181 | 107.92
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | LN:115:129 | 168 | 181 | 107.87
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:68&160 | 168 | 181 | 107.72
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 168 | 181 | 107.7
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | LN:115:100 | 168 | 181 | 107.68
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:100 | LN:115:129 | 168 | 181 | 107.6
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:182N | T:77&78 | 168 | 181 | 107.59
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 168 | 181 | 107.58
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:PA230_R3230 | 168 | 181 | 107.54
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 168 | 181 | 107.39
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:GARD230_R823 | 168 | 181 | 107.38
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - KINTIGH 345 | T:77&78 | 168 | 181 | 107.35
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HCMB/NWES | LN:115:133 | 168 | 181 | 107.34
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:907 NY | 168 | 181 | 107.31
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-MB_30&W-F_171 | LN:115:133 | 168 | 181 | 107.3
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | First:Lockport_907 | 168 | 181 | 107.28
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | MAINSBRG - HOMERCITY 30B 345 | LN:115:133 | 168 | 181 | 107.27
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:180 | T:77&78 | 168 | 181 | 107.23
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:907 NY | LN:115:133 | 168 | 181 | 107.22
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:182S | T:77&78 | 168 | 181 | 107.2
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | First:Lockport_907 | LN:115:133 | 168 | 181 | 107.17
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 168 | 181 | 107.09
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:GARD230_R833 | 168 | 181 | 107.09
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:129 | 168 | 181 | 107.07
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:129 | 168 | 181 | 107.06
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:133 | 168 | 181 | 107.02
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:GARD230_T7-12 | 168 | 181 | 107.02
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:181/922 | T:77&78 | 168 | 181 | 106.99
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | B:GARD72&79 | 168 | 181 | 106.97
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:STOLE230 | 168 | 181 | 106.94
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 168 | 181 | 106.94
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:133 | 168 | 181 | 106.9
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | S:HNT_GRD80 | 168 | 181 | 106.89
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:907 NY | T:77&78 | 168 | 181 | 106.88
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | First:Lockport_907 | T:77&78 | 168 | 181 | 106.84
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 168 | 181 | 106.83
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | HUNTLEY - GARDENVILL 79 230 | 168 | 181 | 106.81
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | HUNTLEY - GARDENVILL 80 230 | 168 | 181 | 106.8
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 168 | 181 | 106.79
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 3TR | LN:115:133 | 168 | 181 | 106.77
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | G:LOCKPORT | 168 | 181 | 106.76
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | PACKARD 230/115 3TR | 168 | 181 | 106.74
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 168 | 181 | 106.74
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | STOLLRD - GARDENVILL 66 230 | 168 | 181 | 106.7
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 168 | 181 | 106.68
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 168 | 181 | 106.68
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | B:Hunt68 | 168 | 181 | 106.67
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 168 | 181 | 106.6
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | TB:2/1:ROB | 168 | 181 | 106.6
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:GARD230_R873 | 168 | 181 | 106.54
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | T:77&80 | 168 | 181 | 106.53
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | ROBINSON - STOLLRD 65 230 | 168 | 181 | 106.5
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:ROB | LN:115:129 | 168 | 181 | 106.49
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 106.48
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 168 | 181 | 106.48
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:LOCKPORT | LN:115:133 | 168 | 181 | 106.47
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:LOCKPORT | T:77&78 | 168 | 181 | 106.46
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | FARMVLY - HOMERCTY | T:77&78 | 168 | 181 | 106.45
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:PACKT3 | 168 | 181 | 106.43
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:PA230_R506 | 168 | 181 | 106.37
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:HUNT230_R1502 | 168 | 181 | 106.36
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 106.23
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | B:GARD73&80 | 168 | 181 | 106.22
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:HUNT230_R1402 | 168 | 181 | 106.17
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | T:78&79 | 168 | 181 | 106.17
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:DUPONT46 | T:77&78 | 168 | 181 | 106.17
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | TB:2/1:NI2 | 168 | 181 | 106.11
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAGARA 230/115 2TR | 168 | 181 | 106.11
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | GEN:KINTIGH | 168 | 181 | 106.1
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | GEN:345:SOMERSET | 168 | 181 | 106.1
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:101 | 168 | 181 | 106.09
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | FARMVLY - HOMERCTY | 168 | 181 | 106.09
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:UDG-184 | LN:115:133 | 168 | 181 | 106.09
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | LN:115:133 | 168 | 181 | 106.05
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | LN:115:133 | 168 | 181 | 106.05
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | R:HC-FV_37&W-F_171 | 168 | 181 | 106.04
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:101 | T:77&78 | 168 | 181 | 106
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:345:37S-FM-FV | T:77&78 | 168 | 181 | 105.99
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:101 | LN:115:133 | 168 | 181 | 105.93
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:PACKT4 | 168 | 181 | 105.89
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:102 | 168 | 181 | 105.86
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:102 | T:77&78 | 168 | 181 | 105.85
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:37 | T:77&78 | 168 | 181 | 105.83
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:DUPONT46 | LN:115:133 | 168 | 181 | 105.79
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:OXBOWNUG | LN:115:133 | 168 | 181 | 105.78
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:120 | T:77&78 | 168 | 181 | 105.75
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:102 | LN:115:133 | 168 | 181 | 105.7
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:129 | 168 | 181 | 105.68
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:36 | T:77&78 | 168 | 181 | 105.66
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 168 | 181 | 105.66
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:37 | 168 | 181 | 105.64
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:120 | 168 | 181 | 105.62
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:129 | 168 | 181 | 105.54
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:ROCH_2T8082 | 168 | 181 | 105.53
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - KINTIGH 345 | LN:115:133 | 168 | 181 | 105.53
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:255_345B302 | 168 | 181 | 105.5
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:37 | LN:115:133 | 168 | 181 | 105.48
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:120 | LN:115:133 | 168 | 181 | 105.48
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | B:STOLE230 | 168 | 181 | 105.48
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | G:LOCKPORT | 168 | 181 | 105.48
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:PA230_R304 | 168 | 181 | 105.36
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:36 | 168 | 181 | 105.35
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:NIAG345_3108 | 168 | 181 | 105.34
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 11 | T:77&78 | 168 | 181 | 105.33
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 12 | T:77&78 | 168 | 181 | 105.33
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 13 | T:77&78 | 168 | 181 | 105.33
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 8 | T:77&78 | 168 | 181 | 105.32
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 9 | T:77&78 | 168 | 181 | 105.32
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | LN:115:101 | 168 | 181 | 105.31
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:NIAG. 10 | T:77&78 | 168 | 181 | 105.31
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:129 | 168 | 181 | 105.3
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | NIAG - NEWROCH 1 345 | 168 | 181 | 105.28
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | STOLLRD - GARDENVILL 66 230 | 168 | 181 | 105.27
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:NIAG345_3308 | 168 | 181 | 105.25
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 168 | 181 | 105.22
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:ROCH_34XC | 168 | 181 | 105.2
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:36 | LN:115:133 | 168 | 181 | 105.19
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | T:40&41 | 168 | 181 | 105.15
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:101 | LN:115:129 | 168 | 181 | 105.15
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAG - KINTIGH 345 | 168 | 181 | 105.12
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | ROBINSON - STOLLRD 65 230 | 168 | 181 | 105.1
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | LN:115:102 | 168 | 181 | 105.07
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI1 | LN:115:129 | 168 | 181 | 105.04
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | TB:2/1:NI1 | 168 | 181 | 105.04
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | NIAGARA 230/115 1TR | 168 | 181 | 105.04
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 1TR | LN:115:129 | 168 | 181 | 105.04
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:LOCKPORT | LN:115:129 | 168 | 181 | 105.02
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | GEN:345:SOMERSET | LN:115:133 | 168 | 181 | 105.01
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | GEN:KINTIGH | LN:115:133 | 168 | 181 | 105.01
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:KINT_39-B112 | 168 | 181 | 104.96
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:133 | 168 | 181 | 104.94
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:102 | LN:115:129 | 168 | 181 | 104.92
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:KINT_B1-3812 | 168 | 181 | 104.88
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | LN:115:907 NY | 168 | 181 | 104.84
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | FARMVLY - HOMERCTY | 168 | 181 | 104.83
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | First:Lockport_907 | 168 | 181 | 104.81
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 168 | 181 | 104.78
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | R:HC-FV_37&W-F_171 | 168 | 181 | 104.78
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | CAP:115:HUN | 168 | 181 | 104.78
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:HUNT230_NEW | 168 | 181 | 104.77
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | LN:115:120 | 168 | 181 | 104.76
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:907 NY | LN:115:129 | 168 | 181 | 104.76
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 168 | 181 | 104.76
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:DUPONT46 | LN:115:129 | 168 | 181 | 104.75
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:ROCH_3414 | 168 | 181 | 104.74
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:ROCH_3514 | 168 | 181 | 104.74
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | First:Lockport_907 | LN:115:129 | 168 | 181 | 104.7
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | CAP:115:HUN | LN:115:133 | 168 | 181 | 104.67
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:120 | LN:115:129 | 168 | 181 | 104.63
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:PK4 | T:77&78 | 168 | 181 | 104.61
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 4TR | T:77&78 | 168 | 181 | 104.61
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:UDG-184 | T:77&78 | 168 | 181 | 104.6
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 168 | 181 | 104.56
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HCWC/NWES | T:77&78 | 168 | 181 | 104.56
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:MBWC/NWES | T:77&78 | 168 | 181 | 104.56
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:133 | 168 | 181 | 104.55
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | WTHRS - MEYER 230 | T:77&78 | 168 | 181 | 104.55
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:39 | 168 | 181 | 104.5
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:5MILE_B | 168 | 181 | 104.45
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:38 | 168 | 181 | 104.45
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:39 | LN:115:133 | 168 | 181 | 104.41
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:LAFA_ELB | 168 | 181 | 104.4
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-FV_37&W-F_171 | LN:115:133 | 168 | 181 | 104.39
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:OXBOWNUG | LN:115:129 | 168 | 181 | 104.38
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | First:Lockport_104 | 168 | 181 | 104.37
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | FARMVLY - HOMERCTY | LN:115:133 | 168 | 181 | 104.37
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:38 | LN:115:133 | 168 | 181 | 104.36
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | B:Hunt67 | 168 | 181 | 104.34
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 168 | 181 | 104.3
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 168 | 181 | 104.3
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 168 | 181 | 104.3
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 168 | 181 | 104.3
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:ROCH_2T8082 | 168 | 181 | 104.28
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | LN:115:37 | 168 | 181 | 104.21
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - KINTIGH 345 | LN:115:129 | 168 | 181 | 104.11
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 168 | 181 | 104.09
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:37 | LN:115:129 | 168 | 181 | 104.04
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | PACKARD 230/115 3TR | 168 | 181 | 104.02
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | G:BRUCE5 | 168 | 181 | 104.01
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:ROCH_34XC | 168 | 181 | 103.98
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | T:40&41 | 168 | 181 | 103.98
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 3TR | LN:115:129 | 168 | 181 | 103.97
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | LN:115:36 | 168 | 181 | 103.96
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 168 | 181 | 103.91
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:NIAG345_3308 | 168 | 181 | 103.88
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:HUNT230_R1202 | 168 | 181 | 103.87
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:HUNT230_R1302 | 168 | 181 | 103.85
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:36 | LN:115:129 | 168 | 181 | 103.79
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 168 | 181 | 103.78
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | B:PACKT3 | 168 | 181 | 103.78
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | NIAG - KINTIGH 345 | 168 | 181 | 103.78
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HCMB/NWES | T:77&78 | 168 | 181 | 103.78
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:129 | 168 | 181 | 103.78
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 168 | 181 | 103.77
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:255_345B202 | 168 | 181 | 103.7
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 168 | 181 | 103.7
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SOMERSET - NEWROCH 1 345 | 168 | 181 | 103.63
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:129 | 168 | 181 | 103.63
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | LN:115:133 | 168 | 181 | 103.62
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:KINT_39-B112 | 168 | 181 | 103.62
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:ROCH_3414 | 168 | 181 | 103.56
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:ROCH_3514 | 168 | 181 | 103.56
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:KINT_B1-3812 | 168 | 181 | 103.55
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | G:DARLIN1 | 168 | 181 | 103.5
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:129 | 168 | 181 | 103.43
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:129 | 168 | 181 | 103.42
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI1 | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.39
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 1TR | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.39
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:129 | 168 | 181 | 103.37
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 168 | 181 | 103.12
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 168 | 181 | 103.11
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 168 | 181 | 103.08
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 168 | 181 | 103.07
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 168 | 181 | 103.04
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | S:PA_HNTL77 | 168 | 181 | 102.91
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI1 | DCT:230:79+80+ELM1-2 | 168 | 181 | 102.85
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 1TR | DCT:230:79+80+ELM1-2 | 168 | 181 | 102.85
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | HUNTLEY - PACKARD 78 230 | 168 | 181 | 102.81
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | S:PA_HNTL78 | 168 | 181 | 102.81
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:908 NY | DCT:230:79+80+ELM1-2 | 168 | 181 | 102.81
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | HUNTLEY - PACKARD 77 230 | 168 | 181 | 102.76
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3230 | 168 | 181 | 102.73
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 168 | 181 | 102.68
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | T:61&64 | 168 | 181 | 102.62
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 168 | 181 | 102.62
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI1 | T:79&80 | 168 | 181 | 102.55
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 1TR | T:79&80 | 168 | 181 | 102.55
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | B:Hunt68 | 168 | 181 | 102.36
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | T:77&80 | 168 | 181 | 102.36
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:908 NY | T:79&80 | 168 | 181 | 102.22
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1502 | 168 | 181 | 102.22
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | LN:115:908 NY | 168 | 181 | 102.15
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 168 | 181 | 102.12
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1402 | 168 | 181 | 102.11
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | T:78&79 | 168 | 181 | 102.11
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:908 NY | LN:115:129 | 168 | 181 | 102.1
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 168 | 181 | 102.1
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 168 | 181 | 102.06
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 102.05
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:100 | DCT:230:79+80+ELM1-2 | 168 | 181 | 102.04
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 3TR | DCT:230:79+80+ELM1-2 | 168 | 181 | 102.03
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 168 | 181 | 102
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | GEN:345:SOMERSET | T:77&78 | 168 | 181 | 101.78
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | GEN:KINTIGH | T:77&78 | 168 | 181 | 101.78
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI1 | T:79&80 | 168 | 181 | 101.69
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 1TR | T:79&80 | 168 | 181 | 101.69
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SB:ROBI230 | 168 | 181 | 101.54
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:100 | T:79&80 | 168 | 181 | 101.45
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | DCT:230:79+80+ELM1-2 | 168 | 181 | 101.44
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | DCT:230:79+80+ELM1-2 | 168 | 181 | 101.44
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 3TR | T:79&80 | 168 | 181 | 101.23
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 168 | 181 | 101.19
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:PA230_R3430 | 168 | 181 | 101.14
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | LN:115:100 | 168 | 181 | 101.12
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:ROB | DCT:230:79+80+ELM1-2 | 168 | 181 | 101.1
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:100 | LN:115:129 | 168 | 181 | 101.07
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:NIAW230_2014 | 168 | 181 | 100.98
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | Base Case | 168 | 181 | 100.95
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | T:79&80 | 168 | 181 | 100.93
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | T:79&80 | 168 | 181 | 100.93
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.89
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.87
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 168 | 181 | 100.86
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI1 | LN:115:129 | 168 | 181 | 100.77
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 1TR | LN:115:129 | 168 | 181 | 100.77
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.75
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - ELM 70 230 | T:79&80 | 168 | 181 | 100.72
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - KINTIGH 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.7
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.68
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_NEW | 168 | 181 | 100.6
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | TB:2/1:NI1 | 168 | 181 | 100.59
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | NIAGARA 230/115 1TR | 168 | 181 | 100.59
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 168 | 181 | 100.51
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:ROB | T:79&80 | 168 | 181 | 100.51
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.41
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3230 | 168 | 181 | 100.35
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:182N | T:79&80 | 168 | 181 | 100.31
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:LOCKPORT | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.31
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | WTHRS - MEYER 230 | T:77&78 | 168 | 181 | 100.3
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 168 | 181 | 100.28
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HCWC/NWES | T:77&78 | 168 | 181 | 100.28
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:MBWC/NWES | T:77&78 | 168 | 181 | 100.28
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:UDG-184 | T:77&78 | 168 | 181 | 100.28
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:101 | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.26
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | SB:255_345B302 | 168 | 181 | 100.25
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | SB:GARD230_R823 | 168 | 181 | 100.2
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | DUNKIRK - SRIPL 68 230 | 168 | 181 | 100.16
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SB:SRIPLEY | 168 | 181 | 100.16
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | SB:NIAG345_3108 | 168 | 181 | 100.16
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | R:EESR/NWES | 168 | 181 | 100.14
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SRIPL - ERIE E 69 230 | 168 | 181 | 100.13
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.12
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:102 | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.1
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 168 | 181 | 100.08
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | NIAG - NEWROCH 1 345 | 168 | 181 | 100.07
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:DUPONT46 | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.07
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1202 | 168 | 181 | 100.05
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | TB:2/1:ROB | 168 | 181 | 100.04
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:119 | 168 | 181 | 100.04
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | T:61&64 | 168 | 181 | 100.04
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:180 | T:79&80 | 168 | 181 | 100.01
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - KINTIGH 345 | T:79&80 | 168 | 181 | 100
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 Max |  |  |  |  | 153.38
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 168 | 181 | NConv
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 168 | 181 | NConv
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 168 | 181 | NConv
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 168 | 181 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 168 | 181 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 168 | 181 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:77&78 | 168 | 181 | 152.85
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:77&78 | 168 | 181 | 146.79
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 168 | 181 | 138.91
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 168 | 181 | 138.14
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:79&80 | 168 | 181 | 137.07
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 168 | 181 | 136.82
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:NIAW230_2014 | 168 | 181 | 135.12
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 181 | 134.68
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA 230/115 2TR | 168 | 181 | 132.25
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:NI2 | 168 | 181 | 132.25
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI2 | LN:115:130 | 168 | 181 | 132.13
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | LN:115:130 | 168 | 181 | 132.13
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 168 | 181 | 132.08
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 181 | 132
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:79&80 | 168 | 181 | 130.77
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R3430 | 168 | 181 | 127.56
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 168 | 181 | 127.51
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 181 | 126.35
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 168 | 181 | 125.94
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:61&64 | 168 | 181 | 125.67
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 125.1
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 168 | 181 | 124.89
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 168 | 181 | 124.71
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:ROBI230 | 168 | 181 | 124.29
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 124.21
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 168 | 181 | 123.78
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1502 | 168 | 181 | 123.32
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R3230 | 168 | 181 | 123.25
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt68 | 168 | 181 | 123.25
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:78&79 | 168 | 181 | 123.08
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1402 | 168 | 181 | 123.08
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:77&80 | 168 | 181 | 123.06
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R506 | 168 | 181 | 122.61
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 181 | 122.6
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:130 | 168 | 181 | 122.34
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:255_345B302 | 168 | 181 | 122.32
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 168 | 181 | 122.18
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:PACKT4 | 168 | 181 | 122.15
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:NIAG345_3108 | 168 | 181 | 122.15
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 122.14
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAG - NEWROCH 1 345 | 168 | 181 | 122.12
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_NEW | 168 | 181 | 121.66
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 168 | 181 | 120.92
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt67 | 168 | 181 | 120.89
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1302 | 168 | 181 | 120.69
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1202 | 168 | 181 | 120.65
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:PK4 | 168 | 181 | 120.59
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | PACKARD 230/115 4TR | 168 | 181 | 120.59
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:255_345B202 | 168 | 181 | 120.55
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SOMERSET - NEWROCH 1 345 | 168 | 181 | 120.48
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:PK4 | LN:115:130 | 168 | 181 | 120.46
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | LN:115:130 | 168 | 181 | 120.46
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:130 | 168 | 181 | 120.3
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:130 | 168 | 181 | 120.24
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL77 | 168 | 181 | 119.78
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 168 | 181 | 119.75
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 78 230 | 168 | 181 | 119.67
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL78 | 168 | 181 | 119.67
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 77 230 | 168 | 181 | 119.62
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 168 | 181 | 119.19
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:61&64 | 168 | 181 | 118.88
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | Base Case | 168 | 181 | 118.77
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:908 NY | 168 | 181 | 118.26
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 118.23
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:908 NY | LN:115:130 | 168 | 181 | 118.21
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI1 | T:77&78 | 168 | 181 | 118.18
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | T:77&78 | 168 | 181 | 118.18
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:ROBI230 | 168 | 181 | 117.74
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI1 | T:77&78 | 168 | 181 | 117.66
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | T:77&78 | 168 | 181 | 117.66
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 168 | 181 | 117.17
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:100 | 168 | 181 | 117.03
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:100 | LN:115:130 | 168 | 181 | 116.98
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R3230 | 168 | 181 | 116.88
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_R823 | 168 | 181 | 116.71
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | T:77&78 | 168 | 181 | 116.65
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_R833 | 168 | 181 | 116.38
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:130 | 168 | 181 | 116.37
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:908 NY | T:77&78 | 168 | 181 | 116.36
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:130 | 168 | 181 | 116.36
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_T7-12 | 168 | 181 | 116.28
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:GARD72&79 | 168 | 181 | 116.24
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | S:HNT_GRD80 | 168 | 181 | 116.14
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - GARDENVILL 79 230 | 168 | 181 | 116.05
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - GARDENVILL 80 230 | 168 | 181 | 116.04
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:ROB | 168 | 181 | 115.88
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt68 | 168 | 181 | 115.86
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 115.86
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:ROB | LN:115:130 | 168 | 181 | 115.78
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_R873 | 168 | 181 | 115.77
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 115.77
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:77&80 | 168 | 181 | 115.71
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1502 | 168 | 181 | 115.59
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:100 | T:77&78 | 168 | 181 | 115.5
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:GARD73&80 | 168 | 181 | 115.42
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1402 | 168 | 181 | 115.39
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:78&79 | 168 | 181 | 115.39
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:182N | T:77&78 | 168 | 181 | 115.29
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:180 | T:77&78 | 168 | 181 | 114.97
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:182S | T:77&78 | 168 | 181 | 114.89
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:130 | 168 | 181 | 114.73
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:130 | 168 | 181 | 114.7
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:181/922 | T:77&78 | 168 | 181 | 114.67
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:255_345B302 | 168 | 181 | 114.66
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 168 | 181 | 114.61
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:ROB | T:77&78 | 168 | 181 | 114.6
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | G:LOCKPORT | 168 | 181 | 114.6
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:STOLE230 | 168 | 181 | 114.6
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 168 | 181 | 114.54
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 168 | 181 | 114.5
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:NIAG345_3108 | 168 | 181 | 114.49
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:LOCKPORT | LN:115:130 | 168 | 181 | 114.49
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | T:77&78 | 168 | 181 | 114.48
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:101 | 168 | 181 | 114.43
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:130 | 168 | 181 | 114.43
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAG - NEWROCH 1 345 | 168 | 181 | 114.42
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | STOLLRD - GARDENVILL 66 230 | 168 | 181 | 114.36
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:101 | LN:115:130 | 168 | 181 | 114.29
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI1 | LN:115:130 | 168 | 181 | 114.2
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 168 | 181 | 114.2
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | LN:115:130 | 168 | 181 | 114.2
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | ROBINSON - STOLLRD 65 230 | 168 | 181 | 114.18
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:NI1 | 168 | 181 | 114.18
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA 230/115 1TR | 168 | 181 | 114.18
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:102 | 168 | 181 | 114.18
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 168 | 181 | 114.17
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 168 | 181 | 114.17
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:LOCKPORT | T:77&78 | 168 | 181 | 114.15
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | T:77&78 | 168 | 181 | 114.07
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:102 | LN:115:130 | 168 | 181 | 114.04
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 168 | 181 | 114.04
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:907 NY | 168 | 181 | 113.96
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | First:Lockport_907 | 168 | 181 | 113.93
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | FARMVLY - HOMERCTY | 168 | 181 | 113.91
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_NEW | 168 | 181 | 113.88
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:907 NY | LN:115:130 | 168 | 181 | 113.88
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | T:77&78 | 168 | 181 | 113.88
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | R:HC-FV_37&W-F_171 | 168 | 181 | 113.86
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:120 | 168 | 181 | 113.83
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | First:Lockport_907 | LN:115:130 | 168 | 181 | 113.83
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:101 | T:77&78 | 168 | 181 | 113.79
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:DUPONT46 | T:77&78 | 168 | 181 | 113.79
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:DUPONT46 | LN:115:130 | 168 | 181 | 113.76
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:120 | LN:115:130 | 168 | 181 | 113.72
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:102 | T:77&78 | 168 | 181 | 113.62
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 113.6
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 168 | 181 | 113.57
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:37 | 168 | 181 | 113.52
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:345:37S-FM-FV | T:77&78 | 168 | 181 | 113.48
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:120 | T:77&78 | 168 | 181 | 113.44
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt67 | 168 | 181 | 113.42
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:37 | LN:115:130 | 168 | 181 | 113.38
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_2T8082 | 168 | 181 | 113.31
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:907 NY | T:77&78 | 168 | 181 | 113.28
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | First:Lockport_907 | T:77&78 | 168 | 181 | 113.25
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:36 | 168 | 181 | 113.24
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | LN:115:130 | 168 | 181 | 113.15
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:36 | LN:115:130 | 168 | 181 | 113.09
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 168 | 181 | 113.08
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 113.08
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:37 | T:77&78 | 168 | 181 | 113.06
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | PACKARD 230/115 3TR | 168 | 181 | 113.04
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | LN:115:130 | 168 | 181 | 113.02
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_34XC | 168 | 181 | 112.98
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:40&41 | 168 | 181 | 112.98
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1202 | 168 | 181 | 112.9
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:36 | T:77&78 | 168 | 181 | 112.89
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1302 | 168 | 181 | 112.88
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:908 NY | T:77&78 | 168 | 181 | 112.88
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:NIAG345_3308 | 168 | 181 | 112.87
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:130 | 168 | 181 | 112.8
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:PACKT3 | 168 | 181 | 112.79
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAG - KINTIGH 345 | 168 | 181 | 112.76
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:255_345B202 | 168 | 181 | 112.71
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SOMERSET - NEWROCH 1 345 | 168 | 181 | 112.63
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:KINT_39-B112 | 168 | 181 | 112.61
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 4 | LN:115:130 | 168 | 181 | 112.57
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 5 | LN:115:130 | 168 | 181 | 112.57
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 6 | LN:115:130 | 168 | 181 | 112.57
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 7 | LN:115:130 | 168 | 181 | 112.56
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:KINT_B1-3812 | 168 | 181 | 112.54
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_3414 | 168 | 181 | 112.53
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_3514 | 168 | 181 | 112.53
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:130 | 168 | 181 | 112.43
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:130 | 168 | 181 | 112.41
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:130 | 168 | 181 | 112.37
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 112.28
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | LN:115:130 | 168 | 181 | 112.25
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | LN:115:130 | 168 | 181 | 112.24
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 112.23
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:182N | LN:115:130 | 168 | 181 | 112.23
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 168 | 181 | 112.22
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:100 | T:77&78 | 168 | 181 | 112.13
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL77 | 168 | 181 | 111.85
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 78 230 | 168 | 181 | 111.74
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL78 | 168 | 181 | 111.74
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 77 230 | 168 | 181 | 111.69
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 168 | 181 | 111.65
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 168 | 181 | 111.65
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 168 | 181 | 111.65
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 168 | 181 | 111.65
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 168 | 181 | 111.32
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 168 | 181 | 111.25
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:ROB | T:77&78 | 168 | 181 | 111.23
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 168 | 181 | 111.23
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:908 NY | 168 | 181 | 111.06
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:908 NY | LN:115:130 | 168 | 181 | 111.04
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI2 | B:PACKT4 | 168 | 181 | 110.99
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | B:PACKT4 | 168 | 181 | 110.99
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI2 | SB:PA230_R506 | 168 | 181 | 110.96
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | SB:PA230_R506 | 168 | 181 | 110.96
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:PK4 | TB:2/1:NI2 | 168 | 181 | 110.94
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:PK4 | NIAGARA 230/115 2TR | 168 | 181 | 110.94
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI2 | PACKARD 230/115 4TR | 168 | 181 | 110.94
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI2 | TB:2/1:PK4 | 168 | 181 | 110.94
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | PACKARD 230/115 4TR | 168 | 181 | 110.94
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | TB:2/1:PK4 | 168 | 181 | 110.94
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | TB:2/1:NI2 | 168 | 181 | 110.94
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | NIAGARA 230/115 2TR | 168 | 181 | 110.94
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI2 | SB:PA230_R3430 | 168 | 181 | 110.93
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | SB:PA230_R3430 | 168 | 181 | 110.93
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:PK4 | SB:NIAW230_2014 | 168 | 181 | 110.83
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | SB:NIAW230_2014 | 168 | 181 | 110.83
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:NIAW230_2014 | 168 | 181 | 110.71
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:182N | T:77&78 | 168 | 181 | 110.7
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 168 | 181 | 110.64
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R3430 | 168 | 181 | 110.56
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 168 | 181 | 110.55
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 168 | 181 | 110.52
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | T:77&78 | 168 | 181 | 110.41
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 168 | 181 | 110.35
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:180 | T:77&78 | 168 | 181 | 110.32
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:182S | T:77&78 | 168 | 181 | 110.28
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 168 | 181 | 110.19
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 168 | 181 | 110.19
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 168 | 181 | 110.18
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:181/922 | T:77&78 | 168 | 181 | 110.12
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:100 | 168 | 181 | 109.95
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:100 | LN:115:130 | 168 | 181 | 109.92
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 168 | 181 | 109.88
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 168 | 181 | 109.88
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:907 NY | T:77&78 | 168 | 181 | 109.87
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 168 | 181 | 109.85
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | First:Lockport_907 | T:77&78 | 168 | 181 | 109.84
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:LOCKPORT | T:77&78 | 168 | 181 | 109.79
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | Base Case | 168 | 181 | 109.76
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 168 | 181 | 109.69
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 168 | 181 | 109.68
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 109.65
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI1 | LN:115:130 | 168 | 181 | 109.6
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | LN:115:130 | 168 | 181 | 109.6
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | T:77&78 | 168 | 181 | 109.54
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:NI1 | 168 | 181 | 109.37
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA 230/115 1TR | 168 | 181 | 109.37
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:DUPONT46 | T:77&78 | 168 | 181 | 109.36
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:345:37S-FM-FV | T:77&78 | 168 | 181 | 109.32
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 168 | 181 | 109.31
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:101 | T:77&78 | 168 | 181 | 109.04
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_R823 | 168 | 181 | 108.96
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:102 | T:77&78 | 168 | 181 | 108.89
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:37 | T:77&78 | 168 | 181 | 108.86
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 168 | 181 | 108.81
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:120 | T:77&78 | 168 | 181 | 108.79
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:ROB | 168 | 181 | 108.79
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | CAP:115:GV1 | T:77&78 | 168 | 181 | 108.78
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | CAP:115:GV2 | T:77&78 | 168 | 181 | 108.78
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:ROB | LN:115:130 | 168 | 181 | 108.72
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:36 | T:77&78 | 168 | 181 | 108.69
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_R833 | 168 | 181 | 108.63
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 11 | T:77&78 | 168 | 181 | 108.6
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 12 | T:77&78 | 168 | 181 | 108.6
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 13 | T:77&78 | 168 | 181 | 108.6
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 8 | T:77&78 | 168 | 181 | 108.6
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 9 | T:77&78 | 168 | 181 | 108.6
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 10 | T:77&78 | 168 | 181 | 108.59
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:130 | 168 | 181 | 108.41
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 168 | 181 | 108.4
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:130 | 168 | 181 | 108.4
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_T7-12 | 168 | 181 | 108.29
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:GARD72&79 | 168 | 181 | 108.29
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:114 | 168 | 181 | 108.22
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:113 | 168 | 181 | 108.18
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | S:HNT_GRD80 | 168 | 181 | 108.15
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:111 | 168 | 181 | 108.15
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | DUNKIRK - SRIPL 68 230 | 168 | 181 | 108.06
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:SRIPLEY | 168 | 181 | 108.06
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - GARDENVILL 79 230 | 168 | 181 | 108.05
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - GARDENVILL 80 230 | 168 | 181 | 108.04
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:113 | LN:115:130 | 168 | 181 | 108.03
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | R:EESR/NWES | 168 | 181 | 108.03
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SRIPL - ERIE E 69 230 | 168 | 181 | 108.03
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:111 | LN:115:130 | 168 | 181 | 107.97
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 168 | 181 | 107.8
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_R873 | 168 | 181 | 107.78
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:119 | 168 | 181 | 107.74
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 11 | LN:115:130 | 168 | 181 | 107.73
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 12 | LN:115:130 | 168 | 181 | 107.73
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 13 | LN:115:130 | 168 | 181 | 107.73
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:UDG-184 | T:77&78 | 168 | 181 | 107.73
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 8 | LN:115:130 | 168 | 181 | 107.72
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 9 | LN:115:130 | 168 | 181 | 107.72
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 10 | LN:115:130 | 168 | 181 | 107.71
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 168 | 181 | 107.68
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:PK4 | T:77&78 | 168 | 181 | 107.66
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | T:77&78 | 168 | 181 | 107.66
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | WTHRS - MEYER 230 | T:77&78 | 168 | 181 | 107.63
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:119 | LN:115:130 | 168 | 181 | 107.62
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 168 | 181 | 107.58
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HCWC/NWES | T:77&78 | 168 | 181 | 107.58
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:MBWC/NWES | T:77&78 | 168 | 181 | 107.58
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | R:DKSR/WRFL | 168 | 181 | 107.47
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-WC_30&W-F_171 | LN:115:130 | 168 | 181 | 107.44
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | R:EESR/WRFL | 168 | 181 | 107.43
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | R:EESR/WF/NWES | 168 | 181 | 107.43
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | WTRCR - MAINSBRG 30A 345 | LN:115:130 | 168 | 181 | 107.42
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:GARD73&80 | 168 | 181 | 107.41
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:MEYER | 168 | 181 | 107.41
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | WTHRS - MEYER 230 | 168 | 181 | 107.41
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HCWC/NWES | LN:115:130 | 168 | 181 | 107.41
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:MBWC/NWES | LN:115:130 | 168 | 181 | 107.41
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 168 | 181 | 107.34
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 168 | 181 | 107.34
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 168 | 181 | 107.34
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 168 | 181 | 107.34
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 168 | 181 | 107.19
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:68&160 | 168 | 181 | 107.19
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 168 | 181 | 107.01
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 168 | 181 | 107
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 168 | 181 | 106.94
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HCMB/NWES | LN:115:130 | 168 | 181 | 106.84
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-MB_30&W-F_171 | LN:115:130 | 168 | 181 | 106.8
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HCMB/NWES | T:77&78 | 168 | 181 | 106.79
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | MAINSBRG - HOMERCITY 30B 345 | LN:115:130 | 168 | 181 | 106.77
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:907 NY | 168 | 181 | 106.76
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | First:Lockport_907 | 168 | 181 | 106.73
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 168 | 181 | 106.72
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:907 NY | LN:115:130 | 168 | 181 | 106.7
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | First:Lockport_907 | LN:115:130 | 168 | 181 | 106.66
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:130 | 168 | 181 | 106.52
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:STOLE230 | 168 | 181 | 106.41
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:130 | 168 | 181 | 106.41
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI1 | DCT:230:79+80+ELM1-2 | 168 | 181 | 106.38
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | DCT:230:79+80+ELM1-2 | 168 | 181 | 106.38
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | LN:115:130 | 168 | 181 | 106.26
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | G:LOCKPORT | 168 | 181 | 106.25
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | PACKARD 230/115 3TR | 168 | 181 | 106.2
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | STOLLRD - GARDENVILL 66 230 | 168 | 181 | 106.17
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:LOCKPORT | LN:115:130 | 168 | 181 | 106.14
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 168 | 181 | 106.06
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 168 | 181 | 106.05
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 168 | 181 | 106.01
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 168 | 181 | 106
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | ROBINSON - STOLLRD 65 230 | 168 | 181 | 105.97
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 168 | 181 | 105.97
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:PACKT3 | 168 | 181 | 105.89
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:908 NY | DCT:230:79+80+ELM1-2 | 168 | 181 | 105.86
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI1 | DCT:230:79+80+ELM1-2 | 168 | 181 | 105.8
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | DCT:230:79+80+ELM1-2 | 168 | 181 | 105.8
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 168 | 181 | 105.76
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | GEN:345:SOMERSET | T:77&78 | 168 | 181 | 105.71
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | GEN:KINTIGH | T:77&78 | 168 | 181 | 105.71
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 168 | 181 | 105.7
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3230 | 168 | 181 | 105.67
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:61&64 | 168 | 181 | 105.66
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:DUPONT46 | LN:115:130 | 168 | 181 | 105.65
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:UDG-184 | LN:115:130 | 168 | 181 | 105.64
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | FARMVLY - HOMERCTY | 168 | 181 | 105.58
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | GEN:345:SOMERSET | 168 | 181 | 105.58
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | GEN:KINTIGH | 168 | 181 | 105.58
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:101 | 168 | 181 | 105.57
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 168 | 181 | 105.56
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI1 | T:79&80 | 168 | 181 | 105.55
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | T:79&80 | 168 | 181 | 105.55
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | R:HC-FV_37&W-F_171 | 168 | 181 | 105.54
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:101 | LN:115:130 | 168 | 181 | 105.44
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 168 | 181 | 105.44
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:77&80 | 168 | 181 | 105.43
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | B:Hunt68 | 168 | 181 | 105.41
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:102 | 168 | 181 | 105.35
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R506 | 168 | 181 | 105.34
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 168 | 181 | 105.3
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:908 NY | T:79&80 | 168 | 181 | 105.29
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 168 | 181 | 105.26
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:102 | LN:115:130 | 168 | 181 | 105.22
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1502 | 168 | 181 | 105.19
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:120 | 168 | 181 | 105.1
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | DCT:230:79+80+ELM1-2 | 168 | 181 | 105.09
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 105.08
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1402 | 168 | 181 | 105.08
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:78&79 | 168 | 181 | 105.08
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:37 | 168 | 181 | 105.07
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | GEN:345:SOMERSET | LN:115:130 | 168 | 181 | 105.06
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:100 | DCT:230:79+80+ELM1-2 | 168 | 181 | 105.06
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | GEN:KINTIGH | LN:115:130 | 168 | 181 | 105.06
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | LN:115:130 | 168 | 181 | 105.04
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_2T8082 | 168 | 181 | 105.02
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | CAP:115:HUN | 168 | 181 | 105.01
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:120 | LN:115:130 | 168 | 181 | 105
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | CAP:115:HUN | LN:115:130 | 168 | 181 | 104.95
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:37 | LN:115:130 | 168 | 181 | 104.94
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA 230/115 2TR | 168 | 181 | 104.87
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:NI2 | 168 | 181 | 104.87
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:PACKT4 | 168 | 181 | 104.86
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI2 | LN:115:130 | 168 | 181 | 104.83
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | LN:115:130 | 168 | 181 | 104.83
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R304 | 168 | 181 | 104.82
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:36 | 168 | 181 | 104.79
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:NIAG345_3308 | 168 | 181 | 104.72
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_34XC | 168 | 181 | 104.69
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI1 | T:79&80 | 168 | 181 | 104.66
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:36 | LN:115:130 | 168 | 181 | 104.66
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | T:79&80 | 168 | 181 | 104.66
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | T:40&41 | 168 | 181 | 104.64
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAG - KINTIGH 345 | 168 | 181 | 104.59
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:ROBI230 | 168 | 181 | 104.58
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:100 | T:79&80 | 168 | 181 | 104.49
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:130 | 168 | 181 | 104.47
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | CAP:115:GV1 | T:77&78 | 168 | 181 | 104.44
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | CAP:115:GV2 | T:77&78 | 168 | 181 | 104.44
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:KINT_39-B112 | 168 | 181 | 104.43
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI2 | DCT:230:79+80+ELM1-2 | 168 | 181 | 104.42
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | DCT:230:79+80+ELM1-2 | 168 | 181 | 104.42
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:KINT_B1-3812 | 168 | 181 | 104.36
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | T:79&80 | 168 | 181 | 104.3
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 168 | 181 | 104.29
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_3414 | 168 | 181 | 104.23
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_3514 | 168 | 181 | 104.23
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:ROB | DCT:230:79+80+ELM1-2 | 168 | 181 | 104.15
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:130 | 168 | 181 | 104.08
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:345:37S-FM-FV-HC | 168 | 181 | 103.99
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.98
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.98
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:5MILE_B | 168 | 181 | 103.96
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:39 | 168 | 181 | 103.95
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | LN:115:130 | 168 | 181 | 103.92
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI2 | T:79&80 | 168 | 181 | 103.91
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:38 | 168 | 181 | 103.91
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | T:79&80 | 168 | 181 | 103.91
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SB:LAFA_ELB | 168 | 181 | 103.9
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | LN:115:130 | 168 | 181 | 103.9
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:39 | LN:115:130 | 168 | 181 | 103.9
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:38 | LN:115:130 | 168 | 181 | 103.85
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - ELM 70 230 | T:79&80 | 168 | 181 | 103.85
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.83
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 168 | 181 | 103.81
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.8
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.77
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:LOCKPORT | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.65
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:ROB | T:79&80 | 168 | 181 | 103.58
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_NEW | 168 | 181 | 103.57
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 168 | 181 | 103.51
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | G:BRUCE5 | 168 | 181 | 103.51
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.51
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:182N | T:79&80 | 168 | 181 | 103.43
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:UDG-184 | T:77&78 | 168 | 181 | 103.38
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | WTHRS - MEYER 230 | T:77&78 | 168 | 181 | 103.35
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:101 | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.32
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 11 | T:77&78 | 168 | 181 | 103.3
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 12 | T:77&78 | 168 | 181 | 103.3
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 13 | T:77&78 | 168 | 181 | 103.3
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 8 | T:77&78 | 168 | 181 | 103.29
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 9 | T:77&78 | 168 | 181 | 103.29
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 168 | 181 | 103.28
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HCWC/NWES | T:77&78 | 168 | 181 | 103.28
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:MBWC/NWES | T:77&78 | 168 | 181 | 103.28
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:NIAG. 10 | T:77&78 | 168 | 181 | 103.28
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:255_345B302 | 168 | 181 | 103.27
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:DUPONT46 | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.27
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3230 | 168 | 181 | 103.24
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.23
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 168 | 181 | 103.2
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:NIAG345_3108 | 168 | 181 | 103.18
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:102 | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.15
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:180 | T:79&80 | 168 | 181 | 103.11
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | NIAG - NEWROCH 1 345 | 168 | 181 | 103.09
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:LOCKPORT | T:79&80 | 168 | 181 | 103.08
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 168 | 181 | 103.08
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_NEW | 168 | 181 | 103.08
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:61&64 | 168 | 181 | 103.07
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | T:79&80 | 168 | 181 | 103.07
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | G:DARLIN1 | 168 | 181 | 103
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:120 | DCT:230:79+80+ELM1-2 | 168 | 181 | 102.99
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:181/922 | T:79&80 | 168 | 181 | 102.99
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:182S | T:79&80 | 168 | 181 | 102.99
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1202 | 168 | 181 | 102.99
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | B:Hunt67 | 168 | 181 | 102.97
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:907 NY | DCT:230:79+80+ELM1-2 | 168 | 181 | 102.9
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | First:Lockport_907 | DCT:230:79+80+ELM1-2 | 168 | 181 | 102.89
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3230 | 168 | 181 | 102.81
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1302 | 168 | 181 | 102.79
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:79&80 | 168 | 181 | 102.75
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:101 | T:79&80 | 168 | 181 | 102.74
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:DUPONT46 | T:79&80 | 168 | 181 | 102.7
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 168 | 181 | 102.66
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | B:Hunt68 | 168 | 181 | 102.63
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:77&80 | 168 | 181 | 102.61
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:102 | T:79&80 | 168 | 181 | 102.58
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:345:37S-FM-FV-HC | DCT:230:79+80+ELM1-2 | 168 | 181 | 102.56
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 102.56
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | DCT:230:79+80+ELM1-2 | 168 | 181 | 102.54
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | T:79&80 | 168 | 181 | 102.54
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | R:HCMB/NWES | T:77&78 | 168 | 181 | 102.5
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:908 NY | DCT:230:79+80+ELM1-2 | 168 | 181 | 102.41
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 168 | 181 | 102.41
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:120 | T:79&80 | 168 | 181 | 102.41
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | T:79&80 | 168 | 181 | 102.38
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1502 | 168 | 181 | 102.37
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:907 NY | T:79&80 | 168 | 181 | 102.33
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | First:Lockport_907 | T:79&80 | 168 | 181 | 102.3
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1402 | 168 | 181 | 102.24
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:78&79 | 168 | 181 | 102.24
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | SB:255_345B302 | 168 | 181 | 102.11
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | NIAG - NEWROCH 1 345 | 168 | 181 | 102.05
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:ROBI230 | 168 | 181 | 102.03
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 168 | 181 | 102.02
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | SB:NIAG345_3108 | 168 | 181 | 101.87
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:100 | DCT:230:79+80+ELM1-2 | 168 | 181 | 101.72
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 168 | 181 | 101.68
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:77&80 | 168 | 181 | 101.67
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:908 NY | T:79&80 | 168 | 181 | 101.66
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL77 | 168 | 181 | 101.66
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL78 | 168 | 181 | 101.63
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 78 230 | 168 | 181 | 101.63
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | T:61&64 | 168 | 181 | 101.63
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | B:Hunt68 | 168 | 181 | 101.62
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 168 | 181 | 101.62
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 168 | 181 | 101.61
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 168 | 181 | 101.6
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 77 230 | 168 | 181 | 101.59
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 168 | 181 | 101.57
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 168 | 181 | 101.55
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:255_345B202 | 168 | 181 | 101.55
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 101.51
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SOMERSET - NEWROCH 1 345 | 168 | 181 | 101.48
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | T:79&80 | 168 | 181 | 101.47
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 101.46
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:61&64 | 168 | 181 | 101.39
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1502 | 168 | 181 | 101.39
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1402 | 168 | 181 | 101.33
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:78&79 | 168 | 181 | 101.33
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | GEN:345:SOMERSET | T:77&78 | 168 | 181 | 101.28
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | GEN:KINTIGH | T:77&78 | 168 | 181 | 101.28
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 168 | 181 | 101.27
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 168 | 181 | 101.21
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_NEW | 168 | 181 | 101.09
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:OXBOWNUG | LN:115:130 | 168 | 181 | 101.03
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:100 | T:79&80 | 168 | 181 | 100.97
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:77&80 | 168 | 181 | 100.81
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:OXBOWNUG | T:77&78 | 168 | 181 | 100.81
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:ROB | DCT:230:79+80+ELM1-2 | 168 | 181 | 100.8
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 100.74
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | T:78&79 | 168 | 181 | 100.74
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | T:77&80 | 168 | 181 | 100.72
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | B:Hunt68 | 168 | 181 | 100.71
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | B:Hunt67 | 168 | 181 | 100.66
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R823 | 168 | 181 | 100.66
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 168 | 181 | 100.56
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 168 | 181 | 100.53
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3230 | 168 | 181 | 100.51
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1202 | 168 | 181 | 100.51
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:ROBI230 | 168 | 181 | 100.5
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 168 | 181 | 100.49
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:NIAW230_2014 | 168 | 181 | 100.45
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1302 | 168 | 181 | 100.44
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 168 | 181 | 100.44
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_R1202 | 168 | 181 | 100.43
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1402 | 168 | 181 | 100.43
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | S:HNT_GRD80 | 168 | 181 | 100.36
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | B:GARD72&79 | 168 | 181 | 100.36
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - GARDENVILL 80 230 | 168 | 181 | 100.35
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - GARDENVILL 79 230 | 168 | 181 | 100.35
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R833 | 168 | 181 | 100.34
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3430 | 168 | 181 | 100.32
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1502 | 168 | 181 | 100.18
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:GARD230_R823 | 168 | 181 | 100.16
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:NIAW230_2014 | 168 | 181 | 100.08
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:78&79 | 168 | 181 | 100.07
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1402 | 168 | 181 | 100.06
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:ROB | T:79&80 | 168 | 181 | 100.05
| 135451 HUNTLEY1 115 135562 S214-133 115 1 Max |  |  |  |  | 152.85
Dispatch 1 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 233 | 253 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 233 | 253 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 233 | 253 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 233 | 253 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 233 | 253 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 233 | 253 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 233 | 253 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 233 | 253 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 233 | 253 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 233 | 253 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | LN:115:102 | LN:115:120 | 233 | 253 | 102.6
Dispatch 2 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | LN:115:120 | LN:115:102 | 233 | 253 | 102.58
| 135452 LOCKPORT 115 135464 SANBORNT 115 1 Max |  |  |  |  | 102.6
Dispatch 1 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 174 | 181 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 174 | 181 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 174 | 181 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 181 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | LN:115:101 | LN:115:102 | 174 | 181 | 114.21
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | LN:115:102 | LN:115:101 | 174 | 181 | 114.2
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 174 | 181 | 105.22
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 174 | 181 | 105.11
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | NIAG - NEWROCH 1 345 | LN:115:101 | 174 | 181 | 100.4
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | LN:115:908 NY | LN:115:101 | 174 | 181 | 100.39
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | LN:115:101 | LN:115:908 NY | 174 | 181 | 100.38
| 135452 LOCKPORT 115 135467 SHAW-103 115 1 Max |  |  |  |  | 114.21
Dispatch 1 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 233 | 253 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 233 | 253 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 233 | 253 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 233 | 253 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 233 | 253 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 233 | 253 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 233 | 253 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 233 | 253 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 233 | 253 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 233 | 253 | NConv
| 135452 LOCKPORT 115 135510 SHAW-102 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 143 | 165 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 165 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 143 | 165 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 143 | 165 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 143 | 165 | 121.36
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 143 | 165 | 121.26
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 143 | 165 | 119.18
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 143 | 165 | 119.09
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 143 | 165 | 102.83
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 143 | 165 | 102.74
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 143 | 165 | 100.85
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 143 | 165 | 100.77
| 135452 LOCKPORT 115 135851 SHEL-113 115 1 Max |  |  |  |  | 121.36
Dispatch 1 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 130 | 136 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 130 | 136 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 130 | 136 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 130 | 136 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 130 | 136 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 130 | 136 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 130 | 136 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 130 | 136 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 130 | 136 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 130 | 136 | NConv
| 135452 LOCKPORT 115 135865 NAKR-108 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 131 | 144 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 131 | 144 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 131 | 144 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 131 | 144 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 131 | 144 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 131 | 144 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 131 | 144 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 131 | 144 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 131 | 144 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 131 | 144 | NConv
| 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 199 | 199 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 199 | 199 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 199 | 199 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 199 | 199 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 199 | 199 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 199 | 199 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 199 | 199 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 199 | 199 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 199 | 199 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 199 | 199 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 199 | 199 | 102.37
Dispatch 2 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 199 | 199 | 102.24
Dispatch 1 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 199 | 199 | 100.46
Dispatch 1 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 199 | 199 | 100.34
| 135452 LOCKPORT 115 135872 SOUR-111 115 1 Max |  |  |  |  | 102.37
Dispatch 1 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 220 | 252 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 220 | 252 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 220 | 252 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 220 | 252 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 220 | 252 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 220 | 252 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 220 | 252 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 220 | 252 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 220 | 252 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 220 | 252 | NConv
| 135452 LOCKPORT 115 135875 TELRDTP1 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 143 | 165 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 165 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 143 | 165 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 143 | 165 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | STOLLRD - SHLDON 67 230 | SB:STONYRIDGE | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | STOLLRD - SHLDON 67 230 | S:AVOCA | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | STOLLRD - SHLDON 67 230 | CANDQUA - STNYRDG 68A 230 | 143 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 143 | 165 | 125.62
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 143 | 165 | 125.51
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 143 | 165 | 123.37
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 143 | 165 | 123.27
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 143 | 165 | 106.67
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 143 | 165 | 106.58
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 143 | 165 | 104.69
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 143 | 165 | 104.61
| 135452 LOCKPORT 115 135876 TELRDTP1 115 1 Max |  |  |  |  | 125.62
Dispatch 2 | 135453 LONG-180 115 147850 NIAG115E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 265 | 114.22
Dispatch 1 | 135453 LONG-180 115 147850 NIAG115E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 265 | 111.19
Dispatch 2 | 135453 LONG-180 115 147850 NIAG115E 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 200 | 265 | 101.18
| 135453 LONG-180 115 147850 NIAG115E 115 1 Max |  |  |  |  | 114.22
Dispatch 1 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 298 | NConv
Dispatch 1 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 1 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 298 | NConv
Dispatch 1 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 298 | NConv
Dispatch 1 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 298 | NConv
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 298 | NConv
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 298 | NConv
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | T:77&78 | 239 | 298 | 121.05
Dispatch 1 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | T:77&78 | 239 | 298 | 117.05
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | Base Case | 239 | 298 | 116.54
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 239 | 298 | 111.5
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | T:79&80 | 239 | 298 | 110.88
Dispatch 1 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | Base Case | 239 | 298 | 110.14
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SB:NIAW230_2014 | 239 | 298 | 108.24
Dispatch 1 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 239 | 298 | 107.44
Dispatch 1 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | T:79&80 | 239 | 298 | 106.68
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | TB:2/1:NI2 | 239 | 298 | 106.48
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | NIAGARA 230/115 2TR | 239 | 298 | 106.48
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | TB:2/1:NI2 | LN:115:130 | 239 | 298 | 106.37
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAGARA 230/115 2TR | LN:115:130 | 239 | 298 | 106.37
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SB:PA230_R3430 | 239 | 298 | 103.96
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 239 | 298 | 103.13
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | T:61&64 | 239 | 298 | 102.96
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 239 | 298 | 102.91
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 239 | 298 | 102.62
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SB:ROBI230 | 239 | 298 | 102.13
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | B:Hunt68 | 239 | 298 | 101.91
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | T:77&80 | 239 | 298 | 101.81
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SB:HUNT230_R1502 | 239 | 298 | 101.56
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SB:PA230_R3230 | 239 | 298 | 101.49
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | T:78&79 | 239 | 298 | 101.42
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SB:HUNT230_R1402 | 239 | 298 | 101.42
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:130 | 239 | 298 | 101.22
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SB:255_345B302 | 239 | 298 | 101.2
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SB:NIAG345_3108 | 239 | 298 | 101.07
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | NIAG - NEWROCH 1 345 | 239 | 298 | 101.05
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SB:PA230_R506 | 239 | 298 | 100.93
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | B:PACKT4 | 239 | 298 | 100.65
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SB:HUNT230_NEW | 239 | 298 | 100.54
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | G:OXBOWNUG | LN:115:130 | 239 | 298 | 100.54
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | B:Hunt67 | 239 | 298 | 100.25
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SB:255_345B202 | 239 | 298 | 100.06
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SOMERSET - NEWROCH 1 345 | 239 | 298 | 100.01
| 135454 MLPN-129 115 135461 PACK(S)W 115 1 Max |  |  |  |  | 121.05
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 298 | NConv
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 298 | NConv
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 298 | NConv
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | T:77&78 | 239 | 298 | 125.18
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | T:77&78 | 239 | 298 | 120.97
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | Base Case | 239 | 298 | 120.54
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 239 | 298 | 115.29
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | T:77&78 | 239 | 298 | 114.76
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | T:79&80 | 239 | 298 | 114.66
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | Base Case | 239 | 298 | 113.91
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:NIAW230_2014 | 239 | 298 | 111.35
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 239 | 298 | 111.1
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | T:77&78 | 239 | 298 | 110.87
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | T:79&80 | 239 | 298 | 110.32
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | Base Case | 239 | 298 | 109.74
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | NIAGARA 230/115 2TR | 239 | 298 | 109.56
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | TB:2/1:NI2 | 239 | 298 | 109.56
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | TB:2/1:NI2 | LN:115:129 | 239 | 298 | 109.45
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAGARA 230/115 2TR | LN:115:129 | 239 | 298 | 109.45
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:PA230_R3430 | 239 | 298 | 107.07
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:129 | 239 | 298 | 106.61
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | LN:115:129 | 239 | 298 | 106.49
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | T:61&64 | 239 | 298 | 106.45
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | NIAGARA - ROBINSON 64 345 | 239 | 298 | 106.09
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:ROBI230 | 239 | 298 | 105.57
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 239 | 298 | 105.48
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | B:Hunt68 | 239 | 298 | 105.44
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | T:77&80 | 239 | 298 | 105.36
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:HUNT230_R1502 | 239 | 298 | 105.03
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:PA230_R3230 | 239 | 298 | 104.93
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | T:79&80 | 239 | 298 | 104.88
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | T:78&79 | 239 | 298 | 104.87
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:HUNT230_R1402 | 239 | 298 | 104.87
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:129 | 239 | 298 | 104.72
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:255_345B302 | 239 | 298 | 104.7
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:NIAG345_3108 | 239 | 298 | 104.56
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | NIAG - NEWROCH 1 345 | 239 | 298 | 104.54
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:HUNT230_NEW | 239 | 298 | 103.97
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:PA230_R506 | 239 | 298 | 103.95
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | B:Hunt67 | 239 | 298 | 103.68
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | B:PACKT4 | 239 | 298 | 103.66
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:255_345B202 | 239 | 298 | 103.51
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | Base Case | 239 | 298 | 103.5
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SOMERSET - NEWROCH 1 345 | 239 | 298 | 103.46
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:HUNT230_R1302 | 239 | 298 | 103.33
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:HUNT230_R1202 | 239 | 298 | 103.29
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:129 | 239 | 298 | 103.07
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:129 | 239 | 298 | 103.03
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | S:PA_HNTL77 | 239 | 298 | 102.76
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | SB:NIAW230_2014 | 239 | 298 | 102.72
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | HUNTLEY - PACKARD 78 230 | 239 | 298 | 102.68
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | S:PA_HNTL78 | 239 | 298 | 102.68
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | PACKARD 230/115 4TR | 239 | 298 | 102.68
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | TB:2/1:PK4 | 239 | 298 | 102.68
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | HUNTLEY - PACKARD 77 230 | 239 | 298 | 102.65
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | TB:2/1:PK4 | LN:115:129 | 239 | 298 | 102.58
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | PACKARD 230/115 4TR | LN:115:129 | 239 | 298 | 102.58
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:129 | 239 | 298 | 102.32
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | T:61&64 | 239 | 298 | 102.12
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | LN:115:908 NY | 239 | 298 | 101.77
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:908 NY | LN:115:129 | 239 | 298 | 101.72
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | NIAGARA - ROBINSON 64 345 | 239 | 298 | 101.71
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 239 | 298 | 101.57
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:ROBI230 | 239 | 298 | 101.4
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | LN:115:129 | 239 | 298 | 101.3
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | NIAGARA 230/115 2TR | 239 | 298 | 101.01
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | TB:2/1:NI2 | 239 | 298 | 101.01
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | LN:115:100 | 239 | 298 | 100.96
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | TB:2/1:NI2 | LN:115:133 | 239 | 298 | 100.92
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAGARA 230/115 2TR | LN:115:133 | 239 | 298 | 100.92
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:100 | LN:115:129 | 239 | 298 | 100.9
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:PA230_R3230 | 239 | 298 | 100.86
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | T:79&80 | 239 | 298 | 100.82
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:GARD230_R823 | 239 | 298 | 100.82
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:GARD230_R833 | 239 | 298 | 100.6
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:129 | 239 | 298 | 100.58
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:129 | 239 | 298 | 100.58
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | B:Hunt68 | 239 | 298 | 100.52
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:GARD230_T7-12 | 239 | 298 | 100.52
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | B:GARD72&79 | 239 | 298 | 100.52
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | LN:115:129 | 239 | 298 | 100.47
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | LN:115:133 | 239 | 298 | 100.46
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | S:HNT_GRD80 | 239 | 298 | 100.46
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | T:77&80 | 239 | 298 | 100.44
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | HUNTLEY - GARDENVILL 79 230 | 239 | 298 | 100.4
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | HUNTLEY - GARDENVILL 80 230 | 239 | 298 | 100.39
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | TB:2/1:ROB | 239 | 298 | 100.23
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:GARD230_R873 | 239 | 298 | 100.23
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | TB:2/1:ROB | LN:115:129 | 239 | 298 | 100.16
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | G:OXBOWNUG | LN:115:129 | 239 | 298 | 100.13
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SB:HUNT230_R1502 | 239 | 298 | 100.11
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | B:GARD73&80 | 239 | 298 | 100
| 135455 MLPN-130 115 135461 PACK(S)W 115 1 Max |  |  |  |  | 125.18
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 298 | NConv
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 298 | NConv
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 298 | NConv
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | T:77&78 | 239 | 298 | 117.93
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | T:77&78 | 239 | 298 | 113.79
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:133 | T:77&78 | 239 | 298 | 112.57
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | Base Case | 239 | 298 | 111.87
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:133 | T:77&78 | 239 | 298 | 108.67
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 239 | 298 | 108.17
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | T:79&80 | 239 | 298 | 107.54
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:133 | Base Case | 239 | 298 | 106.8
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | Base Case | 239 | 298 | 105.24
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | SB:NIAW230_2014 | 239 | 298 | 104.45
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 239 | 298 | 104.06
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | T:79&80 | 239 | 298 | 103.28
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 239 | 298 | 103.23
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | TB:2/1:NI2 | 239 | 298 | 102.68
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | NIAGARA 230/115 2TR | 239 | 298 | 102.68
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:133 | T:79&80 | 239 | 298 | 102.63
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | TB:2/1:NI2 | LN:115:129 | 239 | 298 | 102.55
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | NIAGARA 230/115 2TR | LN:115:129 | 239 | 298 | 102.55
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:133 | SB:NIAW230_2014 | 239 | 298 | 100.53
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:133 | Base Case | 239 | 298 | 100.49
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | SB:PA230_R3430 | 239 | 298 | 100.12
| 135455 MLPN-130 115 135469 SUMIT PK 115 1 Max |  |  |  |  | 117.93
Dispatch 1 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 176 | 211 | NConv
Dispatch 1 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 176 | 211 | NConv
Dispatch 1 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 176 | 211 | NConv
Dispatch 1 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 176 | 211 | NConv
Dispatch 1 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 176 | 211 | NConv
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 176 | 211 | NConv
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 176 | 211 | NConv
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 176 | 211 | NConv
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 176 | 211 | NConv
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 176 | 211 | NConv
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | LN:115:101 | LN:115:102 | 176 | 211 | 114.34
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | LN:115:102 | LN:115:101 | 176 | 211 | 114.33
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 176 | 211 | 104.11
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 176 | 211 | 104.02
Dispatch 1 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | LN:115:101 | LN:115:102 | 176 | 211 | 101.93
Dispatch 1 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | LN:115:102 | LN:115:101 | 176 | 211 | 101.92
| 135456 MTNS-120 115 135470 SWAN-103 115 1 Max |  |  |  |  | 114.34
Dispatch 1 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 176 | 258 | NConv
Dispatch 1 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 176 | 258 | NConv
Dispatch 1 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 176 | 258 | NConv
Dispatch 1 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 176 | 258 | NConv
Dispatch 1 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 176 | 258 | NConv
Dispatch 2 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 176 | 258 | NConv
Dispatch 2 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 176 | 258 | NConv
Dispatch 2 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 176 | 258 | NConv
Dispatch 2 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 176 | 258 | NConv
Dispatch 2 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 176 | 258 | NConv
| 135456 MTNS-120 115 147850 NIAG115E 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 160 | 166 | NConv
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 160 | 166 | NConv
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 160 | 166 | NConv
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 160 | 166 | NConv
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 160 | 166 | NConv
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 160 | 166 | NConv
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 160 | 166 | NConv
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 160 | 166 | NConv
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 160 | 166 | NConv
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 160 | 166 | NConv
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 160 | 166 | NConv
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 160 | 166 | NConv
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 160 | 166 | 180.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 160 | 166 | 177.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:77&78 | 160 | 166 | 167.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:77&78 | 160 | 166 | 160.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:77&78 | 160 | 166 | 160.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 160 | 166 | 158.46
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:77&78 | 160 | 166 | 154.45
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 160 | 166 | 153.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 160 | 166 | 149.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:77&78 | 160 | 166 | 148.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:79&80 | 160 | 166 | 148.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 160 | 166 | 147.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 160 | 166 | 144.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 160 | 166 | 143.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:79&80 | 160 | 166 | 143.76
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 160 | 166 | 143.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 160 | 166 | 142.97
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:77&78 | 160 | 166 | 142.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:79&80 | 160 | 166 | 141.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 160 | 166 | 141.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:77&78 | 160 | 166 | 140.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 160 | 166 | 140.85
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 160 | 166 | 140.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 160 | 166 | 140.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:77&78 | 160 | 166 | 139.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:77&78 | 160 | 166 | 139.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 160 | 166 | 139.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 160 | 166 | 139.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 160 | 166 | 139.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:77&78 | 160 | 166 | 139.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 160 | 166 | 139.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 160 | 166 | 138.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | T:77&78 | 160 | 166 | 138.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:77&78 | 160 | 166 | 138.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 160 | 166 | 138.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:79&80 | 160 | 166 | 137.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 160 | 166 | 137.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 160 | 166 | 136.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 160 | 166 | 136.91
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 160 | 166 | 136.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | T:77&78 | 160 | 166 | 136.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 160 | 166 | 136.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 160 | 166 | 136.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | T:77&78 | 160 | 166 | 136.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 160 | 166 | 135.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 160 | 166 | 135.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 160 | 166 | 135.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:77&78 | 160 | 166 | 135.6
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 160 | 166 | 135.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 160 | 166 | 135.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 160 | 166 | 134.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:77&78 | 160 | 166 | 134.96
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:77&78 | 160 | 166 | 134.84
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 160 | 166 | 134.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 160 | 166 | 134.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 160 | 166 | 134.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | T:77&78 | 160 | 166 | 133.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:77&78 | 160 | 166 | 133.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | T:77&78 | 160 | 166 | 133.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | T:77&78 | 160 | 166 | 133.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | T:77&78 | 160 | 166 | 133.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 160 | 166 | 133.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:133 | T:77&78 | 160 | 166 | 133.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:130 | T:77&78 | 160 | 166 | 132.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | T:77&78 | 160 | 166 | 132.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:77&78 | 160 | 166 | 132.55
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 160 | 166 | 132.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:129 | T:77&78 | 160 | 166 | 132.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 160 | 166 | 132.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 160 | 166 | 132.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | T:77&78 | 160 | 166 | 132.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 160 | 166 | 131.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 160 | 166 | 131.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 160 | 166 | 131.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - KINTIGH 345 | T:77&78 | 160 | 166 | 131.67
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 160 | 166 | 131.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:HUN | T:77&78 | 160 | 166 | 131.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 160 | 166 | 131.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ERIE E - 4 MILE 230 | T:77&78 | 160 | 166 | 131.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:JAMESGN7 | T:77&78 | 160 | 166 | 131.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 131.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | T:77&78 | 160 | 166 | 131.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:79&80 | 160 | 166 | 131.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | T:77&78 | 160 | 166 | 131.28
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 160 | 166 | 131.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:77&80 | 160 | 166 | 131.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:Hunt68 | 160 | 166 | 131.01
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | T:77&78 | 160 | 166 | 130.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 160 | 166 | 130.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 130.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 130.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 160 | 166 | 130.59
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 160 | 166 | 130.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 160 | 166 | 130.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 160 | 166 | 130.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:180 | 160 | 166 | 130.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:182N | 160 | 166 | 130.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:HUNT230_R1502 | 160 | 166 | 130.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:HUNT230_R1402 | 160 | 166 | 129.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:78&79 | 160 | 166 | 129.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 160 | 166 | 129.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:Hunt68 | 160 | 166 | 128.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:77&80 | 160 | 166 | 128.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:HUNT230_NEW | 160 | 166 | 128.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | T:77&78 | 160 | 166 | 128.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:HUNT230_R1502 | 160 | 166 | 127.87
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | T:77&78 | 160 | 166 | 127.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:Hunt67 | 160 | 166 | 127.83
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | T:77&78 | 160 | 166 | 127.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:133 | T:77&78 | 160 | 166 | 127.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:HUNT230_R1402 | 160 | 166 | 127.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:78&79 | 160 | 166 | 127.65
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | T:77&78 | 160 | 166 | 127.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GARD230_T7-12 | 160 | 166 | 127.46
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:130 | T:77&78 | 160 | 166 | 127.43
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 127.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 160 | 166 | 127.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | T:77&78 | 160 | 166 | 127.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 160 | 166 | 127.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | T:77&78 | 160 | 166 | 127.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:HUNT230_R1302 | 160 | 166 | 127.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:129 | T:77&78 | 160 | 166 | 127.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:HUNT230_R1202 | 160 | 166 | 127.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:182S | 160 | 166 | 126.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:180 | 160 | 166 | 126.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | T:77&78 | 160 | 166 | 126.77
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 160 | 166 | 126.72
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 160 | 166 | 126.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:GINNA | T:77&78 | 160 | 166 | 126.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | T:77&78 | 160 | 166 | 126.67
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - KINTIGH 345 | T:77&78 | 160 | 166 | 126.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | T:77&78 | 160 | 166 | 126.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:182N | 160 | 166 | 126.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:182N | 160 | 166 | 126.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 160 | 166 | 126.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 160 | 166 | 126.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:HUNT230_NEW | 160 | 166 | 126.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 160 | 166 | 126.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:908 NY | T:77&78 | 160 | 166 | 126.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:Hunt67 | 160 | 166 | 126.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926A | T:77&78 | 160 | 166 | 126.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | S:PA_HNTL77 | 160 | 166 | 125.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | S:PA_HNTL78 | 160 | 166 | 125.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | HUNTLEY - PACKARD 78 230 | 160 | 166 | 125.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:79&80 | 160 | 166 | 125.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:3/2:FV | T:77&78 | 160 | 166 | 125.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | T:77&78 | 160 | 166 | 125.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | HUNTLEY - PACKARD 77 230 | 160 | 166 | 125.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:STOLE230 | 160 | 166 | 125.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 160 | 166 | 125.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 125.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 125.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 160 | 166 | 125.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GARD230_T7-12 | 160 | 166 | 125.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 125.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 160 | 166 | 125.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:182N | 160 | 166 | 125.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 160 | 166 | 125.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:HUNT230_R1302 | 160 | 166 | 125.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 160 | 166 | 125.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:79&80 | 160 | 166 | 125.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:HUNT230_R1202 | 160 | 166 | 125.01
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 160 | 166 | 124.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV1 | T:77&78 | 160 | 166 | 124.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV2 | T:77&78 | 160 | 166 | 124.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 166 | 124.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:182S | 160 | 166 | 124.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:182S | 160 | 166 | 124.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:79&80 | 160 | 166 | 124.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:79&80 | 160 | 166 | 124.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:182N | 160 | 166 | 124.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | ROBINSON - STOLLRD 65 230 | 160 | 166 | 124.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | T:77&78 | 160 | 166 | 124.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | T:77&78 | 160 | 166 | 124.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:79&80 | 160 | 166 | 124.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 124.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 160 | 166 | 124.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | T:77&78 | 160 | 166 | 124.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | S:PA_HNTL77 | 160 | 166 | 124.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | FARMVLY - HOMERCTY | 160 | 166 | 124.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HC-FV_37&W-F_171 | 160 | 166 | 124.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 124.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:79&80 | 160 | 166 | 124.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | HUNTLEY - PACKARD 78 230 | 160 | 166 | 124.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | S:PA_HNTL78 | 160 | 166 | 124.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | HUNTLEY - PACKARD 77 230 | 160 | 166 | 123.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 160 | 166 | 123.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | FARMVLY - HOMERCTY | 160 | 166 | 123.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:HC-FV_37&W-F_171 | 160 | 166 | 123.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:182S | 160 | 166 | 123.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:STOLE230 | 160 | 166 | 123.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:79&80 | 160 | 166 | 123.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 123.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:77&80 | 160 | 166 | 123.46
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:Hunt68 | 160 | 166 | 123.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | DCT:230:79+80+ELM1-2 | 160 | 166 | 123.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 160 | 166 | 123.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 160 | 166 | 123.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | ROBINSON - STOLLRD 65 230 | 160 | 166 | 123.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:PA230_R3430 | 160 | 166 | 123.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:54/921 | 160 | 166 | 122.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:182S | 160 | 166 | 122.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 122.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GARD230_R823 | 160 | 166 | 122.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 160 | 166 | 122.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 122.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:182S | 160 | 166 | 122.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 160 | 166 | 122.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 160 | 166 | 122.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | T:79&80 | 160 | 166 | 122.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 160 | 166 | 122.52
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:HUNT230_R1502 | 160 | 166 | 122.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 160 | 166 | 122.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 160 | 166 | 122.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 160 | 166 | 122.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GARD230_R833 | 160 | 166 | 122.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 166 | 122.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 166 | 122.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 160 | 166 | 122.31
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:HUNT230_R1402 | 160 | 166 | 122.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:78&79 | 160 | 166 | 122.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:907 NY | T:77&78 | 160 | 166 | 122.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | TB:2/1:PK3 | 160 | 166 | 122.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:GARD72&79 | 160 | 166 | 122.17
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - WTRCR 31 345 | T:77&78 | 160 | 166 | 122.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 160 | 166 | 122.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:182N | 160 | 166 | 122.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:182N | 160 | 166 | 122.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:Hunt68 | 160 | 166 | 122.04
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:77&80 | 160 | 166 | 122.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:79&80 | 160 | 166 | 121.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | S:HNT_GRD80 | 160 | 166 | 121.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 160 | 166 | 121.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:40&41 | 160 | 166 | 121.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | DCT:230:79+80+ELM1-2 | 160 | 166 | 121.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:182N | 160 | 166 | 121.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 121.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 7 | T:77&78 | 160 | 166 | 121.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 121.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 4 | T:77&78 | 160 | 166 | 121.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 5 | T:77&78 | 160 | 166 | 121.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 6 | T:77&78 | 160 | 166 | 121.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:195 | 160 | 166 | 121.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:ROBI230 | 160 | 166 | 121.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | TB:2/1:PK3 | 160 | 166 | 121.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:182N | 160 | 166 | 121.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | T:77&78 | 160 | 166 | 121.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GARD230_R873 | 160 | 166 | 121.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:182S | 160 | 166 | 121.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:182N | 160 | 166 | 121.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 11 | T:77&78 | 160 | 166 | 121.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 12 | T:77&78 | 160 | 166 | 121.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 13 | T:77&78 | 160 | 166 | 121.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 8 | T:77&78 | 160 | 166 | 121.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 9 | T:77&78 | 160 | 166 | 121.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:182S | 160 | 166 | 121.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:GINNA | T:77&78 | 160 | 166 | 121.65
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 10 | T:77&78 | 160 | 166 | 121.65
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | T:77&78 | 160 | 166 | 121.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | DCT:230:79+80+ELM1-2 | 160 | 166 | 121.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | T:79&80 | 160 | 166 | 121.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | T:79&80 | 160 | 166 | 121.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:41&33 | 160 | 166 | 121.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:PA230_R3430 | 160 | 166 | 121.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:182S | 160 | 166 | 121.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GARD230_R823 | 160 | 166 | 121.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 160 | 166 | 121.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCWC/NWES | T:77&78 | 160 | 166 | 121.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:MBWC/NWES | T:77&78 | 160 | 166 | 121.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:195 | 160 | 166 | 121.47
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | T:77&78 | 160 | 166 | 121.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:PA230_R3230 | 160 | 166 | 121.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:182N | 160 | 166 | 121.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 160 | 166 | 121.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:40&41 | 160 | 166 | 121.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:GARD73&80 | 160 | 166 | 121.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:54/921 | 160 | 166 | 121.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | T:79&80 | 160 | 166 | 121.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926A | T:77&78 | 160 | 166 | 121.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:NI1 | T:77&78 | 160 | 166 | 121.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | T:77&78 | 160 | 166 | 121.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | T:79&80 | 160 | 166 | 121.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:182S | 160 | 166 | 121.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - ELM 70 230 | T:79&80 | 160 | 166 | 121.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 160 | 166 | 121.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GARD230_R833 | 160 | 166 | 121.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:191 | 160 | 166 | 121.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:182S | 160 | 166 | 121.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:41&33 | 160 | 166 | 121.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:182S | 160 | 166 | 121.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:HUNT230_R1502 | 160 | 166 | 121.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:GARD72&79 | 160 | 166 | 120.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 120.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:192 | 160 | 166 | 120.88
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | T:77&78 | 160 | 166 | 120.83
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:HUNT230_R1402 | 160 | 166 | 120.81
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:78&79 | 160 | 166 | 120.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:34&42 | 160 | 166 | 120.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | T:79&80 | 160 | 166 | 120.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | S:HNT_GRD80 | 160 | 166 | 120.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:191 | 160 | 166 | 120.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:182N | 160 | 166 | 120.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GARD230_R873 | 160 | 166 | 120.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:182N | 160 | 166 | 120.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:101 | 160 | 166 | 120.67
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:3/2:FV | T:77&78 | 160 | 166 | 120.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | T:77&78 | 160 | 166 | 120.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 160 | 166 | 120.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:182N | 160 | 166 | 120.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:192 | 160 | 166 | 120.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 120.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 120.57
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:180 | 160 | 166 | 120.55
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:HUNT230_NEW | 160 | 166 | 120.53
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:79&80 | 160 | 166 | 120.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 120.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:182N | 160 | 166 | 120.48
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 160 | 166 | 120.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 166 | 120.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:ROBI230 | 160 | 166 | 120.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:182N | 160 | 166 | 120.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_NEW | 160 | 166 | 120.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:182S | 160 | 166 | 120.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:908 NY | T:77&78 | 160 | 166 | 120.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | DCT:230:79+80+ELM1-2 | 160 | 166 | 120.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:102 | 160 | 166 | 120.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | LN:115:182N | 160 | 166 | 120.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:GARD73&80 | 160 | 166 | 120.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:182S | 160 | 166 | 120.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:34&42 | 160 | 166 | 120.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | T:79&80 | 160 | 166 | 120.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:182S | 160 | 166 | 120.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:182N | 160 | 166 | 120.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:Hunt67 | 160 | 166 | 120.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | DCT:230:79+80+ELM1-2 | 160 | 166 | 120.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | PACKARD 230/115 3TR | T:77&78 | 160 | 166 | 120.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 120
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 120
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 120
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | LN:115:182N | 160 | 166 | 119.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:120 | 160 | 166 | 119.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | DCT:230:79+80+ELM1-2 | 160 | 166 | 119.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 160 | 166 | 119.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | T:79&80 | 160 | 166 | 119.87
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | T:77&78 | 160 | 166 | 119.86
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | T:77&78 | 160 | 166 | 119.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:182N | 160 | 166 | 119.86
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 166 | 119.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:61&64 | 160 | 166 | 119.84
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:79&80 | 160 | 166 | 119.81
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GARD230_T7-12 | 160 | 166 | 119.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | T:79&80 | 160 | 166 | 119.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:182S | 160 | 166 | 119.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:79&80 | 160 | 166 | 119.69
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV1 | T:77&78 | 160 | 166 | 119.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV2 | T:77&78 | 160 | 166 | 119.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | LN:115:182N | 160 | 166 | 119.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCMB/NWES | T:77&78 | 160 | 166 | 119.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:101 | 160 | 166 | 119.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:345:37S-FM-FV-HC | 160 | 166 | 119.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:PA230_R3230 | 160 | 166 | 119.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:5MILE_B | 160 | 166 | 119.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | T:79&80 | 160 | 166 | 119.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 160 | 166 | 119.52
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 160 | 166 | 119.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | LN:115:182S | 160 | 166 | 119.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | Base Case | 160 | 166 | 119.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:HUNT230_R1202 | 160 | 166 | 119.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | T:79&80 | 160 | 166 | 119.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | T:79&80 | 160 | 166 | 119.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | T:79&80 | 160 | 166 | 119.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:102 | 160 | 166 | 119.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:HUNT230_R1302 | 160 | 166 | 119.36
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | T:77&78 | 160 | 166 | 119.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | T:79&80 | 160 | 166 | 119.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:HUNT230_NEW | 160 | 166 | 119.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:345:37S-FM-FV-HC | 160 | 166 | 119.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:5MILE_B | 160 | 166 | 119.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 160 | 166 | 119.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | DCT:230:79+80+ELM1-2 | 160 | 166 | 119.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | LN:115:182S | 160 | 166 | 119.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:Hunt67 | 160 | 166 | 119.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | NIAGARA - ROBINSON 64 345 | 160 | 166 | 119.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | Base Case | 160 | 166 | 119.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 160 | 166 | 119.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:LAPER_345_2 | 160 | 166 | 119.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:LAPER_345_1 | 160 | 166 | 119.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:120 | 160 | 166 | 119.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:182S | 160 | 166 | 119.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 119.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | DCT:230:79+80+ELM1-2 | 160 | 166 | 119.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:LAFAYETT | 160 | 166 | 119.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 118.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 160 | 166 | 118.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | LN:115:182S | 160 | 166 | 118.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:61&64 | 160 | 166 | 118.89
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:79&80 | 160 | 166 | 118.85
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:182N | 160 | 166 | 118.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 160 | 166 | 118.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:38 | 160 | 166 | 118.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | LN:115:182N | 160 | 166 | 118.76
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:182N | 160 | 166 | 118.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:LAPER_345_3 | 160 | 166 | 118.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:LAPER_345_4 | 160 | 166 | 118.7
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 160 | 166 | 118.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | LN:115:182N | 160 | 166 | 118.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | T:79&80 | 160 | 166 | 118.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:OAKD345_B5 | 160 | 166 | 118.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:LAFA_ELB | 160 | 166 | 118.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 118.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:OAKD345_B6 | 160 | 166 | 118.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:LAPER_345_1 | 160 | 166 | 118.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:LAPER_345_2 | 160 | 166 | 118.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | LN:115:182S | 160 | 166 | 118.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 118.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 118.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | LN:115:182S | 160 | 166 | 118.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:133 | T:79&80 | 160 | 166 | 118.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:LAFAYETT | 160 | 166 | 118.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GARD230_T7-12 | 160 | 166 | 118.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 7 | T:77&78 | 160 | 166 | 118.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:79&80 | 160 | 166 | 118.48
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 4 | T:77&78 | 160 | 166 | 118.48
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 5 | T:77&78 | 160 | 166 | 118.48
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 6 | T:77&78 | 160 | 166 | 118.48
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | DCT:230:79+80+ELM1-2 | 160 | 166 | 118.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | DCT:230:79+80+ELM1-2 | 160 | 166 | 118.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:39 | 160 | 166 | 118.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:NIAG345_3108 | 160 | 166 | 118.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | NIAG - NEWROCH 1 345 | 160 | 166 | 118.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | T:79&80 | 160 | 166 | 118.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:COOP345_42-4182 | 160 | 166 | 118.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:255_345B302 | 160 | 166 | 118.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:31&41 | 160 | 166 | 118.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:130 | T:79&80 | 160 | 166 | 118.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - ELM 70 230 | DCT:230:79+80+ELM1-2 | 160 | 166 | 118.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:HUNT230_R1302 | 160 | 166 | 118.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | NIAGARA - ROBINSON 64 345 | 160 | 166 | 118.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:HUNT230_R1202 | 160 | 166 | 118.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:LAPER_345_4 | 160 | 166 | 118.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:LAPER_345_3 | 160 | 166 | 118.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | LN:115:182N | 160 | 166 | 118.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | S:PA_HNTL77 | 160 | 166 | 118.17
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:182S | 160 | 166 | 118.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:LAFA_ELB | 160 | 166 | 118.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:OAKD345_B5 | 160 | 166 | 118.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 118.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:OAKD345_B6 | 160 | 166 | 118.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | LN:115:182N | 160 | 166 | 118.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:NIAG345_3108 | 160 | 166 | 118.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:180 | 160 | 166 | 118.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | NIAG - NEWROCH 1 345 | 160 | 166 | 118.08
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 160 | 166 | 118.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | HUNTLEY - PACKARD 78 230 | 160 | 166 | 118.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | S:PA_HNTL78 | 160 | 166 | 118.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:79&80 | 160 | 166 | 118.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:129 | T:79&80 | 160 | 166 | 118.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:255_345B302 | 160 | 166 | 118.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:EDIC345_R915 | 160 | 166 | 118
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:345:37S-FM-FV | 160 | 166 | 118
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:5MILE | 160 | 166 | 118
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:79&80 | 160 | 166 | 117.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | HUNTLEY - PACKARD 77 230 | 160 | 166 | 117.97
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 160 | 166 | 117.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:38 | 160 | 166 | 117.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | LN:115:182S | 160 | 166 | 117.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | LN:115:182S | 160 | 166 | 117.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | LN:115:182S | 160 | 166 | 117.94
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:182S | 160 | 166 | 117.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:MP11&41 | 160 | 166 | 117.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:COOP345_4182 | 160 | 166 | 117.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:COOP345_42-4182 | 160 | 166 | 117.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MARC345_3208 | 160 | 166 | 117.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:705 NY | 160 | 166 | 117.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | First:Lancaster_705 | 160 | 166 | 117.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MARC345_3202 | 160 | 166 | 117.88
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:182S | 160 | 166 | 117.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | MARCY - COOPERS 345 SC | 160 | 166 | 117.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:31&41 | 160 | 166 | 117.84
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 160 | 166 | 117.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:77&76 | 160 | 166 | 117.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:255_345B202 | 160 | 166 | 117.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SOMERSET - NEWROCH 1 345 | 160 | 166 | 117.79
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 117.78
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:STOLE230 | 160 | 166 | 117.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | T:79&80 | 160 | 166 | 117.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | T:79&80 | 160 | 166 | 117.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | LN:115:182S | 160 | 166 | 117.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:182N | 160 | 166 | 117.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 166 | 117.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 166 | 117.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 160 | 166 | 117.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | LN:115:182N | 160 | 166 | 117.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:EDIC345_R915 | 160 | 166 | 117.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:EDIC345_R935 | 160 | 166 | 117.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:30&40 | 160 | 166 | 117.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HC-SR_37&W-F_171 | 160 | 166 | 117.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:FV-5M_37&W-F_171 | 160 | 166 | 117.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R823 | 160 | 166 | 117.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | FARMVLY - 5MILE 345 | 160 | 166 | 117.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:255_345B202 | 160 | 166 | 117.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:39 | 160 | 166 | 117.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:345:37S-FM-FV | 160 | 166 | 117.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:5MILE | 160 | 166 | 117.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:705 NY | 160 | 166 | 117.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | First:Lancaster_705 | 160 | 166 | 117.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SOMERSET - NEWROCH 1 345 | 160 | 166 | 117.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:MP11&41 | 160 | 166 | 117.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:COOP345_4182 | 160 | 166 | 117.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | T:79&80 | 160 | 166 | 117.48
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 160 | 166 | 117.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:MARC345_3208 | 160 | 166 | 117.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:MARC345_3202 | 160 | 166 | 117.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | LN:115:182S | 160 | 166 | 117.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:182S | 160 | 166 | 117.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | MARCY - COOPERS 345 SC | 160 | 166 | 117.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:FV-5M_37&W-F_171 | 160 | 166 | 117.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:HC-SR_37&W-F_171 | 160 | 166 | 117.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:77&76 | 160 | 166 | 117.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | FARMVLY - 5MILE 345 | 160 | 166 | 117.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | LN:115:182N | 160 | 166 | 117.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | LN:115:182N | 160 | 166 | 117.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:182N | 160 | 166 | 117.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 160 | 166 | 117.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | LN:115:182N | 160 | 166 | 117.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:EDIC345_R400 | 160 | 166 | 117.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 160 | 166 | 117.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 160 | 166 | 117.3
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | S:PA_HNTL77 | 160 | 166 | 117.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 160 | 166 | 117.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 160 | 166 | 117.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MARC345_3108 | 160 | 166 | 117.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:69J&70K | 160 | 166 | 117.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | LN:115:182N | 160 | 166 | 117.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | LN:115:182N | 160 | 166 | 117.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | LN:115:182S | 160 | 166 | 117.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | LN:115:182S | 160 | 166 | 117.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | LN:115:182S | 160 | 166 | 117.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | HOMERCTY - STOLLRD 37 345 | 160 | 166 | 117.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:STOLE345 | 160 | 166 | 117.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | 5 MILE - STOLLE 37A 345 | 160 | 166 | 117.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | First:Lancaster_STOL_HOMER_345 | 160 | 166 | 117.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:EDIC345_R935 | 160 | 166 | 117.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&80 | 160 | 166 | 117.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:30&40 | 160 | 166 | 117.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R833 | 160 | 166 | 117.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:5M-SR_37&W-F_171 | 160 | 166 | 117.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | LN:115:182N | 160 | 166 | 117.08
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | S:PA_HNTL78 | 160 | 166 | 117.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | HUNTLEY - PACKARD 78 230 | 160 | 166 | 117.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | DCT:230:79+80+ELM1-2 | 160 | 166 | 117.05
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:182N | 160 | 166 | 117.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | LN:115:182N | 160 | 166 | 117.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | LN:115:182S | 160 | 166 | 117.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | LN:115:182S | 160 | 166 | 117.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | HUNTLEY - PACKARD 77 230 | 160 | 166 | 117.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | LN:115:182S | 160 | 166 | 117.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | LN:115:182S | 160 | 166 | 117.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | LN:115:182S | 160 | 166 | 117.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | LN:115:182S | 160 | 166 | 117.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:EDIC345_R400 | 160 | 166 | 116.95
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 160 | 166 | 116.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | S:STOLLE345 | 160 | 166 | 116.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | B:Hunt68 | 160 | 166 | 116.92
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 160 | 166 | 116.77
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:182S | 160 | 166 | 116.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | T:78&79 | 160 | 166 | 116.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:79&80 | 160 | 166 | 116.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:903 NY | LN:115:182S | 160 | 166 | 116.73
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:54/921 | 160 | 166 | 116.72
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | ROBINSON - STOLLRD 65 230 | 160 | 166 | 116.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | T:77&80 | 160 | 166 | 116.7
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | FARMVLY - HOMERCTY | 160 | 166 | 116.67
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:HC-FV_37&W-F_171 | 160 | 166 | 116.65
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:STOLE230 | 160 | 166 | 116.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 116.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | T:79&80 | 160 | 166 | 116.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | T:79&80 | 160 | 166 | 116.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 160 | 166 | 116.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCWC/NWES | T:77&78 | 160 | 166 | 116.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:MBWC/NWES | T:77&78 | 160 | 166 | 116.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:77&80 | 160 | 166 | 116.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:182S | 160 | 166 | 116.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | B:Hunt68 | 160 | 166 | 116.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | B:GARD72&79 | 160 | 166 | 116.31
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | DCT:230:79+80+ELM1-2 | 160 | 166 | 116.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:182S | 160 | 166 | 116.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_R1202 | 160 | 166 | 116.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1402 | 160 | 166 | 116.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 116.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | S:HNT_GRD80 | 160 | 166 | 116.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 116.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 116.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | B:Hunt68 | 160 | 166 | 116.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - ELM 70 230 | T:79&80 | 160 | 166 | 116.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | T:79&80 | 160 | 166 | 116.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:77&80 | 160 | 166 | 116.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | FARMVLY - HOMERCTY | 160 | 166 | 115.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | ROBINSON - STOLLRD 65 230 | 160 | 166 | 115.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HC-FV_37&W-F_171 | 160 | 166 | 115.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | B:Hunt67 | 160 | 166 | 115.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | B:Hunt68 | 160 | 166 | 115.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1502 | 160 | 166 | 115.82
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | T:79&80 | 160 | 166 | 115.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:GARD230_R873 | 160 | 166 | 115.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1402 | 160 | 166 | 115.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:78&79 | 160 | 166 | 115.7
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 115.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 166 | 115.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_R1302 | 160 | 166 | 115.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1502 | 160 | 166 | 115.52
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:PA230_R3430 | 160 | 166 | 115.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1502 | 160 | 166 | 115.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:HUNT230_R1502 | 160 | 166 | 115.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | B:GARD73&80 | 160 | 166 | 115.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1402 | 160 | 166 | 115.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:78&79 | 160 | 166 | 115.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | T:79&80 | 160 | 166 | 115.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 115.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 115.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 115.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:HUNT230_R1402 | 160 | 166 | 115.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:78&79 | 160 | 166 | 115.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_NEW | 160 | 166 | 115.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | T:79&80 | 160 | 166 | 115.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GARD230_R823 | 160 | 166 | 115.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 160 | 166 | 114.96
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | DCT:230:79+80+ELM1-2 | 160 | 166 | 114.88
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:PA230_R3430 | 160 | 166 | 114.78
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | T:79&80 | 160 | 166 | 114.78
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCMB/NWES | T:77&78 | 160 | 166 | 114.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GARD230_R833 | 160 | 166 | 114.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | DCT:230:79+80+ELM1-2 | 160 | 166 | 114.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GARD230_R823 | 160 | 166 | 114.65
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | DCT:230:79+80+ELM1-2 | 160 | 166 | 114.55
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:182S | 160 | 166 | 114.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 160 | 166 | 114.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:182S | 160 | 166 | 114.43
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | T:79&80 | 160 | 166 | 114.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | T:79&80 | 160 | 166 | 114.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | T:79&80 | 160 | 166 | 114.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:GARD72&79 | 160 | 166 | 114.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:182N | 160 | 166 | 114.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:182N | 160 | 166 | 114.28
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | DCT:230:79+80+ELM1-2 | 160 | 166 | 114.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GARD230_R833 | 160 | 166 | 114.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | DCT:230:79+80+ELM1-2 | 160 | 166 | 114.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 160 | 166 | 114.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:926 NY | DCT:230:79+80+ELM1-2 | 160 | 166 | 114.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:182S | 160 | 166 | 114.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | T:79&80 | 160 | 166 | 114.08
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:195 | 160 | 166 | 114.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:182S | 160 | 166 | 114.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:MEYER | DCT:230:79+80+ELM1-2 | 160 | 166 | 114.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | S:HNT_GRD80 | 160 | 166 | 114.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:40&41 | 160 | 166 | 114.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 113.95
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 113.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.93
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:GARD72&79 | 160 | 166 | 113.9
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - WTRCR 31 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.88
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | T:79&80 | 160 | 166 | 113.86
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GARD230_R873 | 160 | 166 | 113.86
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:182S | 160 | 166 | 113.8
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:54/921 | 160 | 166 | 113.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:HUNT230_NEW | 160 | 166 | 113.76
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | T:79&80 | 160 | 166 | 113.75
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GARD230_R873 | 160 | 166 | 113.73
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.72
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:41&33 | 160 | 166 | 113.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_NEW | 160 | 166 | 113.72
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | S:HNT_GRD80 | 160 | 166 | 113.69
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:40&41 | 160 | 166 | 113.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:191 | 160 | 166 | 113.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 113.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 113.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:182N | 160 | 166 | 113.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:MEYER | T:79&80 | 160 | 166 | 113.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | T:79&80 | 160 | 166 | 113.58
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:182N | 160 | 166 | 113.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:GINNA | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:926 NY | T:79&80 | 160 | 166 | 113.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:192 | 160 | 166 | 113.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 160 | 166 | 113.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_NEW | 160 | 166 | 113.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:GARD73&80 | 160 | 166 | 113.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - WTRCR 31 345 | T:79&80 | 160 | 166 | 113.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:195 | 160 | 166 | 113.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | B:Hunt67 | 160 | 166 | 113.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:182S | 160 | 166 | 113.36
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | T:79&80 | 160 | 166 | 113.36
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:41&33 | 160 | 166 | 113.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | T:79&80 | 160 | 166 | 113.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:GARD73&80 | 160 | 166 | 113.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | B:Hunt67 | 160 | 166 | 113.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | B:Hunt68 | 160 | 166 | 113.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:182S | 160 | 166 | 113.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:182N | 160 | 166 | 113.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - KINTIGH 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:ROBI230 | 160 | 166 | 113.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - ELM 70 230 | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:GARD230_T7-12 | 160 | 166 | 113.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:79&80 | 160 | 166 | 113.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | B:Hunt67 | 160 | 166 | 113.12
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | T:79&80 | 160 | 166 | 113.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:GINNA | T:79&80 | 160 | 166 | 113.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:133 | T:79&80 | 160 | 166 | 113.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | T:79&80 | 160 | 166 | 113.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:STONY230 | 160 | 166 | 113.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:77&80 | 160 | 166 | 113.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN GILBOA #3&4 | 160 | 166 | 113.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | ERIE E - 4 MILE 230 | 160 | 166 | 113.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GILB345_3302 | 160 | 166 | 113.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:191 | 160 | 166 | 113.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | DCT:230:79+80+ELM1-2 | 160 | 166 | 113.01
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:182N | 160 | 166 | 112.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:182S | 160 | 166 | 112.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GILB345_3308 | 160 | 166 | 112.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:PA230_R304 | 160 | 166 | 112.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:NTHF3&4 | 160 | 166 | 112.98
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:34&42 | 160 | 166 | 112.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN GILBOA #1&2 | 160 | 166 | 112.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GILB345_3202 | 160 | 166 | 112.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:908 NY | DCT:230:79+80+ELM1-2 | 160 | 166 | 112.91
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:192 | 160 | 166 | 112.9
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:130 | T:79&80 | 160 | 166 | 112.89
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:ROBI230 | 160 | 166 | 112.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | T:79&80 | 160 | 166 | 112.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:926 NY | 160 | 166 | 112.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - WTRCR 31 345 | LN:115:182N | 160 | 166 | 112.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:SITHE 1 | 160 | 166 | 112.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:SITHE 2 | 160 | 166 | 112.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GILB345_3308 | 160 | 166 | 112.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:NTHF3&4 | 160 | 166 | 112.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926A | DCT:230:79+80+ELM1-2 | 160 | 166 | 112.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN GILBOA #1&2 | 160 | 166 | 112.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GILB345_3202 | 160 | 166 | 112.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:AMERT | LN:115:182N | 160 | 166 | 112.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SRIPL - ERIE E 69 230 | 160 | 166 | 112.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:GINNA | LN:115:182N | 160 | 166 | 112.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:115:AMERT | 160 | 166 | 112.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:926 NY | LN:115:182N | 160 | 166 | 112.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN: IND PT 2 | 160 | 166 | 112.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:HUNT230_R1302 | 160 | 166 | 112.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | LN:115:182N | 160 | 166 | 112.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:HUNT230_R1502 | 160 | 166 | 112.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:HUNT230_R1202 | 160 | 166 | 112.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:EESR/NWES | 160 | 166 | 112.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | T:79&80 | 160 | 166 | 112.67
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:345:37S-FM-FV-HC | 160 | 166 | 112.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_T7-12 | 160 | 166 | 112.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:BUCHN_11 | 160 | 166 | 112.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | T:79&80 | 160 | 166 | 112.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:BUCHN_9 | 160 | 166 | 112.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:115:AMERT | 160 | 166 | 112.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1202 | 160 | 166 | 112.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:129 | T:79&80 | 160 | 166 | 112.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | DUNKIRK - SRIPL 68 230 | 160 | 166 | 112.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:SRIPLEY | 160 | 166 | 112.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:BUCHN_7 | 160 | 166 | 112.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:182N | 160 | 166 | 112.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | LN:115:182S | 160 | 166 | 112.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SRIPL - ERIE E 69 230 | 160 | 166 | 112.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:BETHSTM | 160 | 166 | 112.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:GARD230_T7-12 | 160 | 166 | 112.58
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:34&42 | 160 | 166 | 112.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:SITHE 1 | 160 | 166 | 112.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:SITHE 2 | 160 | 166 | 112.57
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | TB:2/1:PK3 | 160 | 166 | 112.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:182N | 160 | 166 | 112.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | B:Hunt68 | 160 | 166 | 112.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN: IND PT 2 | 160 | 166 | 112.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1202 | 160 | 166 | 112.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN: IND PT 3 | 160 | 166 | 112.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:182N | 160 | 166 | 112.46
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:182S | 160 | 166 | 112.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:BUCHN_11 | 160 | 166 | 112.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:PACKT3 | 160 | 166 | 112.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:BUCHS_1 | 160 | 166 | 112.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:BUCHS_3 | 160 | 166 | 112.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:BUCHN_9 | 160 | 166 | 112.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:3/2:FV | DCT:230:79+80+ELM1-2 | 160 | 166 | 112.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | STONYCR - WTHRS 230 | 160 | 166 | 112.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | DCT:230:79+80+ELM1-2 | 160 | 166 | 112.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:BUCHN_7 | 160 | 166 | 112.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:HUNT230_R1402 | 160 | 166 | 112.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:78&79 | 160 | 166 | 112.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1302 | 160 | 166 | 112.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:182S | 160 | 166 | 112.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R823 | 160 | 166 | 112.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:BETHSTM | 160 | 166 | 112.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | TB:2/1:ROB | 160 | 166 | 112.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 160 | 166 | 112.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1302 | 160 | 166 | 112.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:180 | 160 | 166 | 112.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:PA230_R304 | 160 | 166 | 112.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN: IND PT 3 | 160 | 166 | 112.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:77&80 | 160 | 166 | 112.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | TB:2/1:ROB | 160 | 166 | 112.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:908 NY | T:79&80 | 160 | 166 | 112.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | LN:115:182N | 160 | 166 | 112.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:67&68&BW | 160 | 166 | 112.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | B:Hunt68 | 160 | 166 | 112.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 160 | 166 | 112.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:BUCHS_1 | 160 | 166 | 112.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:BUCHS_3 | 160 | 166 | 112.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:180 | 160 | 166 | 112.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | LN:115:182N | 160 | 166 | 112.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | STONYCR - WTHRS 230 | 160 | 166 | 112.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HCWC/NWES | 160 | 166 | 112.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:MBWC/NWES | 160 | 166 | 112.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926A | T:79&80 | 160 | 166 | 112.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:5MILE_B | 160 | 166 | 112.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | WTRCR - MAINSBRG 30A 345 | 160 | 166 | 112.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:WATRC345_30-3142 | 160 | 166 | 112.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:WATRC345_B1-3042 | 160 | 166 | 112.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | LN:115:182S | 160 | 166 | 112.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:182S | 160 | 166 | 112.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | LN:115:182S | 160 | 166 | 112.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | LN:115:182S | 160 | 166 | 112.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:DKSR/WRFL | 160 | 166 | 112.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:EESR/WF/NWES | 160 | 166 | 112.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | LN:115:182S | 160 | 166 | 112.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HC-WC_30&W-F_171 | 160 | 166 | 112.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:67&68&BW | 160 | 166 | 112.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | B:Hunt68 | 160 | 166 | 112.13
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:182N | 160 | 166 | 112.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | LN:115:182N | 160 | 166 | 112.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SIN:130 | 160 | 166 | 112.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SIN:120_130 | 160 | 166 | 112.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:W97&W98 | 160 | 166 | 112.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | LN:115:182N | 160 | 166 | 112.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | LN:115:182N | 160 | 166 | 112.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | LN:115:182S | 160 | 166 | 112.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:EESR/WRFL | 160 | 166 | 112.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | LN:115:182N | 160 | 166 | 112.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:61&64 | 160 | 166 | 112.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:77&80 | 160 | 166 | 112.04
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R833 | 160 | 166 | 112.01
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:182N | 160 | 166 | 111.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:HCWC/NWES | 160 | 166 | 111.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:MBWC/NWES | 160 | 166 | 111.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:HUNT230_R1502 | 160 | 166 | 111.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SIN:130 | 160 | 166 | 111.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SIN:120_130 | 160 | 166 | 111.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:W97&W98 | 160 | 166 | 111.96
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&80 | 160 | 166 | 111.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:WATRC345_B1-3042 | 160 | 166 | 111.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:WATRC345_30-3142 | 160 | 166 | 111.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | WTRCR - MAINSBRG 30A 345 | 160 | 166 | 111.92
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:61&64 | 160 | 166 | 111.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:PACKT3 | 160 | 166 | 111.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:WTHERS230 | 160 | 166 | 111.91
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | PACKARD 230/115 3TR | T:77&78 | 160 | 166 | 111.9
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:NI1 | T:77&78 | 160 | 166 | 111.89
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | T:77&78 | 160 | 166 | 111.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:HC-WC_30&W-F_171 | 160 | 166 | 111.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:77&80 | 160 | 166 | 111.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:3/2:FV | T:79&80 | 160 | 166 | 111.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:EESR/WF/NWES | 160 | 166 | 111.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | T:79&80 | 160 | 166 | 111.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:DKSR/WRFL | 160 | 166 | 111.83
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:101 | 160 | 166 | 111.8
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | TB:2/1:PK3 | 160 | 166 | 111.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:FRGT/WRFL | 160 | 166 | 111.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:EESR/WRFL | 160 | 166 | 111.78
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:101 | 160 | 166 | 111.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | S:PA_HNTL77 | 160 | 166 | 111.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | NIAGARA 230/115 1TR | 160 | 166 | 111.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | TB:2/1:NI1 | 160 | 166 | 111.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:68&160 | 160 | 166 | 111.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:NIAW230_2014 | 160 | 166 | 111.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HCMB/NWES | 160 | 166 | 111.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:HUNT230_R1402 | 160 | 166 | 111.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | B:Hunt68 | 160 | 166 | 111.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:78&79 | 160 | 166 | 111.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:WTHERS230 | 160 | 166 | 111.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:NI1 | LN:115:182N | 160 | 166 | 111.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:100 | 160 | 166 | 111.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | LN:115:182N | 160 | 166 | 111.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:HUNT230_R1502 | 160 | 166 | 111.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:100 | 160 | 166 | 111.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV1 | DCT:230:79+80+ELM1-2 | 160 | 166 | 111.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV2 | DCT:230:79+80+ELM1-2 | 160 | 166 | 111.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 111.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | S:PA_HNTL78 | 160 | 166 | 111.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | MAINSBRG - HOMERCITY 30B 345 | 160 | 166 | 111.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:FRGT/WRFL | 160 | 166 | 111.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 111.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926A | LN:115:182S | 160 | 166 | 111.58
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | LN:115:182S | 160 | 166 | 111.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HC-MB_30&W-F_171 | 160 | 166 | 111.57
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | LN:115:182S | 160 | 166 | 111.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | LN:115:182S | 160 | 166 | 111.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | DCT:230:79+80+ELM1-2 | 160 | 166 | 111.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | DCT:230:79+80+ELM1-2 | 160 | 166 | 111.55
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | T:78&79 | 160 | 166 | 111.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:HUNT230_R1502 | 160 | 166 | 111.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | LN:115:182S | 160 | 166 | 111.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | B:STOLE230 | 160 | 166 | 111.52
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:5MILE_B | 160 | 166 | 111.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:102 | 160 | 166 | 111.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:102 | 160 | 166 | 111.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | Base Case | 160 | 166 | 111.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | T:77&80 | 160 | 166 | 111.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | First:Lancaster_926A | 160 | 166 | 111.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:182N | 160 | 166 | 111.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:NI1 | LN:115:182S | 160 | 166 | 111.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:HCMB/NWES | 160 | 166 | 111.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | LN:115:182S | 160 | 166 | 111.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | LN:115:182N | 160 | 166 | 111.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:68&160 | 160 | 166 | 111.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | NIAGARA 230/115 1TR | 160 | 166 | 111.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | TB:2/1:NI1 | 160 | 166 | 111.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:NIAW230_2014 | 160 | 166 | 111.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926A | LN:115:182N | 160 | 166 | 111.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | LN:115:182N | 160 | 166 | 111.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | First:Lancaster_926A | 160 | 166 | 111.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:HUNT230_R1402 | 160 | 166 | 111.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | MAINSBRG - HOMERCITY 30B 345 | 160 | 166 | 111.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:78&79 | 160 | 166 | 111.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:345:37S-FM-FV-HC | 160 | 166 | 111.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:HC-MB_30&W-F_171 | 160 | 166 | 111.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 111.33
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | LN:115:182S | 160 | 166 | 111.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:180 | 160 | 166 | 111.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | WTHRS - MEYER 230 | 160 | 166 | 111.31
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:120 | 160 | 166 | 111.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:OSWE_R955 | 160 | 166 | 111.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:OSWEGO 5 | 160 | 166 | 111.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:77&80 | 160 | 166 | 111.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:LAPER_345_2 | 160 | 166 | 111.28
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:LAPER_345_1 | 160 | 166 | 111.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | T:79&80 | 160 | 166 | 111.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | T:79&80 | 160 | 166 | 111.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 111.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 111.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | PACKARD 230/115 3TR | 160 | 166 | 111.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:HUNT230_R1402 | 160 | 166 | 111.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:78&79 | 160 | 166 | 111.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:120 | 160 | 166 | 111.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | NIAGARA - ROBINSON 64 345 | 160 | 166 | 111.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | B:GARD72&79 | 160 | 166 | 111.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:MEYER | 160 | 166 | 111.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:LAFAYETT | 160 | 166 | 111.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | NIAGARA - ROBINSON 64 345 | 160 | 166 | 111.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:OSWE_R965 | 160 | 166 | 111.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV1 | T:79&80 | 160 | 166 | 111.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV2 | T:79&80 | 160 | 166 | 111.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | LN:115:182N | 160 | 166 | 111.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:HUNT230_NEW | 160 | 166 | 111.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:OSWE_R955 | 160 | 166 | 111.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:OSWEGO 5 | 160 | 166 | 111.16
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | LN:115:182S | 160 | 166 | 111.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | PACKARD 230/115 3TR | LN:115:182N | 160 | 166 | 111.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | LN:115:182S | 160 | 166 | 111.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | B:Hunt68 | 160 | 166 | 111.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:LOCKPORT | 160 | 166 | 111.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:OSWE_R965 | 160 | 166 | 111.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:908 NY | 160 | 166 | 111.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_R1202 | 160 | 166 | 111.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1402 | 160 | 166 | 111.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 160 | 166 | 111.05
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | S:HNT_GRD80 | 160 | 166 | 111.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:LOCKPORT | 160 | 166 | 111.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 111.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 111.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 160 | 166 | 111.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:345:37S-FM-FV | 160 | 166 | 111.01
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:5MILE | 160 | 166 | 111.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 111.01
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | LN:115:182N | 160 | 166 | 110.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:9MIPT1 | 160 | 166 | 110.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:908 NY | 160 | 166 | 110.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:77&80 | 160 | 166 | 110.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 110.94
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:77&80 | 160 | 166 | 110.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:908 NY | LN:115:182S | 160 | 166 | 110.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 110.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 160 | 166 | 110.93
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:LAPER_345_4 | 160 | 166 | 110.92
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:LAPER_345_3 | 160 | 166 | 110.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:OSWE_R925 | 160 | 166 | 110.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | B:Hunt68 | 160 | 166 | 110.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:OSWEGO 6 | 160 | 166 | 110.91
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | Base Case | 160 | 166 | 110.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV1 | LN:115:182N | 160 | 166 | 110.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV2 | LN:115:182N | 160 | 166 | 110.89
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:LAPER_345_1 | 160 | 166 | 110.88
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:LAPER_345_2 | 160 | 166 | 110.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV1 | LN:115:182S | 160 | 166 | 110.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV2 | LN:115:182S | 160 | 166 | 110.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 110.87
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 110.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 160 | 166 | 110.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 110.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:3/2:FV | LN:115:182N | 160 | 166 | 110.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | PACKARD 230/115 3TR | 160 | 166 | 110.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | LN:115:182N | 160 | 166 | 110.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:OSWE_R935 | 160 | 166 | 110.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:9MIPT1 | 160 | 166 | 110.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | PACKARD 230/115 3TR | LN:115:182S | 160 | 166 | 110.84
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:LAFAYETT | 160 | 166 | 110.83
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:OAKD345_B5 | 160 | 166 | 110.82
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:LAFA_ELB | 160 | 166 | 110.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | LN:115:182N | 160 | 166 | 110.82
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:OAKD345_B6 | 160 | 166 | 110.8
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 110.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:OSWE_R925 | 160 | 166 | 110.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | B:Hunt67 | 160 | 166 | 110.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 110.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:OSWEGO 6 | 160 | 166 | 110.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:180 | 160 | 166 | 110.78
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:NIAG345_3108 | 160 | 166 | 110.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | B:Hunt68 | 160 | 166 | 110.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | B:Hunt68 | 160 | 166 | 110.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | WTHRS - MEYER 230 | 160 | 166 | 110.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:OSWE_R935 | 160 | 166 | 110.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | DCT:230:79+80+ELM1-2 | 160 | 166 | 110.72
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | NIAG - NEWROCH 1 345 | 160 | 166 | 110.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:FITZPATR | 160 | 166 | 110.7
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | LN:115:182S | 160 | 166 | 110.69
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | LN:115:182S | 160 | 166 | 110.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 110.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:MLS3&OMS | 160 | 166 | 110.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SIN:250 | 160 | 166 | 110.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:MILLST3 | 160 | 166 | 110.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:77&80 | 160 | 166 | 110.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:61&191 | 160 | 166 | 110.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:908 NY | LN:115:182N | 160 | 166 | 110.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:255_345B302 | 160 | 166 | 110.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:MEYER | 160 | 166 | 110.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:705 NY | 160 | 166 | 110.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | First:Lancaster_705 | 160 | 166 | 110.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | LN:115:182S | 160 | 166 | 110.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:COOP345_42-4182 | 160 | 166 | 110.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:GARD230_R873 | 160 | 166 | 110.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | FARMVLY - FARMVLY | 160 | 166 | 110.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | TB:3/2:FV | 160 | 166 | 110.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:MILLST3 | 160 | 166 | 110.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:MLS3&OMS | 160 | 166 | 110.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SIN:250 | 160 | 166 | 110.6
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1502 | 160 | 166 | 110.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:FITZPATR | 160 | 166 | 110.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 110.57
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:31&41 | 160 | 166 | 110.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1402 | 160 | 166 | 110.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | T:79&80 | 160 | 166 | 110.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:HUNT230_NEW | 160 | 166 | 110.53
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:LAPER_345_3 | 160 | 166 | 110.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:LAPER_345_4 | 160 | 166 | 110.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:78&79 | 160 | 166 | 110.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | B:Hunt67 | 160 | 166 | 110.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | B:Hunt68 | 160 | 166 | 110.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | FARMVLY - HOMERCTY | 160 | 166 | 110.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:3/2:FV | LN:115:182S | 160 | 166 | 110.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:61&191 | 160 | 166 | 110.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | LN:115:182S | 160 | 166 | 110.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | R:HC-FV_37&W-F_171 | 160 | 166 | 110.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:195 | 160 | 166 | 110.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:OAKD345_B5 | 160 | 166 | 110.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:LAFA_ELB | 160 | 166 | 110.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:OAKD345_B6 | 160 | 166 | 110.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 110.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | LN:115:182N | 160 | 166 | 110.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:195 | 160 | 166 | 110.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:FV-5M_37&W-F_171 | 160 | 166 | 110.33
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:HC-SR_37&W-F_171 | 160 | 166 | 110.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:GARD230_R823 | 160 | 166 | 110.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | FARMVLY - 5MILE 345 | 160 | 166 | 110.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:HUNT230_R1302 | 160 | 166 | 110.28
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:EDIC345_R915 | 160 | 166 | 110.27
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:38 | 160 | 166 | 110.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1502 | 160 | 166 | 110.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | LN:115:182S | 160 | 166 | 110.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:182S | 160 | 166 | 110.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | B:GARD73&80 | 160 | 166 | 110.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:SEABROOK | 160 | 166 | 110.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:SEAB&OMS | 160 | 166 | 110.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_R1302 | 160 | 166 | 110.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:MP11&41 | 160 | 166 | 110.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | First:Lancaster_STOL_HOMER_345 | 160 | 166 | 110.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | 5 MILE - STOLLE 37A 345 | 160 | 166 | 110.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:STOLE345 | 160 | 166 | 110.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | HOMERCTY - STOLLRD 37 345 | 160 | 166 | 110.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:COOP345_4182 | 160 | 166 | 110.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1502 | 160 | 166 | 110.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:HUNT230_NEW | 160 | 166 | 110.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:MARC345_3208 | 160 | 166 | 110.17
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:NIAG345_3108 | 160 | 166 | 110.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:HUNT230_R1202 | 160 | 166 | 110.16
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:MARC345_3202 | 160 | 166 | 110.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:SEAB&OMS | 160 | 166 | 110.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:SEABROOK | 160 | 166 | 110.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1402 | 160 | 166 | 110.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:78&79 | 160 | 166 | 110.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:COOP345_42-4182 | 160 | 166 | 110.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:38 | 160 | 166 | 110.13
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | NIAG - NEWROCH 1 345 | 160 | 166 | 110.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | B:Hunt67 | 160 | 166 | 110.13
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | MARCY - COOPERS 345 SC | 160 | 166 | 110.12
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:255_345B202 | 160 | 166 | 110.12
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:5M-SR_37&W-F_171 | 160 | 166 | 110.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | LN:115:182N | 160 | 166 | 110.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:77&76 | 160 | 166 | 110.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1502 | 160 | 166 | 110.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SOMERSET - NEWROCH 1 345 | 160 | 166 | 110.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:31&41 | 160 | 166 | 110.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:255_345B302 | 160 | 166 | 110.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | LN:115:182S | 160 | 166 | 110.04
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | LN:115:182S | 160 | 166 | 110.04
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | LN:115:182S | 160 | 166 | 110.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | FARMVLY - FARMVLY | 160 | 166 | 110.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | TB:3/2:FV | 160 | 166 | 110.04
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | LN:115:182S | 160 | 166 | 110.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | LN:115:182S | 160 | 166 | 110.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | LN:115:182S | 160 | 166 | 110.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:HUNT230_NEW | 160 | 166 | 110.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | LN:115:182N | 160 | 166 | 110
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | S:STOLLE345 | 160 | 166 | 109.95
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1502 | 160 | 166 | 109.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:HUNT230_R1502 | 160 | 166 | 109.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:GARD230_R833 | 160 | 166 | 109.89
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | LN:115:182S | 160 | 166 | 109.88
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1402 | 160 | 166 | 109.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1402 | 160 | 166 | 109.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:78&79 | 160 | 166 | 109.87
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:78&79 | 160 | 166 | 109.86
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | LN:115:182S | 160 | 166 | 109.85
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:EDIC345_R935 | 160 | 166 | 109.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:GARD230_T7-12 | 160 | 166 | 109.83
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:39 | 160 | 166 | 109.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | FARMVLY - HOMERCTY | 160 | 166 | 109.82
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:30&40 | 160 | 166 | 109.81
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:EDIC345_R915 | 160 | 166 | 109.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | R:HC-FV_37&W-F_171 | 160 | 166 | 109.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | B:Hunt67 | 160 | 166 | 109.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | TB:2/1:PK3 | 160 | 166 | 109.78
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:67&37A | 160 | 166 | 109.77
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | LN:115:182S | 160 | 166 | 109.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:78&79 | 160 | 166 | 109.75
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:39 | 160 | 166 | 109.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | TB:2/1:PK3 | 160 | 166 | 109.73
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | LN:115:182S | 160 | 166 | 109.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:HUNT230_R1402 | 160 | 166 | 109.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&80 | 160 | 166 | 109.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 160 | 166 | 109.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:MP11&41 | 160 | 166 | 109.7
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:COOP345_4182 | 160 | 166 | 109.7
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MARC345_3208 | 160 | 166 | 109.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MARC345_3202 | 160 | 166 | 109.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:HUNT230_R1302 | 160 | 166 | 109.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MARC_765_7402 | 160 | 166 | 109.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MSU1_7202>7214>7208>7214 | 160 | 166 | 109.65
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | MARCY - COOPERS 345 SC | 160 | 166 | 109.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:EDIC345_R400 | 160 | 166 | 109.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | HQ-NY 765 | 160 | 166 | 109.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | B:Hunt68 | 160 | 166 | 109.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:NI1 | DCT:230:79+80+ELM1-2 | 160 | 166 | 109.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | DCT:230:79+80+ELM1-2 | 160 | 166 | 109.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:77&76 | 160 | 166 | 109.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:345:37S-FM-FV | 160 | 166 | 109.6
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:5MILE | 160 | 166 | 109.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:MARC_765_7402 | 160 | 166 | 109.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:MSU1_7202>7214>7208>7214 | 160 | 166 | 109.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | HQ-NY 765 | 160 | 166 | 109.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | B:Hunt67 | 160 | 166 | 109.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:KINT_39-B112 | 160 | 166 | 109.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:KINT_39-B112 | 160 | 166 | 109.58
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:182S | 160 | 166 | 109.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:HUNT230_R1202 | 160 | 166 | 109.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | LN:115:182N | 160 | 166 | 109.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:KINT_B1-3812 | 160 | 166 | 109.55
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:FV-5M_37&W-F_171 | 160 | 166 | 109.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HC-SR_37&W-F_171 | 160 | 166 | 109.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:KINT_B1-3812 | 160 | 166 | 109.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:255_345B202 | 160 | 166 | 109.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | S:PA_HNTL77 | 160 | 166 | 109.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | TB:2/1:PK3 | 160 | 166 | 109.52
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SOMERSET - NEWROCH 1 345 | 160 | 166 | 109.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | FARMVLY - 5MILE 345 | 160 | 166 | 109.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:182N | 160 | 166 | 109.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:GARD230_T7-12 | 160 | 166 | 109.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:903 NY | LN:115:182S | 160 | 166 | 109.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:GARD230_R823 | 160 | 166 | 109.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:191 | 160 | 166 | 109.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 109.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | S:PA_HNTL78 | 160 | 166 | 109.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SANDY_DC | 160 | 166 | 109.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SANDY_DC&OMS | 160 | 166 | 109.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:191 | 160 | 166 | 109.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:PA230_R3230 | 160 | 166 | 109.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | LN:115:182N | 160 | 166 | 109.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:195 | 160 | 166 | 109.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 109.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SANDY_DC | 160 | 166 | 109.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SANDY_DC&OMS | 160 | 166 | 109.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - HOMERCTY | 160 | 166 | 109.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | R:HC-FV_37&W-F_171 | 160 | 166 | 109.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:EDIC345_R935 | 160 | 166 | 109.33
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:30&40 | 160 | 166 | 109.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | FARMVLY - HOMERCTY | 160 | 166 | 109.31
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:705 NY | 160 | 166 | 109.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | First:Lancaster_705 | 160 | 166 | 109.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | R:HC-FV_37&W-F_171 | 160 | 166 | 109.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:192 | 160 | 166 | 109.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:HUNT230_R1302 | 160 | 166 | 109.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:180 | 160 | 166 | 109.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:192 | 160 | 166 | 109.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:PA230_R3430 | 160 | 166 | 109.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | LN:115:182N | 160 | 166 | 109.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | LN:115:182N | 160 | 166 | 109.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:77&80 | 160 | 166 | 109.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:PA230_R3230 | 160 | 166 | 109.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MASS_765_7108 | 160 | 166 | 109.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lockport_907 | DCT:230:79+80+ELM1-2 | 160 | 166 | 109.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | LN:115:182N | 160 | 166 | 109.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | LN:115:182N | 160 | 166 | 109.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | LN:115:182N | 160 | 166 | 109.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:EDIC345_R400 | 160 | 166 | 109.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MASS_765_7102 | 160 | 166 | 109.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:907 NY | DCT:230:79+80+ELM1-2 | 160 | 166 | 109.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:MASS_765_7108 | 160 | 166 | 109.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:HUNT230_R1202 | 160 | 166 | 109.13
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:MEYER | DCT:230:79+80+ELM1-2 | 160 | 166 | 109.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | B:Hunt68 | 160 | 166 | 109.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:HUNT230_R1302 | 160 | 166 | 109.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | DCT:230:79+80+ELM1-2 | 160 | 166 | 109.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:MASS_765_7102 | 160 | 166 | 109.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | LN:115:182N | 160 | 166 | 109.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:180 | 160 | 166 | 109.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:GARD230_R833 | 160 | 166 | 109.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&80 | 160 | 166 | 109.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | B:Hunt68 | 160 | 166 | 109.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | B:Hunt68 | 160 | 166 | 109.05
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:77&80 | 160 | 166 | 109.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | LN:115:182N | 160 | 166 | 109
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - WTRCR 31 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 109
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:NI1 | T:79&80 | 160 | 166 | 108.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:HUNT230_R1202 | 160 | 166 | 108.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | T:79&80 | 160 | 166 | 108.98
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MARC345_3108 | 160 | 166 | 108.96
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:69J&70K | 160 | 166 | 108.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | FARMVLY - HOMERCTY | 160 | 166 | 108.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | S:PA_HNTL77 | 160 | 166 | 108.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1502 | 160 | 166 | 108.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:GARD230_R823 | 160 | 166 | 108.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | R:HC-FV_37&W-F_171 | 160 | 166 | 108.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:195 | 160 | 166 | 108.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 108.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | S:PA_HNTL78 | 160 | 166 | 108.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 160 | 166 | 108.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 108.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 160 | 166 | 108.76
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 11 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.75
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 12 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.75
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 13 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.75
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 8 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.75
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 9 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.75
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 10 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:GARD230_T7-12 | 160 | 166 | 108.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1402 | 160 | 166 | 108.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:78&79 | 160 | 166 | 108.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | PACKARD 230/115 3TR | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | FARMVLY - HOMERCTY | 160 | 166 | 108.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:GARD230_T7-12 | 160 | 166 | 108.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 7 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-WC_30&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 4 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 5 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 6 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | R:HC-FV_37&W-F_171 | 160 | 166 | 108.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_NEW | 160 | 166 | 108.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | TB:2/1:PK3 | 160 | 166 | 108.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | B:Hunt68 | 160 | 166 | 108.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:GARD230_T7-12 | 160 | 166 | 108.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:GARD230_T7-12 | 160 | 166 | 108.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | S:PA_HNTL77 | 160 | 166 | 108.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_NEW | 160 | 166 | 108.52
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:GINNA | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:115:GINNA | 160 | 166 | 108.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | B:STOLE230 | 160 | 166 | 108.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:GINNA | 160 | 166 | 108.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:GARD230_R833 | 160 | 166 | 108.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:115:GINNA | 160 | 166 | 108.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:GINNA | 160 | 166 | 108.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:HUNT230_NEW | 160 | 166 | 108.48
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_NEW | 160 | 166 | 108.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | S:PA_HNTL78 | 160 | 166 | 108.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 108.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:180 | 160 | 166 | 108.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3430 | 160 | 166 | 108.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:180 | 160 | 166 | 108.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | T:77&80 | 160 | 166 | 108.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:180 | 160 | 166 | 108.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 108.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | S:PA_HNTL77 | 160 | 166 | 108.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:77&80 | 160 | 166 | 108.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:180 | 160 | 166 | 108.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:GARD230_T7-12 | 160 | 166 | 108.36
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lockport_907 | T:79&80 | 160 | 166 | 108.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | B:Hunt67 | 160 | 166 | 108.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_T7-12 | 160 | 166 | 108.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1502 | 160 | 166 | 108.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | T:77&80 | 160 | 166 | 108.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTRCR - MAINSBRG 30A 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCWC/NWES | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:MBWC/NWES | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | R:HC-FV_37&W-F_171 | 160 | 166 | 108.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:HUNT230_R1502 | 160 | 166 | 108.33
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:907 NY | T:79&80 | 160 | 166 | 108.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | B:GARD72&79 | 160 | 166 | 108.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1502 | 160 | 166 | 108.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | FARMVLY - HOMERCTY | 160 | 166 | 108.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:40&41 | 160 | 166 | 108.31
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - WTRCR 31 345 | T:79&80 | 160 | 166 | 108.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | T:79&80 | 160 | 166 | 108.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | B:Hunt68 | 160 | 166 | 108.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | S:PA_HNTL78 | 160 | 166 | 108.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 108.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-WC_30&W-F_171 | T:79&80 | 160 | 166 | 108.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | B:STOLE230 | 160 | 166 | 108.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 108.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | B:Hunt67 | 160 | 166 | 108.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:191 | 160 | 166 | 108.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3430 | 160 | 166 | 108.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | B:Hunt67 | 160 | 166 | 108.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:PA230_R3230 | 160 | 166 | 108.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:195 | 160 | 166 | 108.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1402 | 160 | 166 | 108.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:78&79 | 160 | 166 | 108.16
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | FARMVLY - HOMERCTY | 160 | 166 | 108.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1402 | 160 | 166 | 108.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:HUNT230_R1402 | 160 | 166 | 108.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:78&79 | 160 | 166 | 108.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:78&79 | 160 | 166 | 108.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | S:HNT_GRD80 | 160 | 166 | 108.13
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 8 | T:79&80 | 160 | 166 | 108.12
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 9 | T:79&80 | 160 | 166 | 108.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | B:Hunt68 | 160 | 166 | 108.12
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926A | DCT:230:79+80+ELM1-2 | 160 | 166 | 108.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 10 | T:79&80 | 160 | 166 | 108.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 11 | T:79&80 | 160 | 166 | 108.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 12 | T:79&80 | 160 | 166 | 108.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 13 | T:79&80 | 160 | 166 | 108.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | R:HC-FV_37&W-F_171 | 160 | 166 | 108.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:ROBI230 | 160 | 166 | 108.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:41&33 | 160 | 166 | 108.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 108.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 7 | T:79&80 | 160 | 166 | 108.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 108.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | PACKARD 230/115 3TR | T:79&80 | 160 | 166 | 108.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:192 | 160 | 166 | 108.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | B:Hunt67 | 160 | 166 | 108.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:54/921 | 160 | 166 | 108.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTRCR - MAINSBRG 30A 345 | T:79&80 | 160 | 166 | 108.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 4 | T:79&80 | 160 | 166 | 108.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 5 | T:79&80 | 160 | 166 | 108.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 6 | T:79&80 | 160 | 166 | 108.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:GARD230_R873 | 160 | 166 | 108
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCWC/NWES | T:79&80 | 160 | 166 | 108
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:MBWC/NWES | T:79&80 | 160 | 166 | 108
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:54/921 | 160 | 166 | 107.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | LN:115:54/921 | 160 | 166 | 107.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | LN:115:54/921 | 160 | 166 | 107.97
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_NEW | 160 | 166 | 107.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 107.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-WC_30&W-F_171 | LN:115:182S | 160 | 166 | 107.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | B:Hunt68 | 160 | 166 | 107.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | FARMVLY - HOMERCTY | 160 | 166 | 107.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTRCR - MAINSBRG 30A 345 | LN:115:182S | 160 | 166 | 107.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCWC/NWES | LN:115:182S | 160 | 166 | 107.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:MBWC/NWES | LN:115:182S | 160 | 166 | 107.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-WC_30&W-F_171 | LN:115:182N | 160 | 166 | 107.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:345:SOMERSET | 160 | 166 | 107.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:KINTIGH | 160 | 166 | 107.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | TB:2/1:PK3 | 160 | 166 | 107.88
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:GINNA | T:79&80 | 160 | 166 | 107.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:HUNT230_R1502 | 160 | 166 | 107.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:345:SOMERSET | 160 | 166 | 107.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:KINTIGH | 160 | 166 | 107.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | R:HC-FV_37&W-F_171 | 160 | 166 | 107.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:180 | 160 | 166 | 107.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTRCR - MAINSBRG 30A 345 | LN:115:182N | 160 | 166 | 107.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCWC/NWES | LN:115:182N | 160 | 166 | 107.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:MBWC/NWES | LN:115:182N | 160 | 166 | 107.84
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | T:79&80 | 160 | 166 | 107.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:191 | 160 | 166 | 107.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | B:Hunt68 | 160 | 166 | 107.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | T:77&80 | 160 | 166 | 107.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | FARMVLY - HOMERCTY | 160 | 166 | 107.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | B:STOLE230 | 160 | 166 | 107.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | B:STOLE230 | 160 | 166 | 107.73
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | DCT:230:79+80+ELM1-2 | 160 | 166 | 107.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 107.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | B:Hunt68 | 160 | 166 | 107.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | R:HC-FV_37&W-F_171 | 160 | 166 | 107.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926B | LN:115:54/921 | 160 | 166 | 107.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:180 | 160 | 166 | 107.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 107.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:HUNT230_R1402 | 160 | 166 | 107.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:78&79 | 160 | 166 | 107.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | T:77&80 | 160 | 166 | 107.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:192 | 160 | 166 | 107.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:BRUCE5 | 160 | 166 | 107.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1302 | 160 | 166 | 107.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | B:GARD73&80 | 160 | 166 | 107.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:BRUCE5 | 160 | 166 | 107.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1202 | 160 | 166 | 107.6
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | T:79&80 | 160 | 166 | 107.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | T:77&80 | 160 | 166 | 107.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | T:77&80 | 160 | 166 | 107.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | T:77&80 | 160 | 166 | 107.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | B:Hunt68 | 160 | 166 | 107.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1202 | 160 | 166 | 107.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:HUNT230_R1302 | 160 | 166 | 107.55
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | T:79&80 | 160 | 166 | 107.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:705 NY | 160 | 166 | 107.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | First:Lancaster_705 | 160 | 166 | 107.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | B:Hunt67 | 160 | 166 | 107.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:HUNT230_R1202 | 160 | 166 | 107.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | B:Hunt68 | 160 | 166 | 107.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | B:Hunt68 | 160 | 166 | 107.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1302 | 160 | 166 | 107.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_NEW | 160 | 166 | 107.45
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | T:79&80 | 160 | 166 | 107.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:54/921 | 160 | 166 | 107.43
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1202 | 160 | 166 | 107.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 107.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | B:STOLE230 | 160 | 166 | 107.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:3/2:FV | DCT:230:79+80+ELM1-2 | 160 | 166 | 107.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | DCT:230:79+80+ELM1-2 | 160 | 166 | 107.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | T:77&80 | 160 | 166 | 107.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | T:77&80 | 160 | 166 | 107.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | B:Hunt68 | 160 | 166 | 107.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:34&42 | 160 | 166 | 107.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926A | T:79&80 | 160 | 166 | 107.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:HUNT230_R1502 | 160 | 166 | 107.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:101 | 160 | 166 | 107.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:180 | 160 | 166 | 107.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | B:Hunt68 | 160 | 166 | 107.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:908 NY | DCT:230:79+80+ELM1-2 | 160 | 166 | 107.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | B:STOLE230 | 160 | 166 | 107.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | T:77&80 | 160 | 166 | 107.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:SCRIBA_R230 | 160 | 166 | 107.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:SCRIBA_R925 | 160 | 166 | 107.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:9 MI PT2 | 160 | 166 | 107.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:40&41 | 160 | 166 | 107.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_T7-12 | 160 | 166 | 107.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | B:Hunt67 | 160 | 166 | 107.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | SB:HUNT230_R1502 | 160 | 166 | 107.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:HUNT230_R1302 | 160 | 166 | 107.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:40&41 | 160 | 166 | 107.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:9 MI PT2 | 160 | 166 | 107.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:SCRIBA_R925 | 160 | 166 | 107.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:SCRIBA_R230 | 160 | 166 | 107.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:HUNT230_R1402 | 160 | 166 | 107.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:PA230_R3230 | 160 | 166 | 107.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:195 | 160 | 166 | 107.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:195 | 160 | 166 | 107.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:191 | 160 | 166 | 107.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:GARD230_T7-12 | 160 | 166 | 107.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | T:78&79 | 160 | 166 | 107.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:HUNT230_R1502 | 160 | 166 | 107.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:HUNT230_R1502 | 160 | 166 | 107.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | B:Hunt68 | 160 | 166 | 107.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | LN:115:180 | 160 | 166 | 107.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | S:HNT_GRD80 | 160 | 166 | 107.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1202 | 160 | 166 | 107.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:102 | 160 | 166 | 107.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:54/921 | 160 | 166 | 107.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1502 | 160 | 166 | 107
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:180 | 160 | 166 | 106.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | B:GARD72&79 | 160 | 166 | 106.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 106.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | First:Lancaster_926B | 160 | 166 | 106.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:PA230_R3230 | 160 | 166 | 106.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 106.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:192 | 160 | 166 | 106.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:DARLIN1 | 160 | 166 | 106.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:DARLIN1 | 160 | 166 | 106.94
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | T:79&80 | 160 | 166 | 106.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:195 | 160 | 166 | 106.92
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:77&80 | 160 | 166 | 106.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:HUNT230_R1502 | 160 | 166 | 106.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | SB:HUNT230_R1402 | 160 | 166 | 106.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | T:78&79 | 160 | 166 | 106.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | B:Hunt68 | 160 | 166 | 106.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:54/921 | 160 | 166 | 106.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | T:77&80 | 160 | 166 | 106.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_NEW | 160 | 166 | 106.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:HUNT230_R1402 | 160 | 166 | 106.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 106.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | T:78&79 | 160 | 166 | 106.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | T:78&79 | 160 | 166 | 106.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | T:78&79 | 160 | 166 | 106.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1402 | 160 | 166 | 106.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | S:PA_HNTL77 | 160 | 166 | 106.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:HUNT230_R1402 | 160 | 166 | 106.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | TB:2/1:PK3 | 160 | 166 | 106.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | TB:2/1:PK3 | 160 | 166 | 106.85
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | DCT:230:79+80+ELM1-2 | 160 | 166 | 106.84
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | DCT:230:79+80+ELM1-2 | 160 | 166 | 106.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:41&33 | 160 | 166 | 106.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:GARD230_R873 | 160 | 166 | 106.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:ROBI230 | 160 | 166 | 106.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:180 | 160 | 166 | 106.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 106.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:40&41 | 160 | 166 | 106.8
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:HUNT230_R1302 | 160 | 166 | 106.79
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | B:STOLE230 | 160 | 166 | 106.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | S:HNT_GRD80 | 160 | 166 | 106.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:41&33 | 160 | 166 | 106.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 106.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:HUNT230_NEW | 160 | 166 | 106.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | LN:115:180 | 160 | 166 | 106.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_NEW | 160 | 166 | 106.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | S:PA_HNTL77 | 160 | 166 | 106.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | TB:2/1:PK3 | 160 | 166 | 106.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:40&41 | 160 | 166 | 106.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:PA230_R3230 | 160 | 166 | 106.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:195 | 160 | 166 | 106.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:195 | 160 | 166 | 106.73
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | B:STOLE230 | 160 | 166 | 106.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 106.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | S:PA_HNTL78 | 160 | 166 | 106.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 106.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV1 | DCT:230:79+80+ELM1-2 | 160 | 166 | 106.7
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV2 | DCT:230:79+80+ELM1-2 | 160 | 166 | 106.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | B:STOLE230 | 160 | 166 | 106.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | B:GARD72&79 | 160 | 166 | 106.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:HUNT230_R1402 | 160 | 166 | 106.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | T:78&79 | 160 | 166 | 106.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-MB_30&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 166 | 106.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 106.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 106.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:120 | 160 | 166 | 106.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:40&41 | 160 | 166 | 106.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 106.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 106.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 106.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | SB:HUNT230_R1502 | 160 | 166 | 106.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | S:PA_HNTL78 | 160 | 166 | 106.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 78 230 | 160 | 166 | 106.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:3/2:FV | T:79&80 | 160 | 166 | 106.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | T:79&80 | 160 | 166 | 106.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:HUNT230_NEW | 160 | 166 | 106.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | B:STOLE230 | 160 | 166 | 106.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | B:Hunt67 | 160 | 166 | 106.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | B:Hunt67 | 160 | 166 | 106.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 77 230 | 160 | 166 | 106.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCMB/NWES | DCT:230:79+80+ELM1-2 | 160 | 166 | 106.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 106.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:GARD230_R823 | 160 | 166 | 106.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:54/921 | 160 | 166 | 106.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | B:Hunt67 | 160 | 166 | 106.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | T:77&80 | 160 | 166 | 106.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1302 | 160 | 166 | 106.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCMB/NWES | LN:115:182S | 160 | 166 | 106.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:HUNT230_R1502 | 160 | 166 | 106.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | LN:115:180 | 160 | 166 | 106.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:54/921 | 160 | 166 | 106.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1202 | 160 | 166 | 106.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | SB:HUNT230_R1502 | 160 | 166 | 106.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | SB:HUNT230_R1502 | 160 | 166 | 106.47
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:908 NY | T:79&80 | 160 | 166 | 106.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:40&41 | 160 | 166 | 106.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 106.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | B:Hunt68 | 160 | 166 | 106.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | B:Hunt68 | 160 | 166 | 106.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:40&41 | 160 | 166 | 106.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | SB:HUNT230_R1402 | 160 | 166 | 106.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | T:78&79 | 160 | 166 | 106.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:GARD230_R873 | 160 | 166 | 106.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | B:Hunt68 | 160 | 166 | 106.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:41&33 | 160 | 166 | 106.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&80 | 160 | 166 | 106.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | T:77&80 | 160 | 166 | 106.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | MAINSBRG - HOMERCITY 30B 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 106.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-MB_30&W-F_171 | T:79&80 | 160 | 166 | 106.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&80 | 160 | 166 | 106.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:180 | 160 | 166 | 106.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | B:GARD73&80 | 160 | 166 | 106.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:195 | 160 | 166 | 106.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-MB_30&W-F_171 | LN:115:182S | 160 | 166 | 106.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 160 | 166 | 106.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | T:79&80 | 160 | 166 | 106.36
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | T:79&80 | 160 | 166 | 106.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | B:Hunt68 | 160 | 166 | 106.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | B:Hunt68 | 160 | 166 | 106.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:61&64 | 160 | 166 | 106.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCMB/NWES | LN:115:182N | 160 | 166 | 106.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCMB/NWES | T:79&80 | 160 | 166 | 106.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | MAINSBRG - HOMERCITY 30B 345 | LN:115:182S | 160 | 166 | 106.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:61&64 | 160 | 166 | 106.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | B:Hunt68 | 160 | 166 | 106.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | B:Hunt68 | 160 | 166 | 106.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | B:Hunt68 | 160 | 166 | 106.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL77 | 160 | 166 | 106.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | TB:2/1:PK3 | 160 | 166 | 106.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | T:77&80 | 160 | 166 | 106.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | B:Hunt68 | 160 | 166 | 106.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | TB:2/1:PK3 | 160 | 166 | 106.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | B:Hunt68 | 160 | 166 | 106.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | B:GARD72&79 | 160 | 166 | 106.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | SB:GARD230_T7-12 | 160 | 166 | 106.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:HUNT230_R1402 | 160 | 166 | 106.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:78&79 | 160 | 166 | 106.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:77&80 | 160 | 166 | 106.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | SB:HUNT230_R1402 | 160 | 166 | 106.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | T:78&79 | 160 | 166 | 106.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | SB:HUNT230_R1402 | 160 | 166 | 106.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | T:78&79 | 160 | 166 | 106.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-MB_30&W-F_171 | LN:115:182N | 160 | 166 | 106.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | B:Hunt67 | 160 | 166 | 106.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:41&33 | 160 | 166 | 106.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:GARD230_R833 | 160 | 166 | 106.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | T:77&80 | 160 | 166 | 106.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | T:77&80 | 160 | 166 | 106.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | S:HNT_GRD80 | 160 | 166 | 106.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:5MILE_B | 160 | 166 | 106.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | MAINSBRG - HOMERCITY 30B 345 | LN:115:182N | 160 | 166 | 106.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 106.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:GARD230_R823 | 160 | 166 | 106.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:ROBI230 | 160 | 166 | 106.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:79&80 | 160 | 166 | 106.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:54/921 | 160 | 166 | 106.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | SB:HUNT230_R1502 | 160 | 166 | 106.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL78 | 160 | 166 | 106.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 106.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:34&42 | 160 | 166 | 106.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | T:77&80 | 160 | 166 | 106.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:77&80 | 160 | 166 | 106.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:191 | 160 | 166 | 106.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:191 | 160 | 166 | 106.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 106.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 106.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:GARD230_R873 | 160 | 166 | 106.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:ROBI230 | 160 | 166 | 106.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 106.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:34&42 | 160 | 166 | 106.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:GARD230_T7-12 | 160 | 166 | 106.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:GARD230_T7-12 | 160 | 166 | 106.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 106.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 7 | LN:115:182S | 160 | 166 | 106.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV1 | T:79&80 | 160 | 166 | 106.05
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV2 | T:79&80 | 160 | 166 | 106.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:191 | 160 | 166 | 106.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:HUNT230_R1302 | 160 | 166 | 106.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | SB:HUNT230_R1502 | 160 | 166 | 106.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:195 | 160 | 166 | 106.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | Base Case | 160 | 166 | 106.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 4 | LN:115:182S | 160 | 166 | 106.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 5 | LN:115:182S | 160 | 166 | 106.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 6 | LN:115:182S | 160 | 166 | 106.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 106.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:54/921 | 160 | 166 | 105.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1302 | 160 | 166 | 105.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:HUNT230_NEW | 160 | 166 | 105.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | SB:GARD230_T7-12 | 160 | 166 | 105.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 105.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1202 | 160 | 166 | 105.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:HUNT230_R1202 | 160 | 166 | 105.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:PA230_R3430 | 160 | 166 | 105.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:192 | 160 | 166 | 105.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:192 | 160 | 166 | 105.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | B:GARD73&80 | 160 | 166 | 105.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:ROBI230 | 160 | 166 | 105.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | SB:HUNT230_R1402 | 160 | 166 | 105.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | T:78&79 | 160 | 166 | 105.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:61&64 | 160 | 166 | 105.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:192 | 160 | 166 | 105.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | FARMVLY - HOMERCTY | 160 | 166 | 105.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | FARMVLY - HOMERCTY | 160 | 166 | 105.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | B:GARD72&79 | 160 | 166 | 105.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | LN:115:195 | 160 | 166 | 105.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:54/921 | 160 | 166 | 105.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | R:HC-FV_37&W-F_171 | 160 | 166 | 105.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | R:HC-FV_37&W-F_171 | 160 | 166 | 105.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:GARD230_R833 | 160 | 166 | 105.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1202 | 160 | 166 | 105.83
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:HUNT230_R1502 | 160 | 166 | 105.81
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | DCT:230:79+80+ELM1-2 | 160 | 166 | 105.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:41&33 | 160 | 166 | 105.81
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:77&80 | 160 | 166 | 105.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1302 | 160 | 166 | 105.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | SB:HUNT230_R1402 | 160 | 166 | 105.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | T:78&79 | 160 | 166 | 105.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | S:HNT_GRD80 | 160 | 166 | 105.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:133 | TB:2/1:PK3 | 160 | 166 | 105.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:LAPER_345_1 | 160 | 166 | 105.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:LAPER_345_2 | 160 | 166 | 105.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | TB:2/1:PK3 | 160 | 166 | 105.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | SB:HUNT230_R1502 | 160 | 166 | 105.77
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 105.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | B:GARD73&80 | 160 | 166 | 105.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:191 | 160 | 166 | 105.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 105.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:926 NY | LN:115:54/921 | 160 | 166 | 105.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:191 | 160 | 166 | 105.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:34&42 | 160 | 166 | 105.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:LAFAYETT | 160 | 166 | 105.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:HUNT230_NEW | 160 | 166 | 105.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 105.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | SB:HUNT230_R1502 | 160 | 166 | 105.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | SB:HUNT230_R1502 | 160 | 166 | 105.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL77 | 160 | 166 | 105.7
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:HUNT230_R1502 | 160 | 166 | 105.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:GARD230_R873 | 160 | 166 | 105.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 105.69
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 105.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:133 | LN:115:195 | 160 | 166 | 105.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:191 | 160 | 166 | 105.65
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:HUNT230_R1202 | 160 | 166 | 105.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 105.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:40&41 | 160 | 166 | 105.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | TB:2/1:PK3 | 160 | 166 | 105.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:HUNT230_R1302 | 160 | 166 | 105.6
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 160 | 166 | 105.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:192 | 160 | 166 | 105.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | SB:HUNT230_R1502 | 160 | 166 | 105.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:133 | 160 | 166 | 105.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | B:Hunt67 | 160 | 166 | 105.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:345:37S-FM-FV-HC | 160 | 166 | 105.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:192 | 160 | 166 | 105.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | SB:HUNT230_NEW | 160 | 166 | 105.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:41&33 | 160 | 166 | 105.58
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:HUNT230_R1402 | 160 | 166 | 105.57
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:78&79 | 160 | 166 | 105.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:HUNT230_NEW | 160 | 166 | 105.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 105.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | S:PA_HNTL78 | 160 | 166 | 105.57
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | B:Hunt68 | 160 | 166 | 105.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:34&42 | 160 | 166 | 105.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:195 | 160 | 166 | 105.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | SB:HUNT230_R1402 | 160 | 166 | 105.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | T:78&79 | 160 | 166 | 105.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:40&41 | 160 | 166 | 105.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:HUNT230_NEW | 160 | 166 | 105.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 105.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | S:PA_HNTL77 | 160 | 166 | 105.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:192 | 160 | 166 | 105.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 105.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:GARD230_T7-12 | 160 | 166 | 105.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:GARD230_R823 | 160 | 166 | 105.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_NEW | 160 | 166 | 105.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:38 | 160 | 166 | 105.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | SB:HUNT230_R1402 | 160 | 166 | 105.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | T:78&79 | 160 | 166 | 105.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | SB:HUNT230_R1402 | 160 | 166 | 105.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | T:78&79 | 160 | 166 | 105.48
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN GILBOA #3&4 | 160 | 166 | 105.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:61&64 | 160 | 166 | 105.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | LN:115:180 | 160 | 166 | 105.47
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GILB345_3302 | 160 | 166 | 105.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:41&33 | 160 | 166 | 105.46
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:HUNT230_R1402 | 160 | 166 | 105.45
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:78&79 | 160 | 166 | 105.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:40&41 | 160 | 166 | 105.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | ROBINSON - STOLLRD 65 230 | 160 | 166 | 105.45
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GILB345_3308 | 160 | 166 | 105.44
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL78 | 160 | 166 | 105.44
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 105.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:LAPER_345_4 | 160 | 166 | 105.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:LAPER_345_3 | 160 | 166 | 105.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | B:Hunt67 | 160 | 166 | 105.44
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:NTHF3&4 | 160 | 166 | 105.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | LN:115:180 | 160 | 166 | 105.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:133 | 160 | 166 | 105.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | B:Hunt67 | 160 | 166 | 105.43
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN GILBOA #1&2 | 160 | 166 | 105.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:GILB345_3202 | 160 | 166 | 105.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | T:79&80 | 160 | 166 | 105.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 7 | DCT:230:79+80+ELM1-2 | 160 | 166 | 105.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SRIPL - ERIE E 69 230 | 160 | 166 | 105.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 105.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | S:PA_HNTL78 | 160 | 166 | 105.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 4 | DCT:230:79+80+ELM1-2 | 160 | 166 | 105.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 5 | DCT:230:79+80+ELM1-2 | 160 | 166 | 105.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 6 | DCT:230:79+80+ELM1-2 | 160 | 166 | 105.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | B:GARD73&80 | 160 | 166 | 105.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | SB:HUNT230_R1402 | 160 | 166 | 105.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | T:78&79 | 160 | 166 | 105.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 160 | 166 | 105.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 105.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 105.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | B:Hunt67 | 160 | 166 | 105.36
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:907 NY | 160 | 166 | 105.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 105.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | SB:HUNT230_R1502 | 160 | 166 | 105.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:OAKD345_B5 | 160 | 166 | 105.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 105.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:OAKD345_B6 | 160 | 166 | 105.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 105.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:LAFA_ELB | 160 | 166 | 105.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:41&33 | 160 | 166 | 105.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:GARD230_R823 | 160 | 166 | 105.33
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:GARD230_R823 | 160 | 166 | 105.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:130 | TB:2/1:PK3 | 160 | 166 | 105.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | LN:115:182S | 160 | 166 | 105.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | TB:2/1:PK3 | 160 | 166 | 105.31
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:115:AMERT | 160 | 166 | 105.3
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | First:Lockport_907 | 160 | 166 | 105.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:GARD230_T7-12 | 160 | 166 | 105.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 105.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:PA230_R3430 | 160 | 166 | 105.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 105.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL78 | 160 | 166 | 105.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | B:Hunt67 | 160 | 166 | 105.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | B:GARD72&79 | 160 | 166 | 105.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:SITHE 1 | 160 | 166 | 105.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:SITHE 2 | 160 | 166 | 105.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | B:Hunt67 | 160 | 166 | 105.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:130 | LN:115:195 | 160 | 166 | 105.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE_B | 160 | 166 | 105.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | LN:115:191 | 160 | 166 | 105.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3230 | 160 | 166 | 105.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | LN:115:182S | 160 | 166 | 105.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | LN:115:182S | 160 | 166 | 105.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lockport_907 | LN:115:182S | 160 | 166 | 105.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 160 | 166 | 105.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:180 | 160 | 166 | 105.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3230 | 160 | 166 | 105.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 105.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN: IND PT 2 | 160 | 166 | 105.17
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:907 NY | LN:115:182S | 160 | 166 | 105.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:41&33 | 160 | 166 | 105.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:5MILE_B | 160 | 166 | 105.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL77 | 160 | 166 | 105.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:GARD230_R833 | 160 | 166 | 105.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | S:HNT_GRD80 | 160 | 166 | 105.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:101 | 160 | 166 | 105.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:130 | 160 | 166 | 105.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:180 | 160 | 166 | 105.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | SB:HUNT230_NEW | 160 | 166 | 105.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:COOP345_42-4182 | 160 | 166 | 105.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 7 | LN:115:182N | 160 | 166 | 105.13
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | STONYCR - WTHRS 230 | 160 | 166 | 105.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:39 | 160 | 166 | 105.12
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:BUCHN_11 | 160 | 166 | 105.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:NIAG345_3108 | 160 | 166 | 105.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:101 | 160 | 166 | 105.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:BUCHN_9 | 160 | 166 | 105.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | NIAG - NEWROCH 1 345 | 160 | 166 | 105.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | SB:HUNT230_R1402 | 160 | 166 | 105.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | T:78&79 | 160 | 166 | 105.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:HUNT230_R1302 | 160 | 166 | 105.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | B:GARD72&79 | 160 | 166 | 105.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:GARD230_R873 | 160 | 166 | 105.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 105.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | LN:115:192 | 160 | 166 | 105.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:34&42 | 160 | 166 | 105.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 4 | LN:115:182N | 160 | 166 | 105.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 5 | LN:115:182N | 160 | 166 | 105.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 6 | LN:115:182N | 160 | 166 | 105.08
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:BUCHN_7 | 160 | 166 | 105.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:31&41 | 160 | 166 | 105.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:61&64 | 160 | 166 | 105.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 105.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 105.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | S:PA_HNTL78 | 160 | 166 | 105.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:BETHSTM | 160 | 166 | 105.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:255_345B302 | 160 | 166 | 105.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:77&80 | 160 | 166 | 105.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | LN:115:180 | 160 | 166 | 105.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:GARD230_R833 | 160 | 166 | 105.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:130 | 160 | 166 | 105.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | TB:2/1:PK3 | 160 | 166 | 105.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:191 | 160 | 166 | 105.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | S:HNT_GRD80 | 160 | 166 | 105
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 105
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:40&41 | 160 | 166 | 104.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | B:Hunt68 | 160 | 166 | 104.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:926 NY | 160 | 166 | 104.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:HUNT230_R1202 | 160 | 166 | 104.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 104.98
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN: IND PT 3 | 160 | 166 | 104.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | B:STOLE230 | 160 | 166 | 104.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CANDQUA - STNYRDG 68A 230 | SB:GARD230_T7-12 | 160 | 166 | 104.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:129 | TB:2/1:PK3 | 160 | 166 | 104.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:34&42 | 160 | 166 | 104.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:61&64 | 160 | 166 | 104.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:345:37S-FM-FV-HC | 160 | 166 | 104.93
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:BUCHS_1 | 160 | 166 | 104.92
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:BUCHS_3 | 160 | 166 | 104.92
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:HUNT230_NEW | 160 | 166 | 104.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:GARD230_R873 | 160 | 166 | 104.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 104.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 104.91
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:GARD230_R833 | 160 | 166 | 104.9
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | LN:115:182S | 160 | 166 | 104.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:133 | LN:115:191 | 160 | 166 | 104.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_NEW | 160 | 166 | 104.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:GARD230_T7-12 | 160 | 166 | 104.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:102 | 160 | 166 | 104.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:129 | LN:115:195 | 160 | 166 | 104.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | SB:HUNT230_NEW | 160 | 166 | 104.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | SB:HUNT230_NEW | 160 | 166 | 104.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:345:37S-FM-FV-HC | 160 | 166 | 104.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | Base Case | 160 | 166 | 104.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:HUNT230_R1302 | 160 | 166 | 104.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:NIAG345_3108 | 160 | 166 | 104.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | NIAG - NEWROCH 1 345 | 160 | 166 | 104.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:192 | 160 | 166 | 104.85
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | B:Hunt68 | 160 | 166 | 104.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:255_345B302 | 160 | 166 | 104.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:102 | 160 | 166 | 104.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 160 | 166 | 104.83
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:STONY230 | 160 | 166 | 104.82
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:DKSR/WRFL | 160 | 166 | 104.82
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | B:Hunt68 | 160 | 166 | 104.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 104.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | Base Case | 160 | 166 | 104.82
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:EESR/WF/NWES | 160 | 166 | 104.81
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926A | LN:115:182S | 160 | 166 | 104.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:EDIC345_R915 | 160 | 166 | 104.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:NIAG345_3108 | 160 | 166 | 104.8
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | ERIE E - 4 MILE 230 | 160 | 166 | 104.79
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:67&68&BW | 160 | 166 | 104.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | NIAG - NEWROCH 1 345 | 160 | 166 | 104.78
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN GILBOA #3&4 | 160 | 166 | 104.77
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GILB345_3302 | 160 | 166 | 104.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | B:Hunt67 | 160 | 166 | 104.77
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:77&80 | 160 | 166 | 104.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:133 | LN:115:192 | 160 | 166 | 104.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | B:GARD73&80 | 160 | 166 | 104.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | SB:GARD230_T7-12 | 160 | 166 | 104.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | SB:GARD230_T7-12 | 160 | 166 | 104.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | SB:GARD230_T7-12 | 160 | 166 | 104.76
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1502 | 160 | 166 | 104.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:NIAG345_3108 | 160 | 166 | 104.75
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GILB345_3308 | 160 | 166 | 104.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:NTHF3&4 | 160 | 166 | 104.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:34&42 | 160 | 166 | 104.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:HUNT230_R1202 | 160 | 166 | 104.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:EESR/WRFL | 160 | 166 | 104.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:MP11&41 | 160 | 166 | 104.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:COOP345_4182 | 160 | 166 | 104.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B302 | 160 | 166 | 104.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | Base Case | 160 | 166 | 104.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt67 | 160 | 166 | 104.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | NIAG - NEWROCH 1 345 | 160 | 166 | 104.72
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:77&80 | 160 | 166 | 104.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN GILBOA #1&2 | 160 | 166 | 104.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:GILB345_3202 | 160 | 166 | 104.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | LN:115:182S | 160 | 166 | 104.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:MARC345_3208 | 160 | 166 | 104.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:MARC345_3202 | 160 | 166 | 104.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:54/921 | 160 | 166 | 104.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:129 | 160 | 166 | 104.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:PA230_R3430 | 160 | 166 | 104.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 160 | 166 | 104.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 104.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | B:STOLE230 | 160 | 166 | 104.7
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1402 | 160 | 166 | 104.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | FARMVLY - HOMERCTY | 160 | 166 | 104.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | FARMVLY - HOMERCTY | 160 | 166 | 104.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:54/921 | 160 | 166 | 104.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | SB:GARD230_T7-12 | 160 | 166 | 104.69
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:78&79 | 160 | 166 | 104.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | MARCY - COOPERS 345 SC | 160 | 166 | 104.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:255_345B302 | 160 | 166 | 104.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:MBWC/NWES | 160 | 166 | 104.67
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:HCWC/NWES | 160 | 166 | 104.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:77&76 | 160 | 166 | 104.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:34&42 | 160 | 166 | 104.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | B:Hunt67 | 160 | 166 | 104.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | B:Hunt67 | 160 | 166 | 104.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:HUNT230_R1302 | 160 | 166 | 104.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_1 | 160 | 166 | 104.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_2 | 160 | 166 | 104.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:120 | 160 | 166 | 104.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:133 | 160 | 166 | 104.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 104.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:195 | 160 | 166 | 104.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 104.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:HUNT230_R1302 | 160 | 166 | 104.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | R:HC-FV_37&W-F_171 | 160 | 166 | 104.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | R:HC-FV_37&W-F_171 | 160 | 166 | 104.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:WATRC345_B1-3042 | 160 | 166 | 104.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | WTRCR - MAINSBRG 30A 345 | 160 | 166 | 104.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:WATRC345_30-3142 | 160 | 166 | 104.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 104.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SIN:120_130 | 160 | 166 | 104.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SIN:130 | 160 | 166 | 104.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:W97&W98 | 160 | 166 | 104.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 7 | T:79&80 | 160 | 166 | 104.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:120 | 160 | 166 | 104.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_2 | 160 | 166 | 104.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_1 | 160 | 166 | 104.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:LAFAYETT | 160 | 166 | 104.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | First:Lancaster_926A | 160 | 166 | 104.6
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:WTHERS230 | 160 | 166 | 104.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | B:GARD73&80 | 160 | 166 | 104.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:129 | 160 | 166 | 104.6
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:HC-WC_30&W-F_171 | 160 | 166 | 104.59
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 4 | T:79&80 | 160 | 166 | 104.59
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 5 | T:79&80 | 160 | 166 | 104.59
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 6 | T:79&80 | 160 | 166 | 104.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:255_345B202 | 160 | 166 | 104.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 104.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | Base Case | 160 | 166 | 104.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SOMERSET - NEWROCH 1 345 | 160 | 166 | 104.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | SB:HUNT230_NEW | 160 | 166 | 104.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:HUNT230_R1202 | 160 | 166 | 104.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:HUNT230_R1202 | 160 | 166 | 104.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 104.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:LAFAYETT | 160 | 166 | 104.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | S:PA_HNTL77 | 160 | 166 | 104.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:GARD230_T7-12 | 160 | 166 | 104.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1202 | 160 | 166 | 104.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | First:Lancaster_705 | 160 | 166 | 104.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:705 NY | 160 | 166 | 104.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | LN:115:180 | 160 | 166 | 104.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:191 | 160 | 166 | 104.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:SITHE 2 | 160 | 166 | 104.53
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:SITHE 1 | 160 | 166 | 104.53
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:907 NY | 160 | 166 | 104.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | LN:115:180 | 160 | 166 | 104.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | LN:115:180 | 160 | 166 | 104.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1302 | 160 | 166 | 104.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:GARD230_R823 | 160 | 166 | 104.53
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:AMERT | LN:115:182N | 160 | 166 | 104.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:345:37S-FM-FV-HC | 160 | 166 | 104.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:PA230_R3430 | 160 | 166 | 104.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:133 | 160 | 166 | 104.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:34&42 | 160 | 166 | 104.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | LN:115:180 | 160 | 166 | 104.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | B:Hunt67 | 160 | 166 | 104.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:PA230_R3430 | 160 | 166 | 104.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | SB:HUNT230_NEW | 160 | 166 | 104.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:GINNA | LN:115:182N | 160 | 166 | 104.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:115:AMERT | 160 | 166 | 104.48
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | First:Lockport_907 | 160 | 166 | 104.48
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | LN:115:182N | 160 | 166 | 104.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | B:Hunt67 | 160 | 166 | 104.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:ROBI230 | 160 | 166 | 104.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:180 | 160 | 166 | 104.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:PA230_R3430 | 160 | 166 | 104.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:ROBI230 | 160 | 166 | 104.46
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN: IND PT 2 | 160 | 166 | 104.45
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 104.44
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | S:PA_HNTL78 | 160 | 166 | 104.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | SB:GARD230_T7-12 | 160 | 166 | 104.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:130 | LN:115:191 | 160 | 166 | 104.44
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:EESR/NWES | 160 | 166 | 104.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 104.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:EDIC345_R935 | 160 | 166 | 104.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:38 | 160 | 166 | 104.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:68&160 | 160 | 166 | 104.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | FARMVLY - HOMERCTY | 160 | 166 | 104.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 104.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | DUNKIRK - SRIPL 68 230 | 160 | 166 | 104.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:SRIPLEY | 160 | 166 | 104.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:BUCHN_11 | 160 | 166 | 104.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | S:PA_HNTL77 | 160 | 166 | 104.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:30&40 | 160 | 166 | 104.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:5MILE_B | 160 | 166 | 104.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | SB:HUNT230_R1302 | 160 | 166 | 104.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | SB:HUNT230_NEW | 160 | 166 | 104.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | SB:HUNT230_NEW | 160 | 166 | 104.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:192 | 160 | 166 | 104.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 104.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:BUCHN_9 | 160 | 166 | 104.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | B:STOLE230 | 160 | 166 | 104.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | SB:HUNT230_NEW | 160 | 166 | 104.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:BUCHN_7 | 160 | 166 | 104.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:38 | 160 | 166 | 104.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SRIPL - ERIE E 69 230 | 160 | 166 | 104.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:GARD230_T7-12 | 160 | 166 | 104.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | FARMVLY - 5MILE 345 | 160 | 166 | 104.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:BETHSTM | 160 | 166 | 104.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:GARD230_R823 | 160 | 166 | 104.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | R:FV-5M_37&W-F_171 | 160 | 166 | 104.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | R:HC-SR_37&W-F_171 | 160 | 166 | 104.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_3 | 160 | 166 | 104.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:LAPER_345_4 | 160 | 166 | 104.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | LN:115:180 | 160 | 166 | 104.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:FRGT/WRFL | 160 | 166 | 104.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:130 | LN:115:192 | 160 | 166 | 104.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | SB:GARD230_T7-12 | 160 | 166 | 104.3
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:HUNT230_R1502 | 160 | 166 | 104.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:LAFA_ELB | 160 | 166 | 104.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:54/921 | 160 | 166 | 104.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | R:HC-FV_37&W-F_171 | 160 | 166 | 104.28
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | LN:115:182S | 160 | 166 | 104.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 104.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | S:PA_HNTL78 | 160 | 166 | 104.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_4 | 160 | 166 | 104.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:LAPER_345_3 | 160 | 166 | 104.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:GARD230_R823 | 160 | 166 | 104.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:HUNT230_NEW | 160 | 166 | 104.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lockport_907 | LN:115:182N | 160 | 166 | 104.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:LAPER_345_1 | 160 | 166 | 104.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:LAPER_345_2 | 160 | 166 | 104.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | SB:HUNT230_R1202 | 160 | 166 | 104.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | TB:2/1:ROB | 160 | 166 | 104.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:5MILE_B | 160 | 166 | 104.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN: IND PT 3 | 160 | 166 | 104.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:907 NY | LN:115:182N | 160 | 166 | 104.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 104.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | B:Hunt67 | 160 | 166 | 104.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:LAFA_ELB | 160 | 166 | 104.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B5 | 160 | 166 | 104.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | B:STOLE230 | 160 | 166 | 104.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 104.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:GARD230_T7-12 | 160 | 166 | 104.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:EDIC345_R400 | 160 | 166 | 104.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:255_345B202 | 160 | 166 | 104.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | SB:HUNT230_R1302 | 160 | 166 | 104.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:130 | 160 | 166 | 104.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | FARMVLY - HOMERCTY | 160 | 166 | 104.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 104.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:OAKD345_B6 | 160 | 166 | 104.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | SB:HUNT230_NEW | 160 | 166 | 104.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:LAFAYETT | 160 | 166 | 104.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:HCMB/NWES | 160 | 166 | 104.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1502 | 160 | 166 | 104.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:GV8 | SB:GARD230_T7-12 | 160 | 166 | 104.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SOMERSET - NEWROCH 1 345 | 160 | 166 | 104.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GARDENVILL 230/115 M8TR | SB:GARD230_T7-12 | 160 | 166 | 104.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:BUCHS_1 | 160 | 166 | 104.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:BUCHS_3 | 160 | 166 | 104.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:NIAG345_3108 | 160 | 166 | 104.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B5 | 160 | 166 | 104.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | FARMVLY - HOMERCTY | 160 | 166 | 104.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | NIAG - NEWROCH 1 345 | 160 | 166 | 104.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | R:HC-FV_37&W-F_171 | 160 | 166 | 104.17
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926B | LN:115:54/921 | 160 | 166 | 104.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:5MILE_B | 160 | 166 | 104.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 104.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:OAKD345_B6 | 160 | 166 | 104.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | S:PA_HNTL77 | 160 | 166 | 104.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B202 | 160 | 166 | 104.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | R:HC-FV_37&W-F_171 | 160 | 166 | 104.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | SB:HUNT230_R1202 | 160 | 166 | 104.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:706 NY | LN:115:54/921 | 160 | 166 | 104.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_706 | LN:115:54/921 | 160 | 166 | 104.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:GARD230_R833 | 160 | 166 | 104.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:HUNT230_NEW | 160 | 166 | 104.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:255_345B302 | 160 | 166 | 104.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:NIAG345_3108 | 160 | 166 | 104.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | NIAG - NEWROCH 1 345 | 160 | 166 | 104.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SOMERSET - NEWROCH 1 345 | 160 | 166 | 104.12
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | LN:115:182S | 160 | 166 | 104.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | MAINSBRG - HOMERCITY 30B 345 | 160 | 166 | 104.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | LN:115:182N | 160 | 166 | 104.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:255_345B302 | 160 | 166 | 104.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:255_345B202 | 160 | 166 | 104.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1302 | 160 | 166 | 104.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:HUNT230_R1402 | 160 | 166 | 104.08
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | R:HC-MB_30&W-F_171 | 160 | 166 | 104.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | B:Hunt67 | 160 | 166 | 104.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:903 NY | LN:115:54/921 | 160 | 166 | 104.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | B:Hunt67 | 160 | 166 | 104.08
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:78&79 | 160 | 166 | 104.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | T:61&191 | 160 | 166 | 104.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:HUNT230_R1502 | 160 | 166 | 104.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:129 | LN:115:191 | 160 | 166 | 104.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:130 | 160 | 166 | 104.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SOMERSET - NEWROCH 1 345 | 160 | 166 | 104.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:GARD230_R823 | 160 | 166 | 104.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:195 | 160 | 166 | 104.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | LN:115:182N | 160 | 166 | 104.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:LAPER_345_2 | 160 | 166 | 104.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:LAPER_345_1 | 160 | 166 | 104.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | WTHRS - MEYER 230 | 160 | 166 | 104.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 104.05
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:67&68&BW | 160 | 166 | 104.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 104.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:39 | 160 | 166 | 104.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | B:Hunt67 | 160 | 166 | 104.04
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | STONYCR - WTHRS 230 | 160 | 166 | 104.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HCWC/NWES | 160 | 166 | 104.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:MBWC/NWES | 160 | 166 | 104.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:180 | 160 | 166 | 104.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 104.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | S:PA_HNTL78 | 160 | 166 | 104.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 104.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:GARD230_R833 | 160 | 166 | 104.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | WTHRS - MEYER 230 | 160 | 166 | 104.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | LN:115:195 | 160 | 166 | 104.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | LN:115:180 | 160 | 166 | 104.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | LN:115:180 | 160 | 166 | 104.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:345:37S-FM-FV-HC | 160 | 166 | 104.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:LAFAYETT | 160 | 166 | 104.01
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1402 | 160 | 166 | 104
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:78&79 | 160 | 166 | 104
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:195 | 160 | 166 | 104
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:LAPER_345_1 | 160 | 166 | 104
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:LAPER_345_2 | 160 | 166 | 104
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | LN:115:182N | 160 | 166 | 103.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:HUNT230_R1302 | 160 | 166 | 103.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | LN:115:182N | 160 | 166 | 103.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:NIAG345_3108 | 160 | 166 | 103.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | NIAG - NEWROCH 1 345 | 160 | 166 | 103.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:39 | 160 | 166 | 103.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:WATRC345_30-3142 | 160 | 166 | 103.98
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | WTRCR - MAINSBRG 30A 345 | 160 | 166 | 103.98
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:WATRC345_B1-3042 | 160 | 166 | 103.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | FARMVLY - HOMERCTY | 160 | 166 | 103.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 103.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_42-4182 | 160 | 166 | 103.98
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:255_345B302 | 160 | 166 | 103.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 103.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | B:MEYER | 160 | 166 | 103.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | B:GARD72&79 | 160 | 166 | 103.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | TB:2/1:PK3 | 160 | 166 | 103.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:GARD230_R833 | 160 | 166 | 103.95
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:MEYER | 160 | 166 | 103.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | S:PA_HNTL77 | 160 | 166 | 103.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:191 | 160 | 166 | 103.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:LAFAYETT | 160 | 166 | 103.94
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:HUNT230_R1202 | 160 | 166 | 103.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:129 | LN:115:192 | 160 | 166 | 103.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:LAPER_345_4 | 160 | 166 | 103.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:LAPER_345_3 | 160 | 166 | 103.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:COOP345_42-4182 | 160 | 166 | 103.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | B:GARD72&79 | 160 | 166 | 103.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | FARMVLY - HOMERCTY | 160 | 166 | 103.93
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HC-WC_30&W-F_171 | 160 | 166 | 103.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | R:HC-FV_37&W-F_171 | 160 | 166 | 103.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:31&41 | 160 | 166 | 103.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:LAFA_ELB | 160 | 166 | 103.9
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:HUNT230_R1402 | 160 | 166 | 103.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | LN:115:195 | 160 | 166 | 103.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | LN:115:195 | 160 | 166 | 103.89
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:78&79 | 160 | 166 | 103.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 103.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:31&41 | 160 | 166 | 103.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 103.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | S:HNT_GRD80 | 160 | 166 | 103.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | B:Hunt67 | 160 | 166 | 103.87
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SIN:120_130 | 160 | 166 | 103.86
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SIN:130 | 160 | 166 | 103.86
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:W97&W98 | 160 | 166 | 103.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | TB:2/1:PK3 | 160 | 166 | 103.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:5MILE_B | 160 | 166 | 103.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 103.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | S:PA_HNTL78 | 160 | 166 | 103.85
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | B:Hunt67 | 160 | 166 | 103.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:OAKD345_B5 | 160 | 166 | 103.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | B:GARD72&79 | 160 | 166 | 103.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:5MILE_B | 160 | 166 | 103.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 103.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:OAKD345_B6 | 160 | 166 | 103.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 103.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | Base Case | 160 | 166 | 103.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1202 | 160 | 166 | 103.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | S:HNT_GRD80 | 160 | 166 | 103.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:54/921 | 160 | 166 | 103.82
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:OSWE_R955 | 160 | 166 | 103.81
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:OSWEGO 5 | 160 | 166 | 103.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | S:PA_HNTL77 | 160 | 166 | 103.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 103.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:54/921 | 160 | 166 | 103.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 103.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:192 | 160 | 166 | 103.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:NIAG345_3108 | 160 | 166 | 103.8
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-WC_30&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 166 | 103.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | B:GARD72&79 | 160 | 166 | 103.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3430 | 160 | 166 | 103.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | R:HC-FV_37&W-F_171 | 160 | 166 | 103.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:38 | 160 | 166 | 103.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | SB:HUNT230_R1302 | 160 | 166 | 103.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | SB:HUNT230_R1302 | 160 | 166 | 103.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:129 | 160 | 166 | 103.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | SB:GARD230_T7-12 | 160 | 166 | 103.77
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | LN:115:182N | 160 | 166 | 103.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | NIAG - NEWROCH 1 345 | 160 | 166 | 103.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:LAPER_345_3 | 160 | 166 | 103.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:LAPER_345_4 | 160 | 166 | 103.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:38 | 160 | 166 | 103.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | FARMVLY - HOMERCTY | 160 | 166 | 103.75
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:OSWE_R965 | 160 | 166 | 103.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | T:40&41 | 160 | 166 | 103.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&80 | 160 | 166 | 103.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:903 NY | 160 | 166 | 103.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | TB:2/1:PK3 | 160 | 166 | 103.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | TB:2/1:PK3 | 160 | 166 | 103.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 103.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_R873 | 160 | 166 | 103.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | T:40&41 | 160 | 166 | 103.73
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | B:Hunt67 | 160 | 166 | 103.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:255_345B302 | 160 | 166 | 103.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HILLSIDE 230/115 4TR | SB:GARD230_T7-12 | 160 | 166 | 103.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:706 NY | 160 | 166 | 103.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | First:Lancaster_706 | 160 | 166 | 103.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:LAFA_ELB | 160 | 166 | 103.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 103.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | S:PA_HNTL78 | 160 | 166 | 103.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | R:HC-FV_37&W-F_171 | 160 | 166 | 103.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:COOP345_42-4182 | 160 | 166 | 103.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | B:Hunt67 | 160 | 166 | 103.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_R823 | 160 | 166 | 103.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:GARD230_R873 | 160 | 166 | 103.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:OAKD345_B5 | 160 | 166 | 103.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | Base Case | 160 | 166 | 103.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | SB:GARD230_T7-12 | 160 | 166 | 103.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | SB:HUNT230_R1202 | 160 | 166 | 103.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | SB:HUNT230_R1202 | 160 | 166 | 103.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:101 | 160 | 166 | 103.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R915 | 160 | 166 | 103.67
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:GARD230_R833 | 160 | 166 | 103.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:180 | 160 | 166 | 103.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:LOCKPORT | 160 | 166 | 103.65
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | B:Hunt68 | 160 | 166 | 103.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 103.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:OAKD345_B6 | 160 | 166 | 103.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 103.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 160 | 166 | 103.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:GARD230_R873 | 160 | 166 | 103.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | S:HNT_GRD80 | 160 | 166 | 103.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | MEYER - CANDQUA 60 230 | SB:GARD230_T7-12 | 160 | 166 | 103.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:PA230_R3430 | 160 | 166 | 103.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:GARD230_R823 | 160 | 166 | 103.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | First:Lancaster_926A | 160 | 166 | 103.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:EESR/WF/NWES | 160 | 166 | 103.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | LN:115:195 | 160 | 166 | 103.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:31&41 | 160 | 166 | 103.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:100 | 160 | 166 | 103.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:129 | 160 | 166 | 103.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:345:37S-FM-FV-HC | 160 | 166 | 103.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R915 | 160 | 166 | 103.62
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926A | LN:115:182N | 160 | 166 | 103.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:255_345B202 | 160 | 166 | 103.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | B:Hunt67 | 160 | 166 | 103.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:GARD230_T7-12 | 160 | 166 | 103.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | B:Hunt67 | 160 | 166 | 103.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | B:Hunt67 | 160 | 166 | 103.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:DKSR/WRFL | 160 | 166 | 103.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:705 NY | 160 | 166 | 103.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | First:Lancaster_705 | 160 | 166 | 103.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | SB:GARD230_T7-12 | 160 | 166 | 103.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | SB:GARD230_T7-12 | 160 | 166 | 103.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:LAFA_ELB | 160 | 166 | 103.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:MP11&41 | 160 | 166 | 103.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | S:HNT_GRD80 | 160 | 166 | 103.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | SB:GARD230_T7-12 | 160 | 166 | 103.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:LAPER_345_4 | 160 | 166 | 103.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:LAPER_345_3 | 160 | 166 | 103.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:COOP345_4182 | 160 | 166 | 103.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3208 | 160 | 166 | 103.59
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV1 | LN:115:182S | 160 | 166 | 103.58
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV2 | LN:115:182S | 160 | 166 | 103.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SOMERSET - NEWROCH 1 345 | 160 | 166 | 103.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | S:PA_HNTL77 | 160 | 166 | 103.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | TB:2/1:PK3 | 160 | 166 | 103.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:GARD230_R873 | 160 | 166 | 103.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | FARMVLY - HOMERCTY | 160 | 166 | 103.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | LN:115:54/921 | 160 | 166 | 103.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | SB:HUNT230_R1302 | 160 | 166 | 103.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | SB:HUNT230_R1302 | 160 | 166 | 103.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:MARC345_3202 | 160 | 166 | 103.57
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:FRGT/WRFL | 160 | 166 | 103.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | S:PA_HNTL78 | 160 | 166 | 103.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 103.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 103.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:MP11&41 | 160 | 166 | 103.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 103.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | S:PA_HNTL78 | 160 | 166 | 103.55
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:EESR/WRFL | 160 | 166 | 103.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:61&191 | 160 | 166 | 103.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 103.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:COOP345_4182 | 160 | 166 | 103.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3208 | 160 | 166 | 103.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | MARCY - COOPERS 345 SC | 160 | 166 | 103.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:GARD230_R873 | 160 | 166 | 103.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | SB:HUNT230_R1302 | 160 | 166 | 103.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | SB:GARD230_T7-12 | 160 | 166 | 103.53
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | LN:115:182S | 160 | 166 | 103.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:COOP345_42-4182 | 160 | 166 | 103.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | SB:GARD230_T7-12 | 160 | 166 | 103.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | SB:GARD230_T7-12 | 160 | 166 | 103.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:MARC345_3202 | 160 | 166 | 103.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 103.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | S:PA_HNTL77 | 160 | 166 | 103.52
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HCMB/NWES | 160 | 166 | 103.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:GARD230_T7-12 | 160 | 166 | 103.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTRCR - MAINSBRG 30A 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 103.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCWC/NWES | DCT:230:79+80+ELM1-2 | 160 | 166 | 103.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:MBWC/NWES | DCT:230:79+80+ELM1-2 | 160 | 166 | 103.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | R:HC-FV_37&W-F_171 | 160 | 166 | 103.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | Base Case | 160 | 166 | 103.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | S:PA_HNTL77 | 160 | 166 | 103.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | LN:115:102 | 160 | 166 | 103.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | LN:115:101 | 160 | 166 | 103.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 103.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 160 | 166 | 103.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 103.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:77&76 | 160 | 166 | 103.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:9MIPT1 | 160 | 166 | 103.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | SB:HUNT230_R1302 | 160 | 166 | 103.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 103.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | MARCY - COOPERS 345 SC | 160 | 166 | 103.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | R:HC-SR_37&W-F_171 | 160 | 166 | 103.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | R:FV-5M_37&W-F_171 | 160 | 166 | 103.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:OAKD345_B5 | 160 | 166 | 103.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | First:Lancaster_705 | 160 | 166 | 103.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:705 NY | 160 | 166 | 103.48
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:WTHERS230 | 160 | 166 | 103.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | First:Lancaster_705 | 160 | 166 | 103.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:705 NY | 160 | 166 | 103.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:255_345B202 | 160 | 166 | 103.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | B:GARD73&80 | 160 | 166 | 103.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SHLDON - STONYCR 230 | SB:GARD230_T7-12 | 160 | 166 | 103.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | SB:HUNT230_R1302 | 160 | 166 | 103.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | SB:HUNT230_R1202 | 160 | 166 | 103.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | SB:HUNT230_R1202 | 160 | 166 | 103.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:OAKD345_B6 | 160 | 166 | 103.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 103.46
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:OSWE_R925 | 160 | 166 | 103.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:31&41 | 160 | 166 | 103.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 103.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:102 | 160 | 166 | 103.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:77&76 | 160 | 166 | 103.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | SB:HUNT230_R1202 | 160 | 166 | 103.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | B:STOLE230 | 160 | 166 | 103.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:39 | 160 | 166 | 103.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:38 | 160 | 166 | 103.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:GARD230_R833 | 160 | 166 | 103.44
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:OSWEGO 6 | 160 | 166 | 103.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SOMERSET - NEWROCH 1 345 | 160 | 166 | 103.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:345:37S-FM-FV-HC | 160 | 166 | 103.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | R:FV-5M_37&W-F_171 | 160 | 166 | 103.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | R:HC-SR_37&W-F_171 | 160 | 166 | 103.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:705 NY | 160 | 166 | 103.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | First:Lancaster_705 | 160 | 166 | 103.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | B:GARD73&80 | 160 | 166 | 103.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | LN:115:54/921 | 160 | 166 | 103.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | MAINSBRG - HOMERCITY 30B 345 | 160 | 166 | 103.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:191 | 160 | 166 | 103.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:GARD230_R833 | 160 | 166 | 103.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | T:41&33 | 160 | 166 | 103.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3430 | 160 | 166 | 103.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:39 | 160 | 166 | 103.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:345:37S-FM-FV-HC | 160 | 166 | 103.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:GARD230_R823 | 160 | 166 | 103.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | T:41&33 | 160 | 166 | 103.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 103.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - HOMERCTY | 160 | 166 | 103.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | S:PA_HNTL77 | 160 | 166 | 103.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | SB:HUNT230_R1202 | 160 | 166 | 103.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | FARMVLY - 5MILE 345 | 160 | 166 | 103.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 103.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:5MILE_B | 160 | 166 | 103.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | S:PA_HNTL78 | 160 | 166 | 103.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | HUNTLEY - PACKARD 78 230 | 160 | 166 | 103.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:OSWE_R935 | 160 | 166 | 103.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | R:HC-FV_37&W-F_171 | 160 | 166 | 103.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | SB:HUNT230_R1302 | 160 | 166 | 103.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 103.36
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HC-MB_30&W-F_171 | 160 | 166 | 103.36
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:191 | 160 | 166 | 103.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:EDIC345_R915 | 160 | 166 | 103.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | LN:115:195 | 160 | 166 | 103.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | FARMVLY - 5MILE 345 | 160 | 166 | 103.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | FARMVLY - HOMERCTY | 160 | 166 | 103.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:255_345B202 | 160 | 166 | 103.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:MP11&41 | 160 | 166 | 103.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | HUNTLEY - PACKARD 77 230 | 160 | 166 | 103.33
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:77&80 | 160 | 166 | 103.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | B:STOLE230 | 160 | 166 | 103.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:MARC345_3208 | 160 | 166 | 103.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:COOP345_4182 | 160 | 166 | 103.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:HUNT230_R1302 | 160 | 166 | 103.31
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | R:HC-FV_37&W-F_171 | 160 | 166 | 103.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | TB:2/1:PK3 | 160 | 166 | 103.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | SB:HUNT230_R1202 | 160 | 166 | 103.31
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | TB:2/1:ROB | 160 | 166 | 103.3
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:192 | 160 | 166 | 103.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:101 | 160 | 166 | 103.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | B:GARD73&80 | 160 | 166 | 103.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:345:37S-FM-FV | 160 | 166 | 103.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:5MILE | 160 | 166 | 103.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SOMERSET - NEWROCH 1 345 | 160 | 166 | 103.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:MARC345_3202 | 160 | 166 | 103.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | SB:HUNT230_R1202 | 160 | 166 | 103.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | S:PA_HNTL78 | 160 | 166 | 103.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 103.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | B:GARD73&80 | 160 | 166 | 103.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:120 | 160 | 166 | 103.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:345:37S-FM-FV | 160 | 166 | 103.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:5MILE | 160 | 166 | 103.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | MARCY - COOPERS 345 SC | 160 | 166 | 103.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:30&40 | 160 | 166 | 103.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | First:Lancaster_926B | 160 | 166 | 103.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 103.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | LN:115:195 | 160 | 166 | 103.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R935 | 160 | 166 | 103.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:MLS3&OMS | 160 | 166 | 103.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SIN:250 | 160 | 166 | 103.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:MILLST3 | 160 | 166 | 103.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:FITZPATR | 160 | 166 | 103.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:HUNT230_R1202 | 160 | 166 | 103.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:192 | 160 | 166 | 103.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 103.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:77&76 | 160 | 166 | 103.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | LN:115:195 | 160 | 166 | 103.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | T:68&160 | 160 | 166 | 103.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-WC_30&W-F_171 | T:79&80 | 160 | 166 | 103.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:5MILE_B | 160 | 166 | 103.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:345:37S-FM-FV | 160 | 166 | 103.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:5MILE | 160 | 166 | 103.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:LAPER_345_1 | 160 | 166 | 103.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:LAPER_345_2 | 160 | 166 | 103.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:101 | 160 | 166 | 103.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:30&40 | 160 | 166 | 103.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R935 | 160 | 166 | 103.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:HUNT230_R1302 | 160 | 166 | 103.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:EDIC345_R915 | 160 | 166 | 103.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 103.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | B:STOLE230 | 160 | 166 | 103.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:ROBI230 | 160 | 166 | 103.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | B:GARD73&80 | 160 | 166 | 103.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 103.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | TB:2/1:PK3 | 160 | 166 | 103.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | TB:2/1:PK3 | 160 | 166 | 103.17
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:3/2:FV | LN:115:182S | 160 | 166 | 103.16
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | B:Hunt68 | 160 | 166 | 103.16
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | LN:115:182S | 160 | 166 | 103.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | FARMVLY - HOMERCTY | 160 | 166 | 103.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:GARD230_R833 | 160 | 166 | 103.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:LAFAYETT | 160 | 166 | 103.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:MP11&41 | 160 | 166 | 103.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | B:GARD72&79 | 160 | 166 | 103.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:255_345B202 | 160 | 166 | 103.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&80 | 160 | 166 | 103.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:COOP345_4182 | 160 | 166 | 103.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:MARC345_3208 | 160 | 166 | 103.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:102 | 160 | 166 | 103.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:HUNT230_R1202 | 160 | 166 | 103.12
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | S:PA_HNTL77 | 160 | 166 | 103.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:MARC345_3202 | 160 | 166 | 103.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | R:HC-FV_37&W-F_171 | 160 | 166 | 103.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | LN:115:195 | 160 | 166 | 103.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:706 NY | FARMVLY - HOMERCTY | 160 | 166 | 103.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_706 | FARMVLY - HOMERCTY | 160 | 166 | 103.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:40&41 | 160 | 166 | 103.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | Base Case | 160 | 166 | 103.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | S:HNT_GRD80 | 160 | 166 | 103.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | B:STOLE230 | 160 | 166 | 103.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:ROBI230 | 160 | 166 | 103.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SOMERSET - NEWROCH 1 345 | 160 | 166 | 103.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:EDIC345_R400 | 160 | 166 | 103.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | B:Hunt68 | 160 | 166 | 103.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | MARCY - COOPERS 345 SC | 160 | 166 | 103.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:77&76 | 160 | 166 | 103.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:39 | 160 | 166 | 103.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | LN:115:191 | 160 | 166 | 103.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | TB:2/1:PK3 | 160 | 166 | 103.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:102 | 160 | 166 | 103.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:GARD230_R823 | 160 | 166 | 103.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | LN:115:182N | 160 | 166 | 103.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:LAPER_345_2 | 160 | 166 | 103.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:LAPER_345_1 | 160 | 166 | 103.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_GRDN_GRDN_230 | B:STOLE230 | 160 | 166 | 103.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:EDIC345_R400 | 160 | 166 | 103.05
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:OSWE_R955 | 160 | 166 | 103.04
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:OSWEGO 5 | 160 | 166 | 103.04
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:908 NY | 160 | 166 | 103.04
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | B:Hunt68 | 160 | 166 | 103.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 103.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:706 NY | R:HC-FV_37&W-F_171 | 160 | 166 | 103.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_706 | R:HC-FV_37&W-F_171 | 160 | 166 | 103.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | TB:2/1:PK3 | 160 | 166 | 103.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 103.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | LN:115:195 | 160 | 166 | 103.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 103.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:40&41 | 160 | 166 | 103.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:COOP345_42-4182 | 160 | 166 | 103.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 103.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | S:PA_HNTL78 | 160 | 166 | 103.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | B:STOLE230 | 160 | 166 | 103.01
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3430 | 160 | 166 | 103
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:LAFAYETT | 160 | 166 | 103
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | B:STOLE230 | 160 | 166 | 103
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:31&41 | 160 | 166 | 103
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:77&80 | 160 | 166 | 102.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | FARMVLY - HOMERCTY | 160 | 166 | 102.99
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_NEW | 160 | 166 | 102.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | LN:115:120 | 160 | 166 | 102.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | B:STOLE230 | 160 | 166 | 102.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | T:30&40 | 160 | 166 | 102.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:101 | 160 | 166 | 102.98
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 102.97
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3430 | 160 | 166 | 102.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:EDIC345_R935 | 160 | 166 | 102.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | S:PA_HNTL77 | 160 | 166 | 102.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | S:PA_HNTL77 | 160 | 166 | 102.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:41&33 | 160 | 166 | 102.97
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:OSWE_R965 | 160 | 166 | 102.96
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCWC/NWES | T:79&80 | 160 | 166 | 102.95
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:MBWC/NWES | T:79&80 | 160 | 166 | 102.95
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1502 | 160 | 166 | 102.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | Base Case | 160 | 166 | 102.95
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTRCR - MAINSBRG 30A 345 | T:79&80 | 160 | 166 | 102.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:120 | 160 | 166 | 102.94
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | R:HC-FV_37&W-F_171 | 160 | 166 | 102.93
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:908 NY | LN:115:182S | 160 | 166 | 102.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | LN:115:191 | 160 | 166 | 102.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | LN:115:191 | 160 | 166 | 102.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | LN:115:192 | 160 | 166 | 102.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R3430 | 160 | 166 | 102.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | LN:115:54/921 | 160 | 166 | 102.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:LAPER_345_4 | 160 | 166 | 102.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:LAPER_345_3 | 160 | 166 | 102.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | S:PA_HNTL77 | 160 | 166 | 102.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | S:PA_HNTL77 | 160 | 166 | 102.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | FARMVLY - HOMERCTY | 160 | 166 | 102.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:LAFA_ELB | 160 | 166 | 102.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | LN:115:54/921 | 160 | 166 | 102.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 102.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CANDQUA - STNYRDG 68A 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 102.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | T:30&40 | 160 | 166 | 102.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:EDIC345_R935 | 160 | 166 | 102.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:38 | 160 | 166 | 102.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 102.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | S:PA_HNTL78 | 160 | 166 | 102.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 102.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | S:PA_HNTL78 | 160 | 166 | 102.81
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:HUNT230_NEW | 160 | 166 | 102.8
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:GARD230_T7-12 | 160 | 166 | 102.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:OAKD345_B5 | 160 | 166 | 102.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:38 | 160 | 166 | 102.8
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:SEAB&OMS | 160 | 166 | 102.79
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:SEABROOK | 160 | 166 | 102.79
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:GARD230_T7-12 | 160 | 166 | 102.79
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1402 | 160 | 166 | 102.79
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:78&79 | 160 | 166 | 102.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 102.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:OAKD345_B6 | 160 | 166 | 102.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 102.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | S:PA_HNTL78 | 160 | 166 | 102.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | HUNTLEY - PACKARD 78 230 | 160 | 166 | 102.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | S:PA_HNTL78 | 160 | 166 | 102.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 102.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:EDIC345_R915 | 160 | 166 | 102.79
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_T7-12 | 160 | 166 | 102.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | LN:115:101 | 160 | 166 | 102.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 102.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:41&33 | 160 | 166 | 102.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:GARD230_R833 | 160 | 166 | 102.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | S:PA_HNTL77 | 160 | 166 | 102.77
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:LOCKPORT | 160 | 166 | 102.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:101 | 160 | 166 | 102.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | LN:115:192 | 160 | 166 | 102.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | LN:115:192 | 160 | 166 | 102.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | R:HC-FV_37&W-F_171 | 160 | 166 | 102.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 102.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 102.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:102 | 160 | 166 | 102.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | B:STOLE345 | 160 | 166 | 102.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | HOMERCTY - STOLLRD 37 345 | 160 | 166 | 102.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | First:Lancaster_STOL_HOMER_345 | 160 | 166 | 102.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | 5 MILE - STOLLE 37A 345 | 160 | 166 | 102.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | HUNTLEY - PACKARD 77 230 | 160 | 166 | 102.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 102.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | B:GARD72&79 | 160 | 166 | 102.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | FARMVLY - HOMERCTY | 160 | 166 | 102.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | T:77&80 | 160 | 166 | 102.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:LAPER_345_4 | 160 | 166 | 102.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:LAPER_345_3 | 160 | 166 | 102.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | T:34&42 | 160 | 166 | 102.73
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | TB:3/2:FV | 160 | 166 | 102.72
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | FARMVLY - FARMVLY | 160 | 166 | 102.72
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:GARD230_T7-12 | 160 | 166 | 102.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | LN:115:120 | 160 | 166 | 102.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:LAFA_ELB | 160 | 166 | 102.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | T:34&42 | 160 | 166 | 102.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:LAPER_345_1 | 160 | 166 | 102.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:LAPER_345_2 | 160 | 166 | 102.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | S:HNT_GRD80 | 160 | 166 | 102.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:9MIPT1 | 160 | 166 | 102.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | S:PA_HNTL77 | 160 | 166 | 102.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | R:5M-SR_37&W-F_171 | 160 | 166 | 102.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 102.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | LN:115:54/921 | 160 | 166 | 102.69
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_NEW | 160 | 166 | 102.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | LN:115:191 | 160 | 166 | 102.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | R:HC-FV_37&W-F_171 | 160 | 166 | 102.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | S:PA_HNTL77 | 160 | 166 | 102.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | B:GARD72&79 | 160 | 166 | 102.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | STONYCR - WTHRS 230 | 160 | 166 | 102.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 102.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | S:PA_HNTL78 | 160 | 166 | 102.67
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:OSWE_R925 | 160 | 166 | 102.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:GARD230_T7-12 | 160 | 166 | 102.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 160 | 166 | 102.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:LAFAYETT | 160 | 166 | 102.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:COOP345_42-4182 | 160 | 166 | 102.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:MP11&41 | 160 | 166 | 102.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:MARC345_3208 | 160 | 166 | 102.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:ROBI230 | 160 | 166 | 102.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:ROBI230 | 160 | 166 | 102.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 102.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:38 | 160 | 166 | 102.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:41&33 | 160 | 166 | 102.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:COOP345_4182 | 160 | 166 | 102.65
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV1 | LN:115:182N | 160 | 166 | 102.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV2 | LN:115:182N | 160 | 166 | 102.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:OSWEGO 6 | 160 | 166 | 102.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | LN:115:182N | 160 | 166 | 102.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:345:37S-FM-FV-HC | 160 | 166 | 102.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:OAKD345_B5 | 160 | 166 | 102.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 102.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:OAKD345_B6 | 160 | 166 | 102.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:MARC345_3202 | 160 | 166 | 102.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 102.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 102.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:GARD230_R873 | 160 | 166 | 102.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:54/921 | 160 | 166 | 102.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | First:Lancaster_GRDN_GRDN_230 | 160 | 166 | 102.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | S:PA_HNTL77 | 160 | 166 | 102.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 102.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | CANDQUA - STNYRDG 68A 230 | 160 | 166 | 102.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | S:AVOCA | 160 | 166 | 102.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:GARD230_T7-12 | 160 | 166 | 102.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:31&41 | 160 | 166 | 102.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:705 NY | 160 | 166 | 102.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | First:Lancaster_705 | 160 | 166 | 102.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 102.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | First:Lancaster_705 | 160 | 166 | 102.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:705 NY | 160 | 166 | 102.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | MARCY - COOPERS 345 SC | 160 | 166 | 102.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 102.6
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:100 | 160 | 166 | 102.59
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | B:Hunt67 | 160 | 166 | 102.59
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 160 | 166 | 102.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:705 NY | 160 | 166 | 102.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | First:Lancaster_705 | 160 | 166 | 102.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:120 | 160 | 166 | 102.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | FARMVLY - HOMERCTY | 160 | 166 | 102.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:NIAG345_3108 | 160 | 166 | 102.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | S:STOLLE345 | 160 | 166 | 102.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 102.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | S:PA_HNTL78 | 160 | 166 | 102.58
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:OSWE_R935 | 160 | 166 | 102.57
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:HUNT230_NEW | 160 | 166 | 102.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | NIAG - NEWROCH 1 345 | 160 | 166 | 102.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | S:HNT_GRD80 | 160 | 166 | 102.57
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:3/2:FV | LN:115:182N | 160 | 166 | 102.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | B:Hunt68 | 160 | 166 | 102.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | LN:115:182N | 160 | 166 | 102.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | LN:115:54/921 | 160 | 166 | 102.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | LN:115:54/921 | 160 | 166 | 102.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | LN:115:54/921 | 160 | 166 | 102.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | First:Lancaster_705 | 160 | 166 | 102.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:705 NY | 160 | 166 | 102.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 160 | 166 | 102.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:102 | 160 | 166 | 102.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | LN:115:54/921 | 160 | 166 | 102.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:STONYRIDGE | 160 | 166 | 102.55
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:HUNT230_R1502 | 160 | 166 | 102.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | R:HC-FV_37&W-F_171 | 160 | 166 | 102.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 102.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 102.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | R:HC-FV_37&W-F_171 | 160 | 166 | 102.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | FARMVLY - HOMERCTY | 160 | 166 | 102.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | R:HC-FV_37&W-F_171 | 160 | 166 | 102.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | LN:115:102 | 160 | 166 | 102.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | LN:115:54/921 | 160 | 166 | 102.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 102.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | T:61&64 | 160 | 166 | 102.53
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | WTHRS - MEYER 230 | 160 | 166 | 102.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | LN:115:192 | 160 | 166 | 102.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:255_345B302 | 160 | 166 | 102.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 102.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | T:61&64 | 160 | 166 | 102.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:GARD230_R823 | 160 | 166 | 102.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | HUNTLEY - PACKARD 78 230 | 160 | 166 | 102.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | S:PA_HNTL78 | 160 | 166 | 102.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:COOP345_42-4182 | 160 | 166 | 102.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | LN:115:120 | 160 | 166 | 102.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:345:37S-FM-FV-HC | 160 | 166 | 102.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3430 | 160 | 166 | 102.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:77&76 | 160 | 166 | 102.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:GARD230_R873 | 160 | 166 | 102.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | FARMVLY - HOMERCTY | 160 | 166 | 102.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | HUNTLEY - PACKARD 78 230 | 160 | 166 | 102.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | S:PA_HNTL78 | 160 | 166 | 102.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | HUNTLEY - PACKARD 77 230 | 160 | 166 | 102.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 102.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:41&33 | 160 | 166 | 102.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:39 | 160 | 166 | 102.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 102.46
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | S:PA_HNTL77 | 160 | 166 | 102.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:31&41 | 160 | 166 | 102.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | First:Lancaster_705 | 160 | 166 | 102.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:705 NY | 160 | 166 | 102.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | R:FV-5M_37&W-F_171 | 160 | 166 | 102.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | R:HC-SR_37&W-F_171 | 160 | 166 | 102.44
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:FITZPATR | 160 | 166 | 102.43
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:MEYER | 160 | 166 | 102.43
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | T:77&80 | 160 | 166 | 102.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:LAPER_345_3 | 160 | 166 | 102.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:LAPER_345_4 | 160 | 166 | 102.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | HUNTLEY - PACKARD 77 230 | 160 | 166 | 102.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | B:STOLE230 | 160 | 166 | 102.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | B:STOLE230 | 160 | 166 | 102.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:39 | 160 | 166 | 102.43
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:MLS3&OMS | 160 | 166 | 102.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:MILLST3 | 160 | 166 | 102.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SIN:250 | 160 | 166 | 102.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1502 | 160 | 166 | 102.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | B:STOLE230 | 160 | 166 | 102.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | B:Hunt67 | 160 | 166 | 102.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | LN:115:54/921 | 160 | 166 | 102.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | LN:115:54/921 | 160 | 166 | 102.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | B:Hunt67 | 160 | 166 | 102.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 102.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | First:Lancaster_GRDN_GRDN_230 | 160 | 166 | 102.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:HUNT230_R1402 | 160 | 166 | 102.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:78&79 | 160 | 166 | 102.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | LN:115:182N | 160 | 166 | 102.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | FARMVLY - FARMVLY | 160 | 166 | 102.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | TB:3/2:FV | 160 | 166 | 102.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:30&40 | 160 | 166 | 102.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | LN:115:191 | 160 | 166 | 102.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:195 | 160 | 166 | 102.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:120 | 160 | 166 | 102.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:GARD230_R823 | 160 | 166 | 102.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | B:STOLE230 | 160 | 166 | 102.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | B:STOLE230 | 160 | 166 | 102.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | S:PA_HNTL78 | 160 | 166 | 102.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 102.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:54/921 | 160 | 166 | 102.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:OAKD345_B5 | 160 | 166 | 102.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | S:PA_HNTL77 | 160 | 166 | 102.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:OAKD345_B6 | 160 | 166 | 102.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 102.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 102.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:EDIC345_R915 | 160 | 166 | 102.33
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:54/921 | 160 | 166 | 102.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:COOP345_42-4182 | 160 | 166 | 102.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:MP11&41 | 160 | 166 | 102.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:MARC345_3208 | 160 | 166 | 102.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:39 | 160 | 166 | 102.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:EDIC345_R935 | 160 | 166 | 102.3
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 102.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:COOP345_4182 | 160 | 166 | 102.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:COOP345_42-4182 | 160 | 166 | 102.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:KINT_39-B112 | 160 | 166 | 102.28
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:PA230_R3430 | 160 | 166 | 102.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | B:Hunt67 | 160 | 166 | 102.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:LAFA_ELB | 160 | 166 | 102.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:MARC345_3202 | 160 | 166 | 102.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:54/921 | 160 | 166 | 102.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:101 | 160 | 166 | 102.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:KINT_B1-3812 | 160 | 166 | 102.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1402 | 160 | 166 | 102.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:78&79 | 160 | 166 | 102.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:101 | 160 | 166 | 102.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:MARC_765_7402 | 160 | 166 | 102.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:MSU1_7202>7214>7208>7214 | 160 | 166 | 102.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | HQ-NY 765 | 160 | 166 | 102.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | B:Hunt68 | 160 | 166 | 102.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | MARCY - COOPERS 345 SC | 160 | 166 | 102.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:903 NY | FARMVLY - HOMERCTY | 160 | 166 | 102.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:34&42 | 160 | 166 | 102.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | B:GARD73&80 | 160 | 166 | 102.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | LN:115:191 | 160 | 166 | 102.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 102.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | S:PA_HNTL78 | 160 | 166 | 102.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:31&41 | 160 | 166 | 102.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_GRDN_GRDN_230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 102.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:61&64 | 160 | 166 | 102.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | FARMVLY - 5MILE 345 | 160 | 166 | 102.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | B:STOLE230 | 160 | 166 | 102.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | FARMVLY - HOMERCTY | 160 | 166 | 102.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 102.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:77&76 | 160 | 166 | 102.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:GARD230_R833 | 160 | 166 | 102.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | LN:115:192 | 160 | 166 | 102.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1502 | 160 | 166 | 102.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:903 NY | R:HC-FV_37&W-F_171 | 160 | 166 | 102.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | B:STOLE230 | 160 | 166 | 102.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:EDIC345_R400 | 160 | 166 | 102.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1202 | 160 | 166 | 102.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 102.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | B:GARD72&79 | 160 | 166 | 102.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 102.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:67&37A | 160 | 166 | 102.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:PA230_R3430 | 160 | 166 | 102.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:EDIC345_R915 | 160 | 166 | 102.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 102.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:WTHERS230 | 160 | 166 | 102.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | B:GARD73&80 | 160 | 166 | 102.16
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:926 NY | LN:115:54/921 | 160 | 166 | 102.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | R:HC-FV_37&W-F_171 | 160 | 166 | 102.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:MP11&41 | 160 | 166 | 102.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:MARC345_3208 | 160 | 166 | 102.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:61&64 | 160 | 166 | 102.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:40&41 | 160 | 166 | 102.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:31&41 | 160 | 166 | 102.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:5MILE | 160 | 166 | 102.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:345:37S-FM-FV | 160 | 166 | 102.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:COOP345_4182 | 160 | 166 | 102.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 102.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:34&42 | 160 | 166 | 102.12
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | B:STOLE230 | 160 | 166 | 102.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | FARMVLY - 5MILE 345 | 160 | 166 | 102.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:MARC345_3202 | 160 | 166 | 102.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | B:STOLE230 | 160 | 166 | 102.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1402 | 160 | 166 | 102.08
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | B:STOLE230 | 160 | 166 | 102.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | MARCY - COOPERS 345 SC | 160 | 166 | 102.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:LAPER_345_1 | 160 | 166 | 102.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:LAPER_345_2 | 160 | 166 | 102.08
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:78&79 | 160 | 166 | 102.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | S:HNT_GRD80 | 160 | 166 | 102.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | LN:115:192 | 160 | 166 | 102.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 102.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:77&76 | 160 | 166 | 102.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | Base Case | 160 | 166 | 102.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:LAFAYETT | 160 | 166 | 102.05
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | FARMVLY - HOMERCTY | 160 | 166 | 102.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | Base Case | 160 | 166 | 102.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:GARD230_R833 | 160 | 166 | 102.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 102.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 102.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&76 | 160 | 166 | 102.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:102 | 160 | 166 | 102.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:102 | 160 | 166 | 102.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:ROBI230 | 160 | 166 | 102.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | B:STOLE230 | 160 | 166 | 102.01
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | R:HC-FV_37&W-F_171 | 160 | 166 | 102.01
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SANDY_DC&OMS | 160 | 166 | 102
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SANDY_DC | 160 | 166 | 102
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:GARD230_R873 | 160 | 166 | 102
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | R:FV-5M_37&W-F_171 | 160 | 166 | 101.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | R:HC-SR_37&W-F_171 | 160 | 166 | 101.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:255_345B202 | 160 | 166 | 101.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | T:30&40 | 160 | 166 | 101.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | B:STOLE230 | 160 | 166 | 101.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:LAPER_345_3 | 160 | 166 | 101.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:LAPER_345_4 | 160 | 166 | 101.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 101.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SOMERSET - NEWROCH 1 345 | 160 | 166 | 101.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:34&42 | 160 | 166 | 101.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 101.96
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:SEAB&OMS | 160 | 166 | 101.95
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:SEABROOK | 160 | 166 | 101.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:PA230_R3430 | 160 | 166 | 101.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | ROBINSON - STOLLRD 65 230 | 160 | 166 | 101.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 101.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | LN:115:54/921 | 160 | 166 | 101.94
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:908 NY | 160 | 166 | 101.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | SB:EDIC345_R935 | 160 | 166 | 101.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | ROBINSON - STOLLRD 65 230 | 160 | 166 | 101.93
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:OAKD345_B5 | 160 | 166 | 101.93
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1302 | 160 | 166 | 101.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:OAKD345_B6 | 160 | 166 | 101.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 101.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | B:Hunt68 | 160 | 166 | 101.91
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:HUNT230_R1302 | 160 | 166 | 101.9
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:705 NY | 160 | 166 | 101.9
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | First:Lancaster_705 | 160 | 166 | 101.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:EDIC345_R915 | 160 | 166 | 101.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | LN:115:54/921 | 160 | 166 | 101.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | LN:115:54/921 | 160 | 166 | 101.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | LN:115:54/921 | 160 | 166 | 101.89
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:HUNT230_R1202 | 160 | 166 | 101.87
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | TB:2/1:PK3 | 160 | 166 | 101.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:MP11&41 | 160 | 166 | 101.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:COOP345_4182 | 160 | 166 | 101.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:77&76 | 160 | 166 | 101.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:MARC345_3208 | 160 | 166 | 101.86
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-MB_30&W-F_171 | DCT:230:79+80+ELM1-2 | 160 | 166 | 101.85
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:MARC345_3202 | 160 | 166 | 101.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | T:40&41 | 160 | 166 | 101.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:COOP345_4182 | 160 | 166 | 101.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | B:Hunt68 | 160 | 166 | 101.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:101 | 160 | 166 | 101.82
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:195 | 160 | 166 | 101.81
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | TB:2/1:PK3 | 160 | 166 | 101.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | MARCY - COOPERS 345 SC | 160 | 166 | 101.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | T:30&40 | 160 | 166 | 101.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:120 | 160 | 166 | 101.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:MP11&41 | 160 | 166 | 101.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:101 | 160 | 166 | 101.81
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:GARD230_R823 | 160 | 166 | 101.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:61&64 | 160 | 166 | 101.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:120 | 160 | 166 | 101.8
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCMB/NWES | DCT:230:79+80+ELM1-2 | 160 | 166 | 101.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:MARC345_3202 | 160 | 166 | 101.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:MARC345_3208 | 160 | 166 | 101.78
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:MASS_765_7108 | 160 | 166 | 101.77
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | T:77&80 | 160 | 166 | 101.77
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | T:77&80 | 160 | 166 | 101.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | SB:EDIC345_R935 | 160 | 166 | 101.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | MARCY - COOPERS 345 SC | 160 | 166 | 101.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | DUNKIRK - SRIPL 68 230 | LN:115:54/921 | 160 | 166 | 101.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:PA230_R3430 | 160 | 166 | 101.76
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | T:77&80 | 160 | 166 | 101.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:GINNA | T:77&80 | 160 | 166 | 101.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:GARD230_R823 | 160 | 166 | 101.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:EDIC345_R915 | 160 | 166 | 101.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:MASS_765_7102 | 160 | 166 | 101.73
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1302 | 160 | 166 | 101.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | T:77&80 | 160 | 166 | 101.72
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:HUNT230_R1202 | 160 | 166 | 101.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:41&33 | 160 | 166 | 101.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R3430 | 160 | 166 | 101.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R3430 | 160 | 166 | 101.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SRIPL - ERIE E 69 230 | LN:115:54/921 | 160 | 166 | 101.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 101.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:908 NY | LN:115:182N | 160 | 166 | 101.69
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | B:GARD72&79 | 160 | 166 | 101.69
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:GARD230_T7-12 | 160 | 166 | 101.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | B:Hunt68 | 160 | 166 | 101.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | B:Hunt68 | 160 | 166 | 101.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | LN:115:54/921 | 160 | 166 | 101.68
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | First:Lancaster_705 | 160 | 166 | 101.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:705 NY | 160 | 166 | 101.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:5MILE_B | 160 | 166 | 101.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | B:Hunt68 | 160 | 166 | 101.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | T:77&80 | 160 | 166 | 101.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:5MILE_B | 160 | 166 | 101.65
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | B:GARD73&80 | 160 | 166 | 101.65
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:HUNT230_R1302 | 160 | 166 | 101.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:195 | 160 | 166 | 101.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:HUNT230_R1202 | 160 | 166 | 101.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | B:Hunt68 | 160 | 166 | 101.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HILLSIDE 230/115 4TR | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:191 | 160 | 166 | 101.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | T:41&33 | 160 | 166 | 101.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | T:40&41 | 160 | 166 | 101.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_GRDN_GRDN_230 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 101.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SHLDON - STONYCR 230 | 160 | 166 | 101.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | MEYER - CANDQUA 60 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 101.57
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | B:Hunt68 | 160 | 166 | 101.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | MAINSBRG - HOMERCITY 30B 345 | DCT:230:79+80+ELM1-2 | 160 | 166 | 101.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | S:HNT_GRD80 | 160 | 166 | 101.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:EDIC345_R935 | 160 | 166 | 101.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | ROBINSON - STOLLRD 65 230 | 160 | 166 | 101.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:LAFA_ELB | 160 | 166 | 101.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:102 | 160 | 166 | 101.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:EDIC345_R915 | 160 | 166 | 101.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:102 | 160 | 166 | 101.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | B:Hunt68 | 160 | 166 | 101.53
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | B:Hunt68 | 160 | 166 | 101.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:EDIC345_R935 | 160 | 166 | 101.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | NIAGARA - ROBINSON 64 345 | 160 | 166 | 101.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:GARD230_R873 | 160 | 166 | 101.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:67&37A | 160 | 166 | 101.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | FARMVLY - HOMERCTY | 160 | 166 | 101.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:PA230_R3430 | 160 | 166 | 101.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:GARD230_R823 | 160 | 166 | 101.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:192 | 160 | 166 | 101.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_NEW | 160 | 166 | 101.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:GARD230_R833 | 160 | 166 | 101.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | MEYER - CANDQUA 60 230 | 160 | 166 | 101.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | B:Hunt68 | 160 | 166 | 101.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | T:77&80 | 160 | 166 | 101.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:30&40 | 160 | 166 | 101.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 101.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | T:40&41 | 160 | 166 | 101.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 101.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ERIE E - 4 MILE 230 | LN:115:54/921 | 160 | 166 | 101.45
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | R:HC-FV_37&W-F_171 | 160 | 166 | 101.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 101.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:NIAG345_3108 | 160 | 166 | 101.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | NIAG - NEWROCH 1 345 | 160 | 166 | 101.43
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:GARD230_R833 | 160 | 166 | 101.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | Base Case | 160 | 166 | 101.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:34&42 | 160 | 166 | 101.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | T:77&80 | 160 | 166 | 101.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:HUNT230_NEW | 160 | 166 | 101.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 101.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | Base Case | 160 | 166 | 101.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | T:77&80 | 160 | 166 | 101.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | T:77&80 | 160 | 166 | 101.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | B:GARD72&79 | 160 | 166 | 101.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | T:69J&70K | 160 | 166 | 101.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:345:37S-FM-FV-HC | 160 | 166 | 101.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SHLDON - STONYCR 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:345:37S-FM-FV-HC | 160 | 166 | 101.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:KINT_39-B112 | 160 | 166 | 101.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MARC_765_7402 | 160 | 166 | 101.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MSU1_7202>7214>7208>7214 | 160 | 166 | 101.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | FARMVLY - HOMERCTY | 160 | 166 | 101.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | T:41&33 | 160 | 166 | 101.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 101.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 101.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:926 NY | 160 | 166 | 101.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | HQ-NY 765 | 160 | 166 | 101.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | SB:PA230_R304 | 160 | 166 | 101.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:KINT_B1-3812 | 160 | 166 | 101.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-MB_30&W-F_171 | T:79&80 | 160 | 166 | 101.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | T:40&41 | 160 | 166 | 101.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | T:40&41 | 160 | 166 | 101.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | SB:PA230_R3230 | 160 | 166 | 101.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | SB:HUNT230_R1502 | 160 | 166 | 101.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | B:Hunt68 | 160 | 166 | 101.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | R:HC-FV_37&W-F_171 | 160 | 166 | 101.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:180 | 160 | 166 | 101.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3430 | 160 | 166 | 101.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:120 | 160 | 166 | 101.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | S:HNT_GRD80 | 160 | 166 | 101.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | S:HNT_GRD80 | 160 | 166 | 101.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:GARD230_R823 | 160 | 166 | 101.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:120 | 160 | 166 | 101.31
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | S:HNT_GRD80 | 160 | 166 | 101.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:EDIC345_R400 | 160 | 166 | 101.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:101 | 160 | 166 | 101.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCMB/NWES | T:79&80 | 160 | 166 | 101.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:GARD230_R873 | 160 | 166 | 101.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:GINNA | SB:HUNT230_R1502 | 160 | 166 | 101.27
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | SB:HUNT230_R1502 | 160 | 166 | 101.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:EDIC345_R915 | 160 | 166 | 101.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | T:77&80 | 160 | 166 | 101.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | B:GARD72&79 | 160 | 166 | 101.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | T:73&74 | 160 | 166 | 101.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 101.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:LAPER_345_2 | 160 | 166 | 101.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:LAPER_345_1 | 160 | 166 | 101.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | B:Hunt67 | 160 | 166 | 101.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 101.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:NIAG345_3108 | 160 | 166 | 101.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:LAPER_345_1 | 160 | 166 | 101.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:LAPER_345_2 | 160 | 166 | 101.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:GARD230_R833 | 160 | 166 | 101.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | T:41&33 | 160 | 166 | 101.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 101.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:NIAG345_3108 | 160 | 166 | 101.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | B:STOLE230 | 160 | 166 | 101.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | NIAG - NEWROCH 1 345 | 160 | 166 | 101.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 101.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | B:Hunt68 | 160 | 166 | 101.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | SB:HUNT230_R1402 | 160 | 166 | 101.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | T:78&79 | 160 | 166 | 101.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1502 | 160 | 166 | 101.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:LAFAYETT | 160 | 166 | 101.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | NIAG - NEWROCH 1 345 | 160 | 166 | 101.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 101.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:LAFAYETT | 160 | 166 | 101.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | T:77&80 | 160 | 166 | 101.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 101.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | B:GARD72&79 | 160 | 166 | 101.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | T:41&33 | 160 | 166 | 101.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | T:41&33 | 160 | 166 | 101.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:38 | 160 | 166 | 101.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:LAPER_345_2 | 160 | 166 | 101.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:LAPER_345_1 | 160 | 166 | 101.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:255_345B302 | 160 | 166 | 101.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:180 | 160 | 166 | 101.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 101.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:255_345B302 | 160 | 166 | 101.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:101 | 160 | 166 | 101.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:180 | 160 | 166 | 101.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | B:GARD72&79 | 160 | 166 | 101.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:38 | 160 | 166 | 101.17
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 101.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:GARD230_R823 | 160 | 166 | 101.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:LAPER_345_2 | 160 | 166 | 101.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:LAPER_345_1 | 160 | 166 | 101.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:LAFAYETT | 160 | 166 | 101.16
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:115:GINNA | 160 | 166 | 101.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:926 NY | SB:HUNT230_R1502 | 160 | 166 | 101.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | SB:HUNT230_R1502 | 160 | 166 | 101.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | B:GARD73&80 | 160 | 166 | 101.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LFYTE - CLARKCRNS 36A 345 | 160 | 166 | 101.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:GINNA | 160 | 166 | 101.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 101.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:40&41 | 160 | 166 | 101.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | B:Hunt67 | 160 | 166 | 101.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:LAFAYETT | 160 | 166 | 101.13
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | B:GARD72&79 | 160 | 166 | 101.12
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.12
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SANDY_DC | 160 | 166 | 101.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SANDY_DC&OMS | 160 | 166 | 101.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1402 | 160 | 166 | 101.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 101.11
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | T:78&79 | 160 | 166 | 101.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:54/921 | 160 | 166 | 101.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | B:Hunt68 | 160 | 166 | 101.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | B:STOLE230 | 160 | 166 | 101.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:40&41 | 160 | 166 | 101.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | SB:PA230_R3430 | 160 | 166 | 101.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:61&64 | 160 | 166 | 101.09
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | B:Hunt68 | 160 | 166 | 101.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:GARD230_R823 | 160 | 166 | 101.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | B:Hunt68 | 160 | 166 | 101.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | S:HNT_GRD80 | 160 | 166 | 101.08
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | T:77&80 | 160 | 166 | 101.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:79&80 | 160 | 166 | 101.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | T:77&80 | 160 | 166 | 101.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | SB:GARD230_R873 | 160 | 166 | 101.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:191 | 160 | 166 | 101.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:54/921 | 160 | 166 | 101.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:706 NY | 160 | 166 | 101.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | First:Lancaster_706 | 160 | 166 | 101.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | S:PA_HNTL77 | 160 | 166 | 101.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | First:Lancaster_706 | 160 | 166 | 101.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:706 NY | 160 | 166 | 101.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | T:34&42 | 160 | 166 | 101.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:GARD230_R873 | 160 | 166 | 101.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:GARD230_R833 | 160 | 166 | 101.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | SB:HUNT230_R1502 | 160 | 166 | 101.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:GINNA | SB:HUNT230_R1402 | 160 | 166 | 101.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:115:GINNA | T:78&79 | 160 | 166 | 101.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 101.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 101.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | SB:HUNT230_R1402 | 160 | 166 | 101.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | T:40&41 | 160 | 166 | 101
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:GINNA | T:78&79 | 160 | 166 | 101
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 160 | 166 | 101
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | T:34&42 | 160 | 166 | 100.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | B:GARD72&79 | 160 | 166 | 100.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | SB:PA230_R3430 | 160 | 166 | 100.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:ROBI230 | 160 | 166 | 100.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:102 | 160 | 166 | 100.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:ROBI230 | 160 | 166 | 100.98
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | T:77&80 | 160 | 166 | 100.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | SB:GARD230_R823 | 160 | 166 | 100.97
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:PA230_R3230 | 160 | 166 | 100.97
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | LN:115:54/921 | 160 | 166 | 100.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | SB:HUNT230_R1502 | 160 | 166 | 100.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | B:GARD73&80 | 160 | 166 | 100.96
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 160 | 166 | 100.96
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 100.95
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | S:PA_HNTL78 | 160 | 166 | 100.95
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:192 | 160 | 166 | 100.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | SB:HUNT230_R1402 | 160 | 166 | 100.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:LOCKPORT | T:78&79 | 160 | 166 | 100.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:40&41 | 160 | 166 | 100.94
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:102 | 160 | 166 | 100.94
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 100.93
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:PACKT3 | 160 | 166 | 100.92
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_NEW | 160 | 166 | 100.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:926 NY | SB:HUNT230_R1402 | 160 | 166 | 100.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:926 NY | T:78&79 | 160 | 166 | 100.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:LAPER_345_3 | 160 | 166 | 100.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:LAPER_345_4 | 160 | 166 | 100.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | Base Case | 160 | 166 | 100.92
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:HUNT230_R1502 | 160 | 166 | 100.91
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 100.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | T:77&80 | 160 | 166 | 100.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:LAPER_345_3 | 160 | 166 | 100.91
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:LAPER_345_4 | 160 | 166 | 100.91
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 100.9
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MASS_765_7108 | 160 | 166 | 100.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | S:HNT_GRD80 | 160 | 166 | 100.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:LAPER_345_3 | 160 | 166 | 100.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:LAPER_345_4 | 160 | 166 | 100.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | SB:HUNT230_R1502 | 160 | 166 | 100.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | B:Hunt68 | 160 | 166 | 100.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | T:61&64 | 160 | 166 | 100.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:PA230_R3230 | 160 | 166 | 100.88
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | B:Hunt68 | 160 | 166 | 100.88
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | S:HNT_GRD80 | 160 | 166 | 100.87
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:180 | 160 | 166 | 100.87
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | SB:GARD230_R873 | 160 | 166 | 100.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:LAFA_ELB | 160 | 166 | 100.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:LAFA_ELB | 160 | 166 | 100.87
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:195 | 160 | 166 | 100.86
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:MASS_765_7102 | 160 | 166 | 100.86
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | T:77&80 | 160 | 166 | 100.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:GARD230_R873 | 160 | 166 | 100.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:LAPER_345_3 | 160 | 166 | 100.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:LAPER_345_4 | 160 | 166 | 100.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:LAFA_ELB | 160 | 166 | 100.86
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:HUNT230_R1502 | 160 | 166 | 100.84
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:180 | 160 | 166 | 100.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:GARD230_R833 | 160 | 166 | 100.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:41&33 | 160 | 166 | 100.84
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:LAFA_ELB | 160 | 166 | 100.84
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | S:PA_HNTL77 | 160 | 166 | 100.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 100.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 100.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:OAKD345_B5 | 160 | 166 | 100.83
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:OAKD345_B6 | 160 | 166 | 100.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 100.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:38 | 160 | 166 | 100.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:OAKD345_B5 | 160 | 166 | 100.82
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 100.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:OAKD345_B5 | 160 | 166 | 100.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:OAKD345_B6 | 160 | 166 | 100.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 100.81
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:39 | 160 | 166 | 100.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:OAKD345_B6 | 160 | 166 | 100.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 100.8
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:38 | 160 | 166 | 100.8
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 100.79
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:41&33 | 160 | 166 | 100.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:39 | 160 | 166 | 100.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:30&40 | 160 | 166 | 100.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:OAKD345_B5 | 160 | 166 | 100.78
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | T:41&33 | 160 | 166 | 100.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | SB:PA230_R3430 | 160 | 166 | 100.77
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | SB:PA230_R3430 | 160 | 166 | 100.77
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:40&41 | 160 | 166 | 100.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:GARD230_R833 | 160 | 166 | 100.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | T:34&42 | 160 | 166 | 100.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:OAKD345_B6 | 160 | 166 | 100.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | OAKDLE - CLARKCRNS 36B 345 | 160 | 166 | 100.76
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:31&41 | 160 | 166 | 100.76
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | S:PA_HNTL77 | 160 | 166 | 100.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | SB:HUNT230_R1402 | 160 | 166 | 100.75
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STONYCR - WTHRS 230 | T:78&79 | 160 | 166 | 100.75
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:191 | 160 | 166 | 100.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:GARD230_R873 | 160 | 166 | 100.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | SB:PA230_R304 | 160 | 166 | 100.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | SB:HUNT230_R1502 | 160 | 166 | 100.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | SB:HUNT230_R1502 | 160 | 166 | 100.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:41&33 | 160 | 166 | 100.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:ROBI230 | 160 | 166 | 100.74
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:101 | 160 | 166 | 100.74
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&80 | 160 | 166 | 100.73
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | T:77&80 | 160 | 166 | 100.73
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&80 | 160 | 166 | 100.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | SB:HUNT230_R1402 | 160 | 166 | 100.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:ROB | T:78&79 | 160 | 166 | 100.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:120 | 160 | 166 | 100.73
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | B:GARD73&80 | 160 | 166 | 100.72
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | SB:HUNT230_R1402 | 160 | 166 | 100.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | T:78&79 | 160 | 166 | 100.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:5M-SR_37&W-F_171 | B:Hunt68 | 160 | 166 | 100.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | S:PA_HNTL78 | 160 | 166 | 100.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 100.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-WC_30&W-F_171 | LN:115:182S | 160 | 166 | 100.71
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:61&64 | 160 | 166 | 100.71
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:NI1 | DCT:230:79+80+ELM1-2 | 160 | 166 | 100.7
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:HUNT230_R1502 | 160 | 166 | 100.7
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA 230/115 1TR | DCT:230:79+80+ELM1-2 | 160 | 166 | 100.7
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 7 | LN:115:182S | 160 | 166 | 100.7
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | B:GARD72&79 | 160 | 166 | 100.69
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 160 | 166 | 100.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 4 | LN:115:182S | 160 | 166 | 100.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 5 | LN:115:182S | 160 | 166 | 100.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:NIAG. 6 | LN:115:182S | 160 | 166 | 100.68
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:GARD230_T7-12 | 160 | 166 | 100.67
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:54/921 | 160 | 166 | 100.67
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:HUNT230_R1302 | 160 | 166 | 100.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 100.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTRCR - MAINSBRG 30A 345 | LN:115:182S | 160 | 166 | 100.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HCWC/NWES | LN:115:182S | 160 | 166 | 100.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:MBWC/NWES | LN:115:182S | 160 | 166 | 100.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | SB:GARD230_R823 | 160 | 166 | 100.66
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | LN:115:101 | 160 | 166 | 100.66
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | PACKARD 230/115 3TR | DCT:230:79+80+ELM1-2 | 160 | 166 | 100.65
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:HUNT230_R1402 | 160 | 166 | 100.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | T:78&79 | 160 | 166 | 100.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | B:STOLE230 | 160 | 166 | 100.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:255_345B202 | 160 | 166 | 100.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:COOP345_42-4182 | 160 | 166 | 100.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | SB:HUNT230_R1402 | 160 | 166 | 100.64
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDL - FRASER 32 345 | T:78&79 | 160 | 166 | 100.64
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 100.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | S:PA_HNTL78 | 160 | 166 | 100.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 78 230 | 160 | 166 | 100.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL77 | 160 | 166 | 100.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | B:GARD73&80 | 160 | 166 | 100.63
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:255_345B202 | 160 | 166 | 100.63
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:61&64 | 160 | 166 | 100.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | T:77&80 | 160 | 166 | 100.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SOMERSET - NEWROCH 1 345 | 160 | 166 | 100.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | T:77&80 | 160 | 166 | 100.62
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:COOP345_42-4182 | 160 | 166 | 100.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:120 | 160 | 166 | 100.61
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:COOP345_42-4182 | 160 | 166 | 100.61
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | SB:HUNT230_R1202 | 160 | 166 | 100.6
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:192 | 160 | 166 | 100.6
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | B:Hunt67 | 160 | 166 | 100.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | T:40&41 | 160 | 166 | 100.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | T:34&42 | 160 | 166 | 100.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926A | B:Hunt68 | 160 | 166 | 100.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SOMERSET - NEWROCH 1 345 | 160 | 166 | 100.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:COOP345_42-4182 | 160 | 166 | 100.6
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:61&64 | 160 | 166 | 100.6
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:HUNT230_R1502 | 160 | 166 | 100.59
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:908 NY | B:Hunt68 | 160 | 166 | 100.59
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_STOL_HOMER_345 | B:Hunt68 | 160 | 166 | 100.58
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_NEW | 160 | 166 | 100.58
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | 5 MILE - STOLLE 37A 345 | B:Hunt68 | 160 | 166 | 100.58
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | HUNTLEY - PACKARD 77 230 | 160 | 166 | 100.58
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HOMERCTY - STOLLRD 37 345 | B:Hunt68 | 160 | 166 | 100.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | T:61&64 | 160 | 166 | 100.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | T:31&41 | 160 | 166 | 100.58
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1202 | 160 | 166 | 100.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:EDIC345_R400 | 160 | 166 | 100.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | SB:PA230_R3430 | 160 | 166 | 100.57
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:COOP345_42-4182 | 160 | 166 | 100.56
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | B:STOLE230 | 160 | 166 | 100.55
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | T:31&41 | 160 | 166 | 100.55
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:HUNT230_R1302 | 160 | 166 | 100.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | S:HNT_GRD80 | 160 | 166 | 100.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | B:GARD73&80 | 160 | 166 | 100.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | B:GARD72&79 | 160 | 166 | 100.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | T:31&41 | 160 | 166 | 100.54
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:30&40 | 160 | 166 | 100.54
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:KINTIGH | 160 | 166 | 100.53
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | GEN:345:SOMERSET | 160 | 166 | 100.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | SB:GARD230_R833 | 160 | 166 | 100.53
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | T:31&41 | 160 | 166 | 100.53
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | SB:HUNT230_R1402 | 160 | 166 | 100.52
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | T:78&79 | 160 | 166 | 100.52
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | SB:HUNT230_R1402 | 160 | 166 | 100.52
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | T:78&79 | 160 | 166 | 100.52
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | ROBINSON - STOLLRD 65 230 | 160 | 166 | 100.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL78 | 160 | 166 | 100.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 78 230 | 160 | 166 | 100.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | NIAG - NEWROCH 1 345 | 160 | 166 | 100.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 100.51
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | SB:HUNT230_R1402 | 160 | 166 | 100.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | T:78&79 | 160 | 166 | 100.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:ROBI230 | 160 | 166 | 100.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | T:34&42 | 160 | 166 | 100.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | T:34&42 | 160 | 166 | 100.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:NIAG345_3108 | 160 | 166 | 100.5
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:102 | 160 | 166 | 100.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | T:41&33 | 160 | 166 | 100.49
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:908 NY | T:77&80 | 160 | 166 | 100.49
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | TB:2/1:PK3 | 160 | 166 | 100.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | SB:PA230_R3430 | 160 | 166 | 100.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | SB:PA230_R3430 | 160 | 166 | 100.48
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | NIAG - NEWROCH 1 345 | 160 | 166 | 100.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:NIAG345_3108 | 160 | 166 | 100.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:255_345B302 | 160 | 166 | 100.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | Base Case | 160 | 166 | 100.46
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 77 230 | 160 | 166 | 100.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | B:GARD72&79 | 160 | 166 | 100.45
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:39 | 160 | 166 | 100.45
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | B:Hunt68 | 160 | 166 | 100.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | LN:345:37S-FM-FV-HC | 160 | 166 | 100.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_926A | T:77&80 | 160 | 166 | 100.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | LN:345:37S-FM-FV-HC | 160 | 166 | 100.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:39 | 160 | 166 | 100.44
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:GARD230_R873 | 160 | 166 | 100.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 100.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | SB:PA230_R3430 | 160 | 166 | 100.43
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | SB:HUNT230_R1502 | 160 | 166 | 100.42
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:180 | 160 | 166 | 100.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 100.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:255_345B302 | 160 | 166 | 100.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | SB:HUNT230_R1502 | 160 | 166 | 100.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | S:HNT_GRD80 | 160 | 166 | 100.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:31&41 | 160 | 166 | 100.41
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | B:GARD73&80 | 160 | 166 | 100.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | SB:EDIC345_R915 | 160 | 166 | 100.4
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | SB:HUNT230_R1402 | 160 | 166 | 100.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:PA230_R3230 | 160 | 166 | 100.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | B:Hunt68 | 160 | 166 | 100.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | B:Hunt68 | 160 | 166 | 100.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | T:77&80 | 160 | 166 | 100.39
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | T:78&79 | 160 | 166 | 100.38
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | T:41&33 | 160 | 166 | 100.38
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | FARMVLY - HOMERCTY | 160 | 166 | 100.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 100.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | SB:HUNT230_R1502 | 160 | 166 | 100.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:40&41 | 160 | 166 | 100.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | LN:115:102 | 160 | 166 | 100.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:903 NY | 160 | 166 | 100.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | SB:EDIC345_R915 | 160 | 166 | 100.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:903 NY | 160 | 166 | 100.37
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:MARC345_3202 | 160 | 166 | 100.37
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | B:GARD73&80 | 160 | 166 | 100.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 100.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | SB:GARD230_R873 | 160 | 166 | 100.36
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | SB:GARD230_R833 | 160 | 166 | 100.35
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | T:MP11&41 | 160 | 166 | 100.35
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | LN:115:195 | 160 | 166 | 100.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | LN:115:195 | 160 | 166 | 100.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:54/921 | 160 | 166 | 100.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 100.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:COOP345_4182 | 160 | 166 | 100.34
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | LN:115:54/921 | 160 | 166 | 100.33
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | B:Hunt67 | 160 | 166 | 100.33
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:40&41 | 160 | 166 | 100.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | SB:HUNT230_R1502 | 160 | 166 | 100.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | SB:PA230_R3430 | 160 | 166 | 100.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | SB:HUNT230_R1502 | 160 | 166 | 100.32
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:MARC345_3208 | 160 | 166 | 100.32
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | R:HC-FV_37&W-F_171 | 160 | 166 | 100.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | SB:GARD230_R823 | 160 | 166 | 100.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | SB:GARD230_R823 | 160 | 166 | 100.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 100.31
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 100.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:EDIC345_R915 | 160 | 166 | 100.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | First:Lancaster_705 | 160 | 166 | 100.3
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:705 NY | 160 | 166 | 100.3
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:195 | 160 | 166 | 100.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:EDIC345_R915 | 160 | 166 | 100.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | MARCY - COOPERS 345 SC | 160 | 166 | 100.29
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:120 | 160 | 166 | 100.29
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:180 | 160 | 166 | 100.28
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 100.28
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:195 | 160 | 166 | 100.28
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | B:GARD72&79 | 160 | 166 | 100.28
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:180 | 160 | 166 | 100.27
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:GARD230_R823 | 160 | 166 | 100.27
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | SB:HUNT230_R1502 | 160 | 166 | 100.27
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | T:40&41 | 160 | 166 | 100.27
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | B:Hunt68 | 160 | 166 | 100.27
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:191 | 160 | 166 | 100.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | B:Hunt68 | 160 | 166 | 100.26
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:COOP345_42-4182 | 160 | 166 | 100.26
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | G:BRUCE5 | 160 | 166 | 100.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 100.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | T:77&80 | 160 | 166 | 100.25
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | T:77&80 | 160 | 166 | 100.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:120 | T:61&64 | 160 | 166 | 100.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:705 NY | 160 | 166 | 100.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | First:Lancaster_705 | 160 | 166 | 100.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:FRAS345_B1-4062 | 160 | 166 | 100.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | EDIC - FRASER 345 SC | 160 | 166 | 100.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | S:HNT_GRD80 | 160 | 166 | 100.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | T:34&42 | 160 | 166 | 100.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:705 NY | 160 | 166 | 100.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | First:Lancaster_705 | 160 | 166 | 100.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:EDIC345_R400 | 160 | 166 | 100.24
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | LN:115:54/921 | 160 | 166 | 100.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:3/2:FV | B:Hunt68 | 160 | 166 | 100.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | B:Hunt68 | 160 | 166 | 100.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | T:MP11&41 | 160 | 166 | 100.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:COOP345_4182 | 160 | 166 | 100.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:FRAS345_40-B262 | 160 | 166 | 100.23
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | B:STOLE230 | 160 | 166 | 100.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | SB:HUNT230_R1402 | 160 | 166 | 100.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | T:78&79 | 160 | 166 | 100.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:MARC345_3208 | 160 | 166 | 100.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | T:MP11&41 | 160 | 166 | 100.22
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:COOP345_4182 | 160 | 166 | 100.22
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | GEN:115:GINNA | 160 | 166 | 100.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | SB:ROBI230 | 160 | 166 | 100.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:MARC345_3208 | 160 | 166 | 100.21
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | G:GINNA | 160 | 166 | 100.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV1 | B:Hunt68 | 160 | 166 | 100.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | CAP:115:GV2 | B:Hunt68 | 160 | 166 | 100.2
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:MARC345_3202 | 160 | 166 | 100.2
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | SB:GARD230_T7-12 | 160 | 166 | 100.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-SR_37&W-F_171 | SB:GARD230_R823 | 160 | 166 | 100.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:FV-5M_37&W-F_171 | SB:GARD230_R823 | 160 | 166 | 100.19
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:MARC345_3202 | 160 | 166 | 100.19
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | T:77&80 | 160 | 166 | 100.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | SB:HUNT230_R1402 | 160 | 166 | 100.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:EDIC345_R935 | 160 | 166 | 100.18
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | T:40&41 | 160 | 166 | 100.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:PACKT3 | 160 | 166 | 100.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:100 | T:78&79 | 160 | 166 | 100.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | GEN:115:AMERT | 160 | 166 | 100.17
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | MARCY - COOPERS 345 SC | 160 | 166 | 100.17
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | LN:115:192 | 160 | 166 | 100.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | MARCY - COOPERS 345 SC | 160 | 166 | 100.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:BLISS1 | SB:GARD230_R823 | 160 | 166 | 100.16
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | SB:HUNT230_R1402 | 160 | 166 | 100.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | T:78&79 | 160 | 166 | 100.15
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | T:77&76 | 160 | 166 | 100.15
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:195 | 160 | 166 | 100.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:NIAG345_3108 | 160 | 166 | 100.14
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | T:77&76 | 160 | 166 | 100.14
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:ROBI230 | 160 | 166 | 100.13
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | SB:GARD230_T7-12 | 160 | 166 | 100.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | S:HNT_GRD80 | 160 | 166 | 100.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | R:EESR/NWES | 160 | 166 | 100.13
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV | SB:GARD230_R823 | 160 | 166 | 100.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | First:Lancaster_926B | 160 | 166 | 100.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 100.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | SB:GARD230_R873 | 160 | 166 | 100.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | SB:GARD230_R873 | 160 | 166 | 100.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | SB:MARC345_3108 | 160 | 166 | 100.11
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | T:34&42 | 160 | 166 | 100.1
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:345:37S-FM-FV-HC | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 100.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | T:34&42 | 160 | 166 | 100.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:38 | B:GARD73&80 | 160 | 166 | 100.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | Base Case | 160 | 166 | 100.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | T:40&41 | 160 | 166 | 100.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - PACKARD 62 230 | T:61&64 | 160 | 166 | 100.08
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:38 | 160 | 166 | 100.08
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | STOLLRD - GARDENVILL 66 230 | 160 | 166 | 100.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | DUNKIRK - SRIPL 68 230 | 160 | 166 | 100.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SB:SRIPLEY | 160 | 166 | 100.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | GEN:SITHE 2 | 160 | 166 | 100.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | GEN:SITHE 1 | 160 | 166 | 100.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | NIAG - NEWROCH 1 345 | 160 | 166 | 100.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | G:INDEK-OL | T:40&41 | 160 | 166 | 100.07
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | SB:HUNT230_R1402 | 160 | 166 | 100.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - 5MILE 345 | T:78&79 | 160 | 166 | 100.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:102 | NIAGARA - ROBINSON 64 345 | 160 | 166 | 100.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | B:GARD72&79 | 160 | 166 | 100.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | B:GARD72&79 | 160 | 166 | 100.06
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | S:PA_HNTL77 | 160 | 166 | 100.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | SB:HUNT230_R1402 | 160 | 166 | 100.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:3/2:FV | T:77&80 | 160 | 166 | 100.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - FARMVLY | T:77&80 | 160 | 166 | 100.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | SB:HUNT230_R1402 | 160 | 166 | 100.05
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1202 | 160 | 166 | 100.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:345:SOMERSET | T:78&79 | 160 | 166 | 100.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | SRIPL - ERIE E 69 230 | 160 | 166 | 100.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | SB:GARD230_R833 | 160 | 166 | 100.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | SB:GARD230_R833 | 160 | 166 | 100.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | GEN:KINTIGH | T:78&79 | 160 | 166 | 100.04
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | SB:ROBI230 | 160 | 166 | 100.03
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | T:34&42 | 160 | 166 | 100.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:255_345B302 | 160 | 166 | 100.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | WTHRS - MEYER 230 | T:77&80 | 160 | 166 | 100.03
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | HUNTLEY - GARDENVILL 79 230 | 160 | 166 | 100.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:705 NY | SB:5MILE_B | 160 | 166 | 100.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | First:Lancaster_705 | SB:5MILE_B | 160 | 166 | 100.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | LN:115:120 | 160 | 166 | 100.02
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:HUNT230_R1302 | 160 | 166 | 100.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | SB:GARD230_R873 | 160 | 166 | 100.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:39 | HUNTLEY - GARDENVILL 80 230 | 160 | 166 | 100.01
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAGARA - ROBINSON 64 345 | SB:5MILE_B | 160 | 166 | 100.01
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | TB:2/1:PK3 | 160 | 166 | 100
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | GEN: IND PT 2 | 160 | 166 | 100
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | B:GARD73&80 | 160 | 166 | 100
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | SB:MARC345_3202 | 160 | 166 | 100
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 Max |  |  |  |  | 180.09
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 200 | 208 | NConv
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 200 | 208 | NConv
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 200 | 208 | NConv
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 200 | 208 | NConv
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 200 | 208 | NConv
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 200 | 208 | NConv
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 200 | 208 | NConv
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 200 | 208 | NConv
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 200 | 208 | NConv
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 200 | 208 | NConv
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 208 | 163.76
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 200 | 208 | 161.2
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | T:77&78 | 200 | 208 | 142.12
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 200 | 208 | 141.34
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 200 | 208 | 137.28
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | T:77&78 | 200 | 208 | 136.62
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | T:77&78 | 200 | 208 | 135.73
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 200 | 208 | 131.6
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | T:77&78 | 200 | 208 | 129.97
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 200 | 208 | 127.71
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 200 | 208 | 127.54
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 200 | 208 | 125.89
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | T:79&80 | 200 | 208 | 124.81
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 200 | 208 | 124.4
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 200 | 208 | 124.39
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:195 | T:77&78 | 200 | 208 | 124.23
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:191 | T:77&78 | 200 | 208 | 122.81
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | TB:2/1:PK3 | T:77&78 | 200 | 208 | 122.73
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:192 | T:77&78 | 200 | 208 | 122.64
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 200 | 208 | 122.41
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 200 | 208 | 122.38
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 200 | 208 | 121.33
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 200 | 208 | 120.89
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 200 | 208 | 120.88
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 200 | 208 | 120.61
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:38 | T:77&78 | 200 | 208 | 120.01
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 200 | 208 | 119.92
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 200 | 208 | 119.87
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:39 | T:77&78 | 200 | 208 | 119.73
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 200 | 208 | 119.57
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:195 | T:77&78 | 200 | 208 | 119.52
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 200 | 208 | 119.47
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 200 | 208 | 119.47
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | T:79&80 | 200 | 208 | 119.3
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV | T:77&78 | 200 | 208 | 119.19
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 200 | 208 | 119.1
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 200 | 208 | 118.86
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 200 | 208 | 118.81
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | T:79&80 | 200 | 208 | 118.75
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:191 | T:77&78 | 200 | 208 | 118.64
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:192 | T:77&78 | 200 | 208 | 118.51
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | FARMVLY - HOMERCTY | T:77&78 | 200 | 208 | 118.43
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 200 | 208 | 117.87
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 200 | 208 | 117.35
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 200 | 208 | 117.32
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:101 | T:77&78 | 200 | 208 | 117.01
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:102 | T:77&78 | 200 | 208 | 116.79
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:133 | T:77&78 | 200 | 208 | 116.73
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | TB:2/1:PK3 | T:77&78 | 200 | 208 | 116.64
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:120 | T:77&78 | 200 | 208 | 116.61
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:130 | T:77&78 | 200 | 208 | 116.5
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 200 | 208 | 116.43
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 200 | 208 | 116.43
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 200 | 208 | 116.43
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 200 | 208 | 116.4
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:129 | T:77&78 | 200 | 208 | 116.2
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | First:Lancaster_922 | T:77&78 | 200 | 208 | 116.13
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 200 | 208 | 116.09
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 200 | 208 | 116.05
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:BLISS1 | T:77&78 | 200 | 208 | 115.89
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 200 | 208 | 115.51
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:INDEK-OL | T:77&78 | 200 | 208 | 115.34
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:38 | T:77&78 | 200 | 208 | 115.24
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 200 | 208 | 115
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 115
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:39 | T:77&78 | 200 | 208 | 114.96
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 200 | 208 | 114.82
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 200 | 208 | 114.74
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 200 | 208 | 114.73
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 200 | 208 | 114.73
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV | T:77&78 | 200 | 208 | 114.47
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 200 | 208 | 114.47
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 200 | 208 | 114.3
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 200 | 208 | 114.26
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 200 | 208 | 114.07
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 200 | 208 | 114.07
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 200 | 208 | 114.07
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 200 | 208 | 114.06
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | FARMVLY - HOMERCTY | T:77&78 | 200 | 208 | 113.88
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | T:79&80 | 200 | 208 | 112.98
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 200 | 208 | 112.88
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 200 | 208 | 112.81
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:5M-SR_37&W-F_171 | T:77&78 | 200 | 208 | 112.47
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | LN:115:180 | 200 | 208 | 112.12
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:101 | T:77&78 | 200 | 208 | 112.06
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:133 | T:77&78 | 200 | 208 | 112.01
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | LN:115:181/922 | 200 | 208 | 111.98
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:102 | T:77&78 | 200 | 208 | 111.87
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:130 | T:77&78 | 200 | 208 | 111.82
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:120 | T:77&78 | 200 | 208 | 111.77
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | First:Lancaster_STOL_HOMER_345 | T:77&78 | 200 | 208 | 111.74
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | 5 MILE - STOLLE 37A 345 | T:77&78 | 200 | 208 | 111.74
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HOMERCTY - STOLLRD 37 345 | T:77&78 | 200 | 208 | 111.74
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 111.61
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | First:Lancaster_922 | T:77&78 | 200 | 208 | 111.48
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:129 | T:77&78 | 200 | 208 | 111.44
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:BLISS1 | T:77&78 | 200 | 208 | 111.42
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | First:Lancaster_GRDN_GRDN_230 | T:77&78 | 200 | 208 | 111.05
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 200 | 208 | 110.97
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | GEN:115:GINNA | T:77&78 | 200 | 208 | 110.83
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:INDEK-OL | T:77&78 | 200 | 208 | 110.81
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:GINNA | T:77&78 | 200 | 208 | 110.8
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - KINTIGH 345 | T:77&78 | 200 | 208 | 110.65
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:100 | T:77&78 | 200 | 208 | 110.52
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 200 | 208 | 110.5
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 200 | 208 | 110.3
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 200 | 208 | 110.28
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:908 NY | T:77&78 | 200 | 208 | 110.12
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STONYCR - WTHRS 230 | T:77&78 | 200 | 208 | 109.97
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 200 | 208 | 109.65
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 200 | 208 | 109.65
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 200 | 208 | 109.65
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 200 | 208 | 109.64
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 200 | 208 | 109.64
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | T:77&80 | 200 | 208 | 109.64
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | B:Hunt68 | 200 | 208 | 109.61
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | CAP:115:GV1 | T:77&78 | 200 | 208 | 109.45
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | CAP:115:GV2 | T:77&78 | 200 | 208 | 109.45
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 200 | 208 | 109.17
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:195 | T:79&80 | 200 | 208 | 109.04
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | GEN:345:SOMERSET | T:77&78 | 200 | 208 | 108.99
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | GEN:KINTIGH | T:77&78 | 200 | 208 | 108.99
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_R1502 | 200 | 208 | 108.82
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 200 | 208 | 108.63
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_R1402 | 200 | 208 | 108.59
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | T:78&79 | 200 | 208 | 108.58
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 200 | 208 | 108.19
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 200 | 208 | 108.01
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | TB:2/1:PK3 | T:79&80 | 200 | 208 | 108
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 107.63
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:191 | T:79&80 | 200 | 208 | 107.62
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 200 | 208 | 107.61
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:192 | T:79&80 | 200 | 208 | 107.44
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 200 | 208 | 107.21
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HCWC/NWES | T:77&78 | 200 | 208 | 107.21
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:MBWC/NWES | T:77&78 | 200 | 208 | 107.21
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | WTHRS - MEYER 230 | T:77&78 | 200 | 208 | 107.15
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_NEW | 200 | 208 | 107.11
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | B:Hunt67 | 200 | 208 | 106.74
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 200 | 208 | 106.71
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 106.67
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 200 | 208 | 106.62
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 200 | 208 | 106.49
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | GEN:115:GINNA | T:77&78 | 200 | 208 | 106.44
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:GINNA | T:77&78 | 200 | 208 | 106.43
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 7 | T:77&78 | 200 | 208 | 106.41
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 11 | T:77&78 | 200 | 208 | 106.39
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 12 | T:77&78 | 200 | 208 | 106.39
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 13 | T:77&78 | 200 | 208 | 106.39
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 8 | T:77&78 | 200 | 208 | 106.39
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 9 | T:77&78 | 200 | 208 | 106.39
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 10 | T:77&78 | 200 | 208 | 106.38
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 4 | T:77&78 | 200 | 208 | 106.38
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 5 | T:77&78 | 200 | 208 | 106.38
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 6 | T:77&78 | 200 | 208 | 106.38
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 200 | 208 | 106.32
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 200 | 208 | 106.27
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 200 | 208 | 106.25
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:GARD230_T7-12 | 200 | 208 | 106.21
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 200 | 208 | 106.21
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 200 | 208 | 106.14
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 200 | 208 | 106.13
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 200 | 208 | 106.13
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 200 | 208 | 106.08
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | OAKDL - FRASER 32 345 | T:77&78 | 200 | 208 | 106.06
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_R1302 | 200 | 208 | 106.03
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_R1202 | 200 | 208 | 105.99
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | TB:2/1:ROB | T:77&78 | 200 | 208 | 105.98
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 105.91
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | TB:2/1:NI1 | T:77&78 | 200 | 208 | 105.84
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAGARA 230/115 1TR | T:77&78 | 200 | 208 | 105.84
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HCMB/NWES | T:77&78 | 200 | 208 | 105.83
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 200 | 208 | 105.71
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STONYCR - WTHRS 230 | T:77&78 | 200 | 208 | 105.59
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:100 | T:77&78 | 200 | 208 | 105.43
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 200 | 208 | 105.41
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:181/922 | 200 | 208 | 105.4
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:181/922 | 200 | 208 | 105.34
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:195 | DCT:230:79+80+ELM1-2 | 200 | 208 | 105.24
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 105.2
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:39 | DCT:230:79+80+ELM1-2 | 200 | 208 | 105.15
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 200 | 208 | 105.15
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | S:PA_HNTL77 | 200 | 208 | 105.08
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:908 NY | T:77&78 | 200 | 208 | 105.06
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | CAP:115:GV1 | T:77&78 | 200 | 208 | 105.02
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | CAP:115:GV2 | T:77&78 | 200 | 208 | 105.02
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 200 | 208 | 105.02
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | S:PA_HNTL78 | 200 | 208 | 104.95
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | HUNTLEY - PACKARD 78 230 | 200 | 208 | 104.95
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | HUNTLEY - PACKARD 77 230 | 200 | 208 | 104.9
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | GEN:345:SOMERSET | T:77&78 | 200 | 208 | 104.86
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | GEN:KINTIGH | T:77&78 | 200 | 208 | 104.86
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV-HC | DCT:230:79+80+ELM1-2 | 200 | 208 | 104.77
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 200 | 208 | 104.73
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | B:STOLE230 | 200 | 208 | 104.63
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - ELM 70 230 | T:79&80 | 200 | 208 | 104.6
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:38 | T:79&80 | 200 | 208 | 104.52
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:195 | T:79&80 | 200 | 208 | 104.39
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 200 | 208 | 104.39
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:79&80 | 200 | 208 | 104.33
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:191 | DCT:230:79+80+ELM1-2 | 200 | 208 | 104.28
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:39 | T:79&80 | 200 | 208 | 104.27
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | PACKARD 230/115 3TR | T:77&78 | 200 | 208 | 104.23
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:192 | DCT:230:79+80+ELM1-2 | 200 | 208 | 104.15
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:181/922 | 200 | 208 | 104.11
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV-HC | T:79&80 | 200 | 208 | 103.98
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-FV_37&W-F_171 | T:79&80 | 200 | 208 | 103.95
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:181/922 | 200 | 208 | 103.9
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | STOLLRD - GARDENVILL 66 230 | 200 | 208 | 103.85
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | B:Hunt68 | 200 | 208 | 103.82
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_NEW | 200 | 208 | 103.78
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | LN:115:180 | 200 | 208 | 103.76
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | T:77&80 | 200 | 208 | 103.74
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | ROBINSON - STOLLRD 65 230 | 200 | 208 | 103.73
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:101 | DCT:230:79+80+ELM1-2 | 200 | 208 | 103.65
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | LN:115:181/922 | 200 | 208 | 103.62
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | FARMVLY - HOMERCTY | T:79&80 | 200 | 208 | 103.6
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 7 | T:77&78 | 200 | 208 | 103.58
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 4 | T:77&78 | 200 | 208 | 103.57
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 5 | T:77&78 | 200 | 208 | 103.57
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:NIAG. 6 | T:77&78 | 200 | 208 | 103.57
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 200 | 208 | 103.55
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:FV-5M_37&W-F_171 | DCT:230:79+80+ELM1-2 | 200 | 208 | 103.55
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV | DCT:230:79+80+ELM1-2 | 200 | 208 | 103.49
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:191 | T:79&80 | 200 | 208 | 103.46
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 103.46
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:102 | DCT:230:79+80+ELM1-2 | 200 | 208 | 103.43
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:192 | T:79&80 | 200 | 208 | 103.33
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | T:77&80 | 200 | 208 | 103.32
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:120 | DCT:230:79+80+ELM1-2 | 200 | 208 | 103.27
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 200 | 208 | 103.25
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | B:Hunt68 | 200 | 208 | 103.23
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | SB:HUNT230_R1502 | 200 | 208 | 103.19
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:101 | T:79&80 | 200 | 208 | 103.02
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 200 | 208 | 102.98
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | SB:HUNT230_R1402 | 200 | 208 | 102.97
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | T:78&79 | 200 | 208 | 102.96
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | TB:2/1:PK3 | DCT:230:79+80+ELM1-2 | 200 | 208 | 102.95
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HCWC/NWES | T:77&78 | 200 | 208 | 102.87
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:MBWC/NWES | T:77&78 | 200 | 208 | 102.87
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 200 | 208 | 102.86
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:102 | T:79&80 | 200 | 208 | 102.8
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV | T:79&80 | 200 | 208 | 102.79
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 200 | 208 | 102.78
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-SR_37&W-F_171 | T:79&80 | 200 | 208 | 102.78
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:FV-5M_37&W-F_171 | T:79&80 | 200 | 208 | 102.78
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | WTHRS - MEYER 230 | T:77&78 | 200 | 208 | 102.77
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:120 | T:79&80 | 200 | 208 | 102.64
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:BLISS1 | DCT:230:79+80+ELM1-2 | 200 | 208 | 102.54
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 200 | 208 | 102.49
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | FARMVLY - 5MILE 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 102.49
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_R1502 | 200 | 208 | 102.45
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | First:Lancaster_922 | DCT:230:79+80+ELM1-2 | 200 | 208 | 102.45
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:PA230_R3430 | 200 | 208 | 102.43
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_R1402 | 200 | 208 | 102.25
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | T:78&79 | 200 | 208 | 102.25
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 102.23
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 200 | 208 | 102.22
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:GARD230_R823 | 200 | 208 | 102.17
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:133 | T:79&80 | 200 | 208 | 102.14
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 200 | 208 | 102.11
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:5M-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 200 | 208 | 102.09
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | TB:2/1:PK3 | T:79&80 | 200 | 208 | 102.03
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 200 | 208 | 102.02
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:INDEK-OL | DCT:230:79+80+ELM1-2 | 200 | 208 | 102.01
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:130 | T:79&80 | 200 | 208 | 101.93
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:GARD230_R833 | 200 | 208 | 101.81
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:BLISS1 | T:79&80 | 200 | 208 | 101.81
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | FARMVLY - 5MILE 345 | T:79&80 | 200 | 208 | 101.8
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 200 | 208 | 101.77
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 200 | 208 | 101.72
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 200 | 208 | 101.7
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 200 | 208 | 101.69
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | First:Lancaster_922 | T:79&80 | 200 | 208 | 101.69
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:129 | T:79&80 | 200 | 208 | 101.68
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | TB:2/1:PK3 | 200 | 208 | 101.67
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | B:GARD72&79 | 200 | 208 | 101.66
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 200 | 208 | 101.62
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 200 | 208 | 101.62
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 200 | 208 | 101.61
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 101.53
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | SB:HUNT230_NEW | 200 | 208 | 101.52
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HCMB/NWES | T:77&78 | 200 | 208 | 101.5
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:5M-SR_37&W-F_171 | T:79&80 | 200 | 208 | 101.47
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:181/922 | 200 | 208 | 101.46
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:181/922 | 200 | 208 | 101.45
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | S:HNT_GRD80 | 200 | 208 | 101.42
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:ROBI230 | 200 | 208 | 101.38
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 200 | 208 | 101.33
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | TB:2/1:PK3 | LN:115:181/922 | 200 | 208 | 101.33
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | HUNTLEY - GARDENVILL 79 230 | 200 | 208 | 101.32
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | HUNTLEY - GARDENVILL 80 230 | 200 | 208 | 101.31
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | LN:115:195 | 200 | 208 | 101.31
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | G:INDEK-OL | T:79&80 | 200 | 208 | 101.3
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | B:Hunt67 | 200 | 208 | 101.1
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:PA230_R3230 | 200 | 208 | 101.02
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:195 | LN:115:181/922 | 200 | 208 | 100.94
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:GARD230_R873 | 200 | 208 | 100.9
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | SB:GARD230_T7-12 | 200 | 208 | 100.86
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 200 | 208 | 100.84
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&80 | 200 | 208 | 100.81
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 200 | 208 | 100.8
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:38 | DCT:230:79+80+ELM1-2 | 200 | 208 | 100.72
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | SB:HUNT230_NEW | 200 | 208 | 100.71
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | STOLLRD - GARDENVILL 66 230 | B:Hunt68 | 200 | 208 | 100.67
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R823 | 200 | 208 | 100.64
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | FARMVLY - HOMERCTY | 200 | 208 | 100.53
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | B:GARD73&80 | 200 | 208 | 100.53
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | SB:HUNT230_R1302 | 200 | 208 | 100.49
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | R:HC-FV_37&W-F_171 | 200 | 208 | 100.49
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:180 | SB:HUNT230_R1202 | 200 | 208 | 100.48
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:39 | DCT:230:79+80+ELM1-2 | 200 | 208 | 100.46
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 200 | 208 | 100.41
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 200 | 208 | 100.38
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:345:37S-FM-FV-HC | DCT:230:79+80+ELM1-2 | 200 | 208 | 100.35
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | LN:115:191 | 200 | 208 | 100.33
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | B:Hunt67 | 200 | 208 | 100.32
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R833 | 200 | 208 | 100.29
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | T:40&41 | 200 | 208 | 100.21
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - GARDENVILL 80 230 | T:78&79 | 200 | 208 | 100.21
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - ELM 70 230 | T:79&80 | 200 | 208 | 100.2
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | HUNTLEY - GARDENVILL 79 230 | T:77&80 | 200 | 208 | 100.18
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | LN:115:192 | 200 | 208 | 100.17
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 200 | 208 | 100.04
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | LN:115:181/922 | LN:115:101 | 200 | 208 | 100.03
| 135460 PACK(N)E 115 135538 LONG-182 115 1 Max |  |  |  |  | 163.76
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | NIAGARA - PACKARD 62 230 | T:61&191 | 247 | 328 | 125.19
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | PACKARD 230/115 3TR | T:61&191 | 247 | 328 | 123.07
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:180 | T:61&191 | 247 | 328 | 122.28
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | PACKARD 230/115 3TR | T:61&191 | 247 | 328 | 113.56
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:101 | T:61&191 | 247 | 328 | 112.16
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:102 | T:61&191 | 247 | 328 | 111.65
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:120 | T:61&191 | 247 | 328 | 111.14
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | NIAGARA - PACKARD 62 230 | T:61&191 | 247 | 328 | 110.92
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | ROBINSON - STOLLRD 65 230 | T:61&191 | 247 | 328 | 110.25
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | STOLLRD - GARDENVILL 66 230 | T:61&191 | 247 | 328 | 109.97
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | GEN:115:AMERT | T:61&191 | 247 | 328 | 109
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 247 | 328 | 107.5
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LFYTE - CLARKCRNS 36A 345 | T:61&191 | 247 | 328 | 106.83
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | R:HC-FV_37&W-F_171 | T:61&191 | 247 | 328 | 106.73
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | FARMVLY - HOMERCTY | T:61&191 | 247 | 328 | 106.71
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:119 | T:61&191 | 247 | 328 | 106.55
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | OAKDLE - CLARKCRNS 36B 345 | T:61&191 | 247 | 328 | 106.54
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | G:HOORKN86 | T:61&191 | 247 | 328 | 106.32
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | G:HOORKN85 | T:61&191 | 247 | 328 | 106.28
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:38 | T:61&191 | 247 | 328 | 106.21
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:113 | T:61&191 | 247 | 328 | 106.08
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:54/921 | T:61&191 | 247 | 328 | 106.04
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | BECK - PACKARD BP76 230 | T:61&191 | 247 | 328 | 106.03
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:114 | T:61&191 | 247 | 328 | 106.02
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:111 | T:61&191 | 247 | 328 | 106
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:39 | T:61&191 | 247 | 328 | 105.99
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:345:37S-FM-FV-HC | T:61&191 | 247 | 328 | 105.69
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | HUNTLEY - PACKARD 78 230 | T:61&191 | 247 | 328 | 105.61
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | HUNTLEY - PACKARD 77 230 | T:61&191 | 247 | 328 | 105.6
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:180 | T:61&191 | 247 | 328 | 102.06
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | TB:3/2:FV | T:61&191 | 247 | 328 | 102.03
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | FARMVLY - FARMVLY | T:61&191 | 247 | 328 | 102.03
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | First:Lockport_103 | T:61&191 | 247 | 328 | 101.98
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:130 | T:61&191 | 247 | 328 | 101.96
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:133 | T:61&191 | 247 | 328 | 101.93
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | CAP:115:GV1 | T:61&191 | 247 | 328 | 101.8
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | CAP:115:GV2 | T:61&191 | 247 | 328 | 101.8
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | STONYCR - WTHRS 230 | T:61&191 | 247 | 328 | 101.63
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | First:Lockport_104 | T:61&191 | 247 | 328 | 101.27
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | GEN:115:GINNA | T:61&191 | 247 | 328 | 101.04
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | G:GINNA | T:61&191 | 247 | 328 | 101.02
Dispatch 1 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 247 | 328 | 101
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | WTHRS - MEYER 230 | T:61&191 | 247 | 328 | 100.49
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | First:Lockport_907 | T:61&191 | 247 | 328 | 100.26
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | LN:115:907 NY | T:61&191 | 247 | 328 | 100.22
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | R:HC-WC_30&W-F_171 | T:61&191 | 247 | 328 | 100.07
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | WTRCR - MAINSBRG 30A 345 | T:61&191 | 247 | 328 | 100.05
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | R:HCWC/NWES | T:61&191 | 247 | 328 | 100.04
Dispatch 2 | 135460 PACK(N)E 115 147850 NIAG115E 115 2 | R:MBWC/NWES | T:61&191 | 247 | 328 | 100.04
| 135460 PACK(N)E 115 147850 NIAG115E 115 2 Max |  |  |  |  | 125.19
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:194 | LN:115:195 | 273 | 351 | 139.06
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:195 | LN:115:194 | 273 | 351 | 139
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:194 | LN:115:195 | 273 | 351 | 119.76
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:195 | LN:115:194 | 273 | 351 | 119.7
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:195 | Base Case | 273 | 351 | 100.6
| 135461 PACK(S)W 115 147851 NIAG115W 115 1 Max |  |  |  |  | 139.06
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:193 | LN:115:195 | 273 | 351 | 139.06
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:195 | LN:115:193 | 273 | 351 | 139
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:193 | LN:115:195 | 273 | 351 | 119.76
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:195 | LN:115:193 | 273 | 351 | 119.7
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:195 | Base Case | 273 | 351 | 100.6
| 135461 PACK(S)W 115 147851 NIAG115W 115 2 Max |  |  |  |  | 139.06
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 273 | 351 | NConv
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 273 | 351 | NConv
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 273 | 351 | NConv
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:193 | LN:115:194 | 273 | 351 | 129.48
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:194 | LN:115:193 | 273 | 351 | 129.48
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:193 | LN:115:194 | 273 | 351 | 109.94
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:194 | LN:115:193 | 273 | 351 | 109.94
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 Max |  |  |  |  | 129.48
Dispatch 1 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 247 | 275 | NConv
Dispatch 1 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 247 | 275 | NConv
Dispatch 1 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 247 | 275 | NConv
Dispatch 1 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 247 | 275 | NConv
Dispatch 1 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 247 | 275 | NConv
Dispatch 2 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 247 | 275 | NConv
Dispatch 2 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 247 | 275 | NConv
Dispatch 2 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 247 | 275 | NConv
Dispatch 2 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 247 | 275 | NConv
Dispatch 2 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 247 | 275 | NConv
| 135464 SANBORNT 115 147850 NIAG115E 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 168 | 181 | NConv
Dispatch 1 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 1 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 168 | 181 | NConv
Dispatch 1 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 168 | 181 | NConv
Dispatch 1 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 168 | 181 | NConv
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 168 | 181 | NConv
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 168 | 181 | NConv
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 181 | NConv
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:101 | LN:115:102 | 168 | 181 | 122.63
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:102 | LN:115:101 | 168 | 181 | 122.62
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 168 | 181 | 109.53
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 168 | 181 | 109.42
Dispatch 1 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:101 | LN:115:102 | 168 | 181 | 108.18
Dispatch 1 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:102 | LN:115:101 | 168 | 181 | 108.18
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | LN:115:102 | 168 | 181 | 104.5
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | LN:115:101 | 168 | 181 | 104.37
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:908 NY | LN:115:101 | 168 | 181 | 104.35
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:101 | LN:115:908 NY | 168 | 181 | 104.34
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:908 NY | LN:115:102 | 168 | 181 | 104.33
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:102 | LN:115:908 NY | 168 | 181 | 104.31
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:102 | 168 | 181 | 102.21
Dispatch 1 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 168 | 181 | 102.18
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:101 | 168 | 181 | 102.12
Dispatch 1 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 168 | 181 | 102.1
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:102 | T:61&64 | 168 | 181 | 101.94
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:100 | LN:115:101 | 168 | 181 | 101.9
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:101 | LN:115:100 | 168 | 181 | 101.9
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:102 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 101.89
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:100 | LN:115:102 | 168 | 181 | 101.87
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:102 | LN:115:100 | 168 | 181 | 101.87
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:101 | T:61&64 | 168 | 181 | 101.85
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:101 | NIAGARA - ROBINSON 64 345 | 168 | 181 | 101.8
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:102 | 168 | 181 | 101.71
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:101 | 168 | 181 | 101.53
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:102 | SB:255_345B302 | 168 | 181 | 101.15
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:101 | SB:255_345B302 | 168 | 181 | 100.98
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:102 | SB:NIAG345_3108 | 168 | 181 | 100.77
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:102 | NIAG - NEWROCH 1 345 | 168 | 181 | 100.74
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:101 | SB:NIAG345_3108 | 168 | 181 | 100.59
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:101 | NIAG - NEWROCH 1 345 | 168 | 181 | 100.56
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:101 | SB:ROBI230 | 168 | 181 | 100.11
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:102 | SB:ROBI230 | 168 | 181 | 100.11
| 135467 SHAW-103 115 135470 SWAN-103 115 1 Max |  |  |  |  | 122.63
Dispatch 1 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 275 | 303 | NConv
Dispatch 1 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 275 | 303 | NConv
Dispatch 1 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 275 | 303 | NConv
Dispatch 1 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 275 | 303 | NConv
Dispatch 1 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 275 | 303 | NConv
Dispatch 2 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 275 | 303 | NConv
Dispatch 2 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 275 | 303 | NConv
Dispatch 2 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 275 | 303 | NConv
Dispatch 2 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 275 | 303 | NConv
Dispatch 2 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 275 | 303 | NConv
| 135468 SNBRN102 115 135510 SHAW-102 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 247 | 275 | NConv
Dispatch 1 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 247 | 275 | NConv
Dispatch 1 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 247 | 275 | NConv
Dispatch 1 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 247 | 275 | NConv
Dispatch 1 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 247 | 275 | NConv
Dispatch 2 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 247 | 275 | NConv
Dispatch 2 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 247 | 275 | NConv
Dispatch 2 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 247 | 275 | NConv
Dispatch 2 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 247 | 275 | NConv
Dispatch 2 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 247 | 275 | NConv
| 135468 SNBRN102 115 147850 NIAG115E 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 298 | NConv
Dispatch 1 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 1 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 298 | NConv
Dispatch 1 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 298 | NConv
Dispatch 1 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 298 | NConv
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 298 | NConv
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 298 | NConv
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | LN:115:133 | T:77&78 | 239 | 298 | 112.03
Dispatch 1 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | LN:115:133 | T:77&78 | 239 | 298 | 108.07
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | LN:115:133 | Base Case | 239 | 298 | 105.53
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | LN:115:129 | T:77&78 | 239 | 298 | 103.98
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 239 | 298 | 102.53
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | LN:115:133 | T:79&80 | 239 | 298 | 101.91
Dispatch 1 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | LN:115:129 | T:77&78 | 239 | 298 | 100.03
| 135469 SUMIT PK 115 135498 ZRMN-130 115 1 Max |  |  |  |  | 112.03
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 88 | 101 | NConv
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 88 | 101 | NConv
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 101 | NConv
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 88 | 101 | NConv
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 120.53
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | LN:115:142 | T:73&74 | 88 | 101 | 119.76
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | LN:115:142 | SB:DUNK230_R1312 | 88 | 101 | 119.57
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | LN:115:142 | SB:DUNK230_R1312 | 88 | 101 | 119.1
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 108.08
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | WTHRS - MEYER 230 | T:73&74 | 88 | 101 | 107.45
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 106.96
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 106.96
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | TB:3/2:FV | T:73&74 | 88 | 101 | 106.32
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | FARMVLY - FARMVLY | T:73&74 | 88 | 101 | 106.32
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 104.63
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | CANDQUA - STNYRDG 68A 230 | T:73&74 | 88 | 101 | 104.01
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 103.87
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 101 | 103.28
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | STONYCR - WTHRS 230 | T:73&74 | 88 | 101 | 103.23
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | LFYTE - CLARKCRNS 36A 345 | T:73&74 | 88 | 101 | 102.87
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:73&74 | 88 | 101 | 102.79
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | T:73&74 | 88 | 101 | 102.63
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | LFYTE - CLARKCRNS 36A 345 | T:73&74 | 88 | 101 | 102.29
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:73&74 | 88 | 101 | 102.2
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | LN:345:37S-FM-FV-HC | T:73&74 | 88 | 101 | 102.11
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | MEYER - CANDQUA 60 230 | T:73&74 | 88 | 101 | 101.26
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | HILLSIDE 230/115 4TR | T:73&74 | 88 | 101 | 101.19
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | LN:345:37S-FM-FV-HC | T:73&74 | 88 | 101 | 101.07
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | T:73&74 | 88 | 101 | 100.89
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | MEYER - CANDQUA 60 230 | T:73&74 | 88 | 101 | 100.65
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | LN:115:167 | T:73&74 | 88 | 101 | 100.64
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | HILLSIDE 230/115 4TR | T:73&74 | 88 | 101 | 100.63
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | 4 MILE - ERIE SE 230 | T:73&74 | 88 | 101 | 100.47
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | T:73&74 | 88 | 101 | 100.46
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | SHLDON - STONYCR 230 | T:73&74 | 88 | 101 | 100.45
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | G:JAMESGN7 | T:73&74 | 88 | 101 | 100.33
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | LN:115:167 | T:73&74 | 88 | 101 | 100
| 135475 S139-141 115 135483 S55-141 115 1 Max |  |  |  |  | 120.53
Dispatch 2 | 135477 S140-38 115 135481 S54-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 121.21
Dispatch 1 | 135477 S140-38 115 135481 S54-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 121
Dispatch 2 | 135477 S140-38 115 135481 S54-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 107.72
Dispatch 1 | 135477 S140-38 115 135481 S54-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 105.52
| 135477 S140-38 115 135481 S54-38 115 1 Max |  |  |  |  | 121.21
Dispatch 2 | 135478 S140-39 115 135482 S54-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 120.35
Dispatch 1 | 135478 S140-39 115 135482 S54-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 120.14
Dispatch 2 | 135478 S140-39 115 135482 S54-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 107
Dispatch 1 | 135478 S140-39 115 135482 S54-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 104.81
| 135478 S140-39 115 135482 S54-39 115 1 Max |  |  |  |  | 120.35
Dispatch 2 | 135479 S154-38 115 135485 S61-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 114.18
Dispatch 1 | 135479 S154-38 115 135485 S61-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 113.8
Dispatch 2 | 135479 S154-38 115 135485 S61-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 103.17
Dispatch 1 | 135479 S154-38 115 135485 S61-38 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 101.03
| 135479 S154-38 115 135485 S61-38 115 1 Max |  |  |  |  | 114.18
Dispatch 2 | 135479 S154-38 115 135492 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 113.26
Dispatch 1 | 135479 S154-38 115 135492 WALDENTP 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 112.86
Dispatch 2 | 135479 S154-38 115 135492 WALDENTP 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 102.61
Dispatch 1 | 135479 S154-38 115 135492 WALDENTP 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 100.47
| 135479 S154-38 115 135492 WALDENTP 115 1 Max |  |  |  |  | 113.26
Dispatch 2 | 135480 S154-39 115 135486 S61-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 113.12
Dispatch 1 | 135480 S154-39 115 135486 S61-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 112.73
Dispatch 2 | 135480 S154-39 115 135486 S61-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 102.31
Dispatch 1 | 135480 S154-39 115 135486 S61-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 100.17
| 135480 S154-39 115 135486 S61-39 115 1 Max |  |  |  |  | 113.12
Dispatch 2 | 135480 S154-39 115 135504 DALE-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 112.15
Dispatch 1 | 135480 S154-39 115 135504 DALE-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 111.74
Dispatch 2 | 135480 S154-39 115 135504 DALE-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 101.71
| 135480 S154-39 115 135504 DALE-39 115 1 Max |  |  |  |  | 112.15
Dispatch 2 | 135482 S54-39 115 135486 S61-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 116.58
Dispatch 1 | 135482 S54-39 115 135486 S61-39 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 116.28
Dispatch 2 | 135482 S54-39 115 135486 S61-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 104.53
Dispatch 1 | 135482 S54-39 115 135486 S61-39 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 174 | 181 | 102.37
| 135482 S54-39 115 135486 S61-39 115 1 Max |  |  |  |  | 116.58
Dispatch 2 | 135492 WALDENTP 115 135503 DALE-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 105.59
Dispatch 1 | 135492 WALDENTP 115 135503 DALE-38 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 174 | 181 | 105.05
| 135492 WALDENTP 115 135503 DALE-38 115 1 Max |  |  |  |  | 105.59
Dispatch 1 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 298 | NConv
Dispatch 1 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 1 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 298 | NConv
Dispatch 1 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 298 | NConv
Dispatch 1 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 239 | 298 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 239 | 298 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 239 | 298 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | LN:115:130 | T:77&78 | 239 | 298 | 113.8
Dispatch 1 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | LN:115:130 | T:77&78 | 239 | 298 | 109.87
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | LN:115:130 | Base Case | 239 | 298 | 107.93
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 239 | 298 | 104.38
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | LN:115:130 | T:79&80 | 239 | 298 | 103.76
Dispatch 1 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | LN:115:130 | Base Case | 239 | 298 | 101.58
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | LN:115:130 | SB:NIAW230_2014 | 239 | 298 | 101.13
Dispatch 1 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 239 | 298 | 100.38
| 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 Max |  |  |  |  | 113.8
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 168 | 185 | NConv
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 185 | NConv
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 168 | 185 | NConv
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 168 | 185 | NConv
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 185 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 168 | 185 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 185 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 168 | 185 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 168 | 185 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 185 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:77&78 | 168 | 185 | 152.64
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:77&78 | 168 | 185 | 146.68
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 168 | 185 | 139.27
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 168 | 185 | 138.18
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 168 | 185 | 137.17
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:79&80 | 168 | 185 | 137.14
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 185 | 136.26
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:NIAW230_2014 | 168 | 185 | 134.99
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 168 | 185 | 133.59
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 168 | 185 | 132.2
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA 230/115 2TR | 168 | 185 | 132.18
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:NI2 | 168 | 185 | 132.18
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | LN:115:130 | 168 | 185 | 132.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | LN:115:130 | 168 | 185 | 132.06
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:79&80 | 168 | 185 | 130.92
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 168 | 185 | 128.13
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R3430 | 168 | 185 | 127.67
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 185 | 126.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 168 | 185 | 126.11
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:61&64 | 168 | 185 | 125.84
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 168 | 185 | 125.39
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 168 | 185 | 125.28
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 168 | 185 | 125.14
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 168 | 185 | 124.77
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:ROBI230 | 168 | 185 | 124.49
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:77&78 | 168 | 185 | 124.46
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1502 | 168 | 185 | 123.55
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt68 | 168 | 185 | 123.54
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R3230 | 168 | 185 | 123.48
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:77&80 | 168 | 185 | 123.36
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:78&79 | 168 | 185 | 123.32
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1402 | 168 | 185 | 123.32
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 168 | 185 | 123.27
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R506 | 168 | 185 | 122.82
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 168 | 185 | 122.78
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 168 | 185 | 122.7
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:130 | 168 | 185 | 122.63
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:255_345B302 | 168 | 185 | 122.61
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:NIAG345_3108 | 168 | 185 | 122.43
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAG - NEWROCH 1 345 | 168 | 185 | 122.41
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:PACKT4 | 168 | 185 | 122.37
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | Base Case | 168 | 185 | 121.94
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_NEW | 168 | 185 | 121.92
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 168 | 185 | 121.67
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt67 | 168 | 185 | 121.2
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1302 | 168 | 185 | 120.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1202 | 168 | 185 | 120.93
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:255_345B202 | 168 | 185 | 120.87
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:PK4 | 168 | 185 | 120.84
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | PACKARD 230/115 4TR | 168 | 185 | 120.84
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SOMERSET - NEWROCH 1 345 | 168 | 185 | 120.8
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:PK4 | LN:115:130 | 168 | 185 | 120.72
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | LN:115:130 | 168 | 185 | 120.72
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:130 | 168 | 185 | 120.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:130 | 168 | 185 | 120.54
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 168 | 185 | 120.37
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL77 | 168 | 185 | 120.08
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL78 | 168 | 185 | 119.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 78 230 | 168 | 185 | 119.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 77 230 | 168 | 185 | 119.93
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 168 | 185 | 119.51
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:61&64 | 168 | 185 | 119.2
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI1 | T:77&78 | 168 | 185 | 118.81
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | T:77&78 | 168 | 185 | 118.81
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:908 NY | 168 | 185 | 118.59
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 168 | 185 | 118.56
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:908 NY | LN:115:130 | 168 | 185 | 118.55
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI1 | T:77&78 | 168 | 185 | 118.26
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | T:77&78 | 168 | 185 | 118.26
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:ROBI230 | 168 | 185 | 118.09
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 168 | 185 | 117.56
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:100 | 168 | 185 | 117.39
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | T:77&78 | 168 | 185 | 117.36
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:100 | LN:115:130 | 168 | 185 | 117.34
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R3230 | 168 | 185 | 117.24
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_R823 | 168 | 185 | 117.08
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:908 NY | T:77&78 | 168 | 185 | 117.07
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_R833 | 168 | 185 | 116.76
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:130 | 168 | 185 | 116.74
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:130 | 168 | 185 | 116.73
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_T7-12 | 168 | 185 | 116.65
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 185 | 116.65
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:GARD72&79 | 168 | 185 | 116.61
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 185 | 116.54
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | S:HNT_GRD80 | 168 | 185 | 116.52
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - GARDENVILL 79 230 | 168 | 185 | 116.43
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - GARDENVILL 80 230 | 168 | 185 | 116.42
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt68 | 168 | 185 | 116.27
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:ROB | 168 | 185 | 116.26
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:100 | T:77&78 | 168 | 185 | 116.2
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:ROB | LN:115:130 | 168 | 185 | 116.16
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_R873 | 168 | 185 | 116.16
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:77&80 | 168 | 185 | 116.14
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:182N | T:77&78 | 168 | 185 | 116.06
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1502 | 168 | 185 | 115.99
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:GARD73&80 | 168 | 185 | 115.82
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1402 | 168 | 185 | 115.79
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:78&79 | 168 | 185 | 115.79
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:180 | T:77&78 | 168 | 185 | 115.74
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:182S | T:77&78 | 168 | 185 | 115.66
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 168 | 185 | 115.48
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:181/922 | T:77&78 | 168 | 185 | 115.47
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 168 | 185 | 115.4
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:ROB | T:77&78 | 168 | 185 | 115.34
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 168 | 185 | 115.33
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | T:77&78 | 168 | 185 | 115.23
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:130 | 168 | 185 | 115.16
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:130 | 168 | 185 | 115.11
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:255_345B302 | 168 | 185 | 115.08
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 168 | 185 | 115.04
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 168 | 185 | 115.04
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | G:LOCKPORT | 168 | 185 | 115.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 168 | 185 | 115.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:STOLE230 | 168 | 185 | 115
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:LOCKPORT | T:77&78 | 168 | 185 | 114.92
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:NIAG345_3108 | 168 | 185 | 114.91
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:LOCKPORT | LN:115:130 | 168 | 185 | 114.9
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAG - NEWROCH 1 345 | 168 | 185 | 114.85
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:101 | 168 | 185 | 114.85
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:130 | 168 | 185 | 114.84
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 168 | 185 | 114.83
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | T:77&78 | 168 | 185 | 114.8
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | STOLLRD - GARDENVILL 66 230 | 168 | 185 | 114.77
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:101 | LN:115:130 | 168 | 185 | 114.71
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | T:77&78 | 168 | 185 | 114.67
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI1 | LN:115:130 | 168 | 185 | 114.62
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | LN:115:130 | 168 | 185 | 114.62
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | ROBINSON - STOLLRD 65 230 | 168 | 185 | 114.6
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:102 | 168 | 185 | 114.6
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:NI1 | 168 | 185 | 114.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA 230/115 1TR | 168 | 185 | 114.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:DUPONT46 | T:77&78 | 168 | 185 | 114.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:101 | T:77&78 | 168 | 185 | 114.55
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:102 | LN:115:130 | 168 | 185 | 114.46
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:345:37S-FM-FV | T:77&78 | 168 | 185 | 114.44
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 185 | 114.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 168 | 185 | 114.41
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:102 | T:77&78 | 168 | 185 | 114.38
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:907 NY | 168 | 185 | 114.38
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | First:Lockport_907 | 168 | 185 | 114.35
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | FARMVLY - HOMERCTY | 168 | 185 | 114.33
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_NEW | 168 | 185 | 114.31
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:907 NY | LN:115:130 | 168 | 185 | 114.3
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | R:HC-FV_37&W-F_171 | 168 | 185 | 114.28
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:120 | 168 | 185 | 114.26
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | First:Lockport_907 | LN:115:130 | 168 | 185 | 114.25
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:DUPONT46 | LN:115:130 | 168 | 185 | 114.25
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:120 | T:77&78 | 168 | 185 | 114.2
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:120 | LN:115:130 | 168 | 185 | 114.15
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:907 NY | T:77&78 | 168 | 185 | 114.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | First:Lockport_907 | T:77&78 | 168 | 185 | 113.99
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:37 | 168 | 185 | 113.94
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 168 | 185 | 113.92
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 168 | 185 | 113.88
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt67 | 168 | 185 | 113.87
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:37 | T:77&78 | 168 | 185 | 113.81
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:37 | LN:115:130 | 168 | 185 | 113.81
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_2T8082 | 168 | 185 | 113.74
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:36 | 168 | 185 | 113.67
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:908 NY | T:77&78 | 168 | 185 | 113.62
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | LN:115:130 | 168 | 185 | 113.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:36 | LN:115:130 | 168 | 185 | 113.53
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | PACKARD 230/115 3TR | 168 | 185 | 113.48
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | LN:115:130 | 168 | 185 | 113.46
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:40&41 | 168 | 185 | 113.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_34XC | 168 | 185 | 113.42
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1202 | 168 | 185 | 113.35
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:HUNT230_R1302 | 168 | 185 | 113.32
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:NIAG345_3308 | 168 | 185 | 113.32
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:130 | 168 | 185 | 113.25
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:PACKT3 | 168 | 185 | 113.23
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAG - KINTIGH 345 | 168 | 185 | 113.21
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:255_345B202 | 168 | 185 | 113.17
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 168 | 185 | 113.14
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SOMERSET - NEWROCH 1 345 | 168 | 185 | 113.09
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 168 | 185 | 113.07
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 185 | 113.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:KINT_39-B112 | 168 | 185 | 113.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 4 | LN:115:130 | 168 | 185 | 113.02
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 5 | LN:115:130 | 168 | 185 | 113.02
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 6 | LN:115:130 | 168 | 185 | 113.02
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 7 | LN:115:130 | 168 | 185 | 113.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:KINT_B1-3812 | 168 | 185 | 112.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_3414 | 168 | 185 | 112.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_3514 | 168 | 185 | 112.98
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | Base Case | 168 | 185 | 112.92
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:130 | 168 | 185 | 112.88
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:130 | 168 | 185 | 112.87
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:100 | T:77&78 | 168 | 185 | 112.86
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:130 | 168 | 185 | 112.83
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | LN:115:130 | 168 | 185 | 112.71
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | LN:115:130 | 168 | 185 | 112.7
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:182N | LN:115:130 | 168 | 185 | 112.69
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 168 | 185 | 112.44
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 168 | 185 | 112.44
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 168 | 185 | 112.44
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 168 | 185 | 112.44
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL77 | 168 | 185 | 112.32
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 168 | 185 | 112.23
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL78 | 168 | 185 | 112.21
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 78 230 | 168 | 185 | 112.21
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 168 | 185 | 112.17
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 77 230 | 168 | 185 | 112.16
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 168 | 185 | 112.06
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:ROB | T:77&78 | 168 | 185 | 111.99
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:908 NY | 168 | 185 | 111.55
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:182N | T:77&78 | 168 | 185 | 111.54
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:908 NY | LN:115:130 | 168 | 185 | 111.53
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | B:PACKT4 | 168 | 185 | 111.47
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | B:PACKT4 | 168 | 185 | 111.47
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | SB:PA230_R506 | 168 | 185 | 111.44
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | SB:PA230_R506 | 168 | 185 | 111.44
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:PK4 | NIAGARA 230/115 2TR | 168 | 185 | 111.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:PK4 | TB:2/1:NI2 | 168 | 185 | 111.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | PACKARD 230/115 4TR | 168 | 185 | 111.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | TB:2/1:PK4 | 168 | 185 | 111.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | PACKARD 230/115 4TR | 168 | 185 | 111.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | TB:2/1:PK4 | 168 | 185 | 111.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | NIAGARA 230/115 2TR | 168 | 185 | 111.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | TB:2/1:NI2 | 168 | 185 | 111.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | SB:PA230_R3430 | 168 | 185 | 111.41
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | SB:PA230_R3430 | 168 | 185 | 111.41
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 168 | 185 | 111.39
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:79&80 | 168 | 185 | 111.37
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 168 | 185 | 111.36
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:PK4 | SB:NIAW230_2014 | 168 | 185 | 111.31
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | SB:NIAW230_2014 | 168 | 185 | 111.31
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 168 | 185 | 111.29
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 168 | 185 | 111.24
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | T:77&78 | 168 | 185 | 111.21
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:NIAW230_2014 | 168 | 185 | 111.19
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:345:37S-FM-FV-HC | T:77&78 | 168 | 185 | 111.19
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:180 | T:77&78 | 168 | 185 | 111.14
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:182S | T:77&78 | 168 | 185 | 111.11
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R3430 | 168 | 185 | 111.04
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 168 | 185 | 111.04
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:181/922 | T:77&78 | 168 | 185 | 110.98
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-SR_37&W-F_171 | T:77&78 | 168 | 185 | 110.8
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:FV-5M_37&W-F_171 | T:77&78 | 168 | 185 | 110.8
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | T:77&78 | 168 | 185 | 110.7
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:907 NY | T:77&78 | 168 | 185 | 110.64
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | First:Lockport_907 | T:77&78 | 168 | 185 | 110.61
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:LOCKPORT | T:77&78 | 168 | 185 | 110.61
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 168 | 185 | 110.59
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 168 | 185 | 110.54
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 168 | 185 | 110.53
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:100 | 168 | 185 | 110.46
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:100 | LN:115:130 | 168 | 185 | 110.43
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | T:77&78 | 168 | 185 | 110.38
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:345:37S-FM-FV | T:77&78 | 168 | 185 | 110.33
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:DUPONT46 | T:77&78 | 168 | 185 | 110.22
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 168 | 185 | 110.15
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI1 | LN:115:130 | 168 | 185 | 110.11
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | LN:115:130 | 168 | 185 | 110.11
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA 230/115 1TR | 168 | 185 | 109.89
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:NI1 | 168 | 185 | 109.89
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:101 | T:77&78 | 168 | 185 | 109.85
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:102 | T:77&78 | 168 | 185 | 109.71
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | FARMVLY - 5MILE 345 | T:77&78 | 168 | 185 | 109.7
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:37 | T:77&78 | 168 | 185 | 109.67
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:120 | T:77&78 | 168 | 185 | 109.61
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | CAP:115:GV1 | T:77&78 | 168 | 185 | 109.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | CAP:115:GV2 | T:77&78 | 168 | 185 | 109.59
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:36 | T:77&78 | 168 | 185 | 109.5
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_R823 | 168 | 185 | 109.49
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 11 | T:77&78 | 168 | 185 | 109.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 12 | T:77&78 | 168 | 185 | 109.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 13 | T:77&78 | 168 | 185 | 109.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 8 | T:77&78 | 168 | 185 | 109.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 9 | T:77&78 | 168 | 185 | 109.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 10 | T:77&78 | 168 | 185 | 109.41
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:ROB | 168 | 185 | 109.32
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 168 | 185 | 109.32
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:ROB | LN:115:130 | 168 | 185 | 109.25
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_R833 | 168 | 185 | 109.17
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:130 | 168 | 185 | 108.96
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:130 | 168 | 185 | 108.94
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:GARD72&79 | 168 | 185 | 108.83
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_T7-12 | 168 | 185 | 108.83
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:113 | 168 | 185 | 108.72
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | S:HNT_GRD80 | 168 | 185 | 108.7
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:111 | 168 | 185 | 108.69
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 168 | 185 | 108.62
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - GARDENVILL 79 230 | 168 | 185 | 108.6
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | DUNKIRK - SRIPL 68 230 | 168 | 185 | 108.6
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:SRIPLEY | 168 | 185 | 108.6
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - GARDENVILL 80 230 | 168 | 185 | 108.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:UDG-184 | T:77&78 | 168 | 185 | 108.58
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:113 | LN:115:130 | 168 | 185 | 108.57
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | R:EESR/NWES | 168 | 185 | 108.57
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SRIPL - ERIE E 69 230 | 168 | 185 | 108.57
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:111 | LN:115:130 | 168 | 185 | 108.51
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:PK4 | T:77&78 | 168 | 185 | 108.5
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | T:77&78 | 168 | 185 | 108.5
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | WTHRS - MEYER 230 | T:77&78 | 168 | 185 | 108.49
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 168 | 185 | 108.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 168 | 185 | 108.41
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HCWC/NWES | T:77&78 | 168 | 185 | 108.4
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:MBWC/NWES | T:77&78 | 168 | 185 | 108.4
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:GARD230_R873 | 168 | 185 | 108.34
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:119 | 168 | 185 | 108.28
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 11 | LN:115:130 | 168 | 185 | 108.27
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 12 | LN:115:130 | 168 | 185 | 108.27
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 13 | LN:115:130 | 168 | 185 | 108.27
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 8 | LN:115:130 | 168 | 185 | 108.27
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 9 | LN:115:130 | 168 | 185 | 108.27
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 10 | LN:115:130 | 168 | 185 | 108.26
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 168 | 185 | 108.19
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 168 | 185 | 108.18
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 168 | 185 | 108.18
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 168 | 185 | 108.18
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:119 | LN:115:130 | 168 | 185 | 108.17
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 168 | 185 | 108.07
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | R:DKSR/WRFL | 168 | 185 | 108.02
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-WC_30&W-F_171 | LN:115:130 | 168 | 185 | 107.99
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:GARD73&80 | 168 | 185 | 107.98
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 168 | 185 | 107.98
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 168 | 185 | 107.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | R:EESR/WRFL | 168 | 185 | 107.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | R:EESR/WF/NWES | 168 | 185 | 107.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | WTRCR - MAINSBRG 30A 345 | LN:115:130 | 168 | 185 | 107.97
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HCWC/NWES | LN:115:130 | 168 | 185 | 107.97
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:MBWC/NWES | LN:115:130 | 168 | 185 | 107.97
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:MEYER | 168 | 185 | 107.96
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | WTHRS - MEYER 230 | 168 | 185 | 107.96
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 168 | 185 | 107.78
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:68&160 | 168 | 185 | 107.74
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HCMB/NWES | T:77&78 | 168 | 185 | 107.63
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 168 | 185 | 107.56
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HCMB/NWES | LN:115:130 | 168 | 185 | 107.4
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-MB_30&W-F_171 | LN:115:130 | 168 | 185 | 107.37
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | MAINSBRG - HOMERCITY 30B 345 | LN:115:130 | 168 | 185 | 107.34
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:907 NY | 168 | 185 | 107.33
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | First:Lockport_907 | 168 | 185 | 107.3
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:907 NY | LN:115:130 | 168 | 185 | 107.27
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | First:Lockport_907 | LN:115:130 | 168 | 185 | 107.23
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI1 | DCT:230:79+80+ELM1-2 | 168 | 185 | 107.2
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | DCT:230:79+80+ELM1-2 | 168 | 185 | 107.2
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:130 | 168 | 185 | 107.1
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:STOLE230 | 168 | 185 | 106.99
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:130 | 168 | 185 | 106.99
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 168 | 185 | 106.85
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 168 | 185 | 106.85
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | G:LOCKPORT | 168 | 185 | 106.84
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | LN:115:130 | 168 | 185 | 106.84
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 168 | 185 | 106.81
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 168 | 185 | 106.79
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | PACKARD 230/115 3TR | 168 | 185 | 106.78
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 168 | 185 | 106.76
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | STOLLRD - GARDENVILL 66 230 | 168 | 185 | 106.75
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:LOCKPORT | LN:115:130 | 168 | 185 | 106.73
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:908 NY | DCT:230:79+80+ELM1-2 | 168 | 185 | 106.73
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 168 | 185 | 106.7
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 168 | 185 | 106.65
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI1 | DCT:230:79+80+ELM1-2 | 168 | 185 | 106.6
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | DCT:230:79+80+ELM1-2 | 168 | 185 | 106.6
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 168 | 185 | 106.6
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 168 | 185 | 106.58
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | GEN:345:SOMERSET | T:77&78 | 168 | 185 | 106.58
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | GEN:KINTIGH | T:77&78 | 168 | 185 | 106.58
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | ROBINSON - STOLLRD 65 230 | 168 | 185 | 106.56
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:61&64 | 168 | 185 | 106.52
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:PACKT3 | 168 | 185 | 106.48
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3230 | 168 | 185 | 106.48
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI1 | T:79&80 | 168 | 185 | 106.39
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | T:79&80 | 168 | 185 | 106.39
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:77&80 | 168 | 185 | 106.33
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | B:Hunt68 | 168 | 185 | 106.29
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:DUPONT46 | LN:115:130 | 168 | 185 | 106.28
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 168 | 185 | 106.27
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 168 | 185 | 106.23
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:UDG-184 | LN:115:130 | 168 | 185 | 106.23
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | FARMVLY - HOMERCTY | 168 | 185 | 106.18
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:908 NY | T:79&80 | 168 | 185 | 106.18
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:101 | 168 | 185 | 106.17
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | GEN:KINTIGH | 168 | 185 | 106.16
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | GEN:345:SOMERSET | 168 | 185 | 106.16
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | R:HC-FV_37&W-F_171 | 168 | 185 | 106.14
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | CAP:115:HUN | 168 | 185 | 106.06
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:101 | LN:115:130 | 168 | 185 | 106.05
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1502 | 168 | 185 | 106.02
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | CAP:115:HUN | LN:115:130 | 168 | 185 | 105.99
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | DCT:230:79+80+ELM1-2 | 168 | 185 | 105.98
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:102 | 168 | 185 | 105.95
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | NIAGARA - ROBINSON 64 345 | 168 | 185 | 105.95
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R506 | 168 | 185 | 105.93
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:100 | DCT:230:79+80+ELM1-2 | 168 | 185 | 105.93
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1402 | 168 | 185 | 105.92
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:78&79 | 168 | 185 | 105.91
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:102 | LN:115:130 | 168 | 185 | 105.83
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:120 | 168 | 185 | 105.71
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:37 | 168 | 185 | 105.67
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | GEN:345:SOMERSET | LN:115:130 | 168 | 185 | 105.67
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | GEN:KINTIGH | LN:115:130 | 168 | 185 | 105.67
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | LN:115:130 | 168 | 185 | 105.65
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_2T8082 | 168 | 185 | 105.63
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:120 | LN:115:130 | 168 | 185 | 105.61
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:37 | LN:115:130 | 168 | 185 | 105.55
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI1 | T:79&80 | 168 | 185 | 105.49
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | T:79&80 | 168 | 185 | 105.49
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA 230/115 2TR | 168 | 185 | 105.48
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:NI2 | 168 | 185 | 105.48
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:ROBI230 | 168 | 185 | 105.47
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:PACKT4 | 168 | 185 | 105.46
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | LN:115:130 | 168 | 185 | 105.44
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | LN:115:130 | 168 | 185 | 105.44
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:PA230_R304 | 168 | 185 | 105.43
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:36 | 168 | 185 | 105.39
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:100 | T:79&80 | 168 | 185 | 105.37
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:NIAG345_3308 | 168 | 185 | 105.33
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | CAP:115:GV1 | T:77&78 | 168 | 185 | 105.31
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | CAP:115:GV2 | T:77&78 | 168 | 185 | 105.31
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_34XC | 168 | 185 | 105.31
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:36 | LN:115:130 | 168 | 185 | 105.27
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | T:40&41 | 168 | 185 | 105.26
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | DCT:230:79+80+ELM1-2 | 168 | 185 | 105.26
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | DCT:230:79+80+ELM1-2 | 168 | 185 | 105.26
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 168 | 185 | 105.23
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAG - KINTIGH 345 | 168 | 185 | 105.21
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | T:79&80 | 168 | 185 | 105.21
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:130 | 168 | 185 | 105.09
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:KINT_39-B112 | 168 | 185 | 105.05
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:ROB | DCT:230:79+80+ELM1-2 | 168 | 185 | 105.04
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:KINT_B1-3812 | 168 | 185 | 104.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 168 | 185 | 104.92
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 168 | 185 | 104.91
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_3414 | 168 | 185 | 104.86
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:ROCH_3514 | 168 | 185 | 104.86
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - ELM 70 230 | T:79&80 | 168 | 185 | 104.81
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | T:79&80 | 168 | 185 | 104.77
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | T:79&80 | 168 | 185 | 104.77
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 168 | 185 | 104.76
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 168 | 185 | 104.76
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:130 | 168 | 185 | 104.71
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | DCT:230:79+80+ELM1-2 | 168 | 185 | 104.68
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 168 | 185 | 104.65
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:345:37S-FM-FV-HC | 168 | 185 | 104.64
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:5MILE_B | 168 | 185 | 104.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:LOCKPORT | DCT:230:79+80+ELM1-2 | 168 | 185 | 104.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:39 | 168 | 185 | 104.58
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | LN:115:130 | 168 | 185 | 104.56
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | LN:115:130 | 168 | 185 | 104.54
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:38 | 168 | 185 | 104.54
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:39 | LN:115:130 | 168 | 185 | 104.53
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:ROB | T:79&80 | 168 | 185 | 104.49
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:38 | LN:115:130 | 168 | 185 | 104.49
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 168 | 185 | 104.45
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_NEW | 168 | 185 | 104.43
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-WC_30&W-F_171 | T:77&78 | 168 | 185 | 104.39
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:182N | T:79&80 | 168 | 185 | 104.39
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:UDG-184 | T:77&78 | 168 | 185 | 104.28
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | WTHRS - MEYER 230 | T:77&78 | 168 | 185 | 104.26
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:DUPONT46 | DCT:230:79+80+ELM1-2 | 168 | 185 | 104.24
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:101 | DCT:230:79+80+ELM1-2 | 168 | 185 | 104.23
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 11 | T:77&78 | 168 | 185 | 104.18
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 12 | T:77&78 | 168 | 185 | 104.18
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 13 | T:77&78 | 168 | 185 | 104.18
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 168 | 185 | 104.18
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 8 | T:77&78 | 168 | 185 | 104.17
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 9 | T:77&78 | 168 | 185 | 104.17
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:255_345B302 | 168 | 185 | 104.17
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 168 | 185 | 104.16
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HCWC/NWES | T:77&78 | 168 | 185 | 104.16
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:MBWC/NWES | T:77&78 | 168 | 185 | 104.16
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 10 | T:77&78 | 168 | 185 | 104.16
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 168 | 185 | 104.16
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | G:BRUCE5 | 168 | 185 | 104.13
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:NIAG345_3108 | 168 | 185 | 104.08
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:102 | DCT:230:79+80+ELM1-2 | 168 | 185 | 104.07
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:180 | T:79&80 | 168 | 185 | 104.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_NEW | 168 | 185 | 104.06
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3230 | 168 | 185 | 104.05
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:LOCKPORT | T:79&80 | 168 | 185 | 104.03
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 168 | 185 | 104.02
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | T:79&80 | 168 | 185 | 104.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | NIAG - NEWROCH 1 345 | 168 | 185 | 103.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:181/922 | T:79&80 | 168 | 185 | 103.97
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:61&64 | 168 | 185 | 103.97
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:182S | T:79&80 | 168 | 185 | 103.94
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:120 | DCT:230:79+80+ELM1-2 | 168 | 185 | 103.91
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | B:Hunt67 | 168 | 185 | 103.86
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1202 | 168 | 185 | 103.83
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:907 NY | DCT:230:79+80+ELM1-2 | 168 | 185 | 103.81
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | First:Lockport_907 | DCT:230:79+80+ELM1-2 | 168 | 185 | 103.79
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3230 | 168 | 185 | 103.73
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | T:79&80 | 168 | 185 | 103.71
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:DUPONT46 | T:79&80 | 168 | 185 | 103.69
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:101 | T:79&80 | 168 | 185 | 103.68
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | G:DARLIN1 | 168 | 185 | 103.64
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:345:37S-FM-FV-HC | DCT:230:79+80+ELM1-2 | 168 | 185 | 103.64
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1302 | 168 | 185 | 103.64
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | B:Hunt68 | 168 | 185 | 103.61
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:77&80 | 168 | 185 | 103.61
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-MB_30&W-F_171 | T:77&78 | 168 | 185 | 103.55
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:102 | T:79&80 | 168 | 185 | 103.52
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HC-FV_37&W-F_171 | T:79&80 | 168 | 185 | 103.51
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | NIAGARA - ROBINSON 64 345 | 168 | 185 | 103.46
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | DCT:230:79+80+ELM1-2 | 168 | 185 | 103.44
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | R:HCMB/NWES | T:77&78 | 168 | 185 | 103.39
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:120 | T:79&80 | 168 | 185 | 103.35
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | FARMVLY - HOMERCTY | T:79&80 | 168 | 185 | 103.35
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:908 NY | DCT:230:79+80+ELM1-2 | 168 | 185 | 103.31
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1502 | 168 | 185 | 103.31
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 168 | 185 | 103.3
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:907 NY | T:79&80 | 168 | 185 | 103.25
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | First:Lockport_907 | T:79&80 | 168 | 185 | 103.22
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1402 | 168 | 185 | 103.18
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:78&79 | 168 | 185 | 103.18
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | SB:255_345B302 | 168 | 185 | 103.12
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | NIAG - NEWROCH 1 345 | 168 | 185 | 103.05
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:345:37S-FM-FV-HC | T:79&80 | 168 | 185 | 103
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | Base Case | 168 | 185 | 102.99
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:ROBI230 | 168 | 185 | 102.96
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 168 | 185 | 102.91
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | SB:NIAG345_3108 | 168 | 185 | 102.88
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | Base Case | 168 | 185 | 102.83
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:100 | DCT:230:79+80+ELM1-2 | 168 | 185 | 102.61
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:77&80 | 168 | 185 | 102.61
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:908 NY | T:79&80 | 168 | 185 | 102.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 168 | 185 | 102.55
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL77 | 168 | 185 | 102.54
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | B:Hunt68 | 168 | 185 | 102.53
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 78 230 | 168 | 185 | 102.5
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL78 | 168 | 185 | 102.5
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | T:61&64 | 168 | 185 | 102.5
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 168 | 185 | 102.48
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 168 | 185 | 102.47
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:255_345B202 | 168 | 185 | 102.47
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 168 | 185 | 102.46
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 77 230 | 168 | 185 | 102.45
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 168 | 185 | 102.43
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 168 | 185 | 102.41
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SOMERSET - NEWROCH 1 345 | 168 | 185 | 102.41
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | T:79&80 | 168 | 185 | 102.4
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 345 | 168 | 185 | 102.38
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 345 | 168 | 185 | 102.32
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | T:61&64 | 168 | 185 | 102.31
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1502 | 168 | 185 | 102.26
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | GEN:345:SOMERSET | T:77&78 | 168 | 185 | 102.25
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | GEN:KINTIGH | T:77&78 | 168 | 185 | 102.25
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 168 | 185 | 102.22
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1402 | 168 | 185 | 102.21
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | T:78&79 | 168 | 185 | 102.21
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 168 | 185 | 102.16
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_NEW | 168 | 185 | 102.05
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:100 | T:79&80 | 168 | 185 | 101.89
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:77&80 | 168 | 185 | 101.84
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:OXBOWNUG | T:77&78 | 168 | 185 | 101.74
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | B:Hunt68 | 168 | 185 | 101.73
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:ROB | DCT:230:79+80+ELM1-2 | 168 | 185 | 101.72
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | T:78&79 | 168 | 185 | 101.7
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | T:77&80 | 168 | 185 | 101.69
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | NIAGARA - ROBINSON 64 345 | 168 | 185 | 101.66
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | B:Hunt67 | 168 | 185 | 101.65
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 168 | 185 | 101.64
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R823 | 168 | 185 | 101.64
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 168 | 185 | 101.62
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:OXBOWNUG | LN:115:130 | 168 | 185 | 101.55
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3230 | 168 | 185 | 101.47
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1202 | 168 | 185 | 101.46
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:ROBI230 | 168 | 185 | 101.44
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1302 | 168 | 185 | 101.39
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 168 | 185 | 101.39
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_R1202 | 168 | 185 | 101.39
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1402 | 168 | 185 | 101.38
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 168 | 185 | 101.34
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | B:GARD72&79 | 168 | 185 | 101.33
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | S:HNT_GRD80 | 168 | 185 | 101.32
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - GARDENVILL 80 230 | 168 | 185 | 101.32
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R833 | 168 | 185 | 101.32
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - GARDENVILL 79 230 | 168 | 185 | 101.32
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:NIAW230_2014 | 168 | 185 | 101.29
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3430 | 168 | 185 | 101.18
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1502 | 168 | 185 | 101.15
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:GARD230_R823 | 168 | 185 | 101.09
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | T:78&79 | 168 | 185 | 101.04
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1402 | 168 | 185 | 101.03
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:ROB | T:79&80 | 168 | 185 | 101
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SB:NIAW230_2014 | 168 | 185 | 100.97
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | B:Hunt67 | 168 | 185 | 100.89
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | B:Hunt68 | 168 | 185 | 100.89
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | Base Case | 168 | 185 | 100.88
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:GARD230_R833 | 168 | 185 | 100.83
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:GARD230_R873 | 168 | 185 | 100.76
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:182N | DCT:230:79+80+ELM1-2 | 168 | 185 | 100.73
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_R1302 | 168 | 185 | 100.72
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1502 | 168 | 185 | 100.72
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | DCT:230:79+80+ELM1-2 | 168 | 185 | 100.65
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 168 | 185 | 100.64
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_NEW | 168 | 185 | 100.62
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 168 | 185 | 100.6
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 168 | 185 | 100.55
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 168 | 185 | 100.55
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - ELM 70 230 | T:79&80 | 168 | 185 | 100.51
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 168 | 185 | 100.51
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | B:GARD73&80 | 168 | 185 | 100.47
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:907 NY | DCT:230:79+80+ELM1-2 | 168 | 185 | 100.43
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | First:Lockport_907 | DCT:230:79+80+ELM1-2 | 168 | 185 | 100.41
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | DUNKIRK - SRIPL 68 230 | 168 | 185 | 100.4
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SB:SRIPLEY | 168 | 185 | 100.4
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | R:EESR/NWES | 168 | 185 | 100.37
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SRIPL - ERIE E 69 230 | 168 | 185 | 100.37
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:180 | DCT:230:79+80+ELM1-2 | 168 | 185 | 100.36
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:181/922 | DCT:230:79+80+ELM1-2 | 168 | 185 | 100.29
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:LOCKPORT | DCT:230:79+80+ELM1-2 | 168 | 185 | 100.29
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:119 | 168 | 185 | 100.28
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:182S | DCT:230:79+80+ELM1-2 | 168 | 185 | 100.26
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:119 | LN:115:130 | 168 | 185 | 100.18
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 168 | 185 | 100.18
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1202 | 168 | 185 | 100.1
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | SB:255_345B302 | 168 | 185 | 100.03
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | B:Hunt67 | 168 | 185 | 100.02
| 135497 ZRMN-133 115 135562 S214-133 115 1 Max |  |  |  |  | 152.64
Dispatch 1 | 147841 NIAGAR2E 230 147834 NIAG 345 345 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 384 | 479 | NConv
Dispatch 2 | 147841 NIAGAR2E 230 147834 NIAG 345 345 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 384 | 479 | NConv
| 147841 NIAGAR2E 230 147834 NIAG 345 345 1 Max |  |  |  |  | 0
Dispatch 1 | 147841 NIAGAR2E 230 147834 NIAG 345 345 2 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 384 | 479 | NConv
Dispatch 2 | 147841 NIAGAR2E 230 147834 NIAG 345 345 2 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 384 | 479 | NConv
| 147841 NIAGAR2E 230 147834 NIAG 345 345 2 Max |  |  |  |  | 0
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 192 | 239 | NConv
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 192 | 239 | NConv
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 192 | 239 | NConv
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 192 | 239 | NConv
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 192 | 239 | NConv
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:255_345B302 | 192 | 239 | NConv
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 192 | 239 | NConv
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:NIAG345_3108 | 192 | 239 | NConv
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:255_345B202 | 192 | 239 | NConv
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 192 | 239 | NConv
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 192 | 239 | 192.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 192 | 239 | 190.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | T:62&BP76 | 192 | 239 | 175.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:77&78 | 192 | 239 | 167.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 164.45
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:61&64 | 192 | 239 | 163.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 192 | 239 | 160.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 192 | 239 | 160.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:77&78 | 192 | 239 | 159.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3230 | 192 | 239 | 159.16
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 192 | 239 | 157.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 192 | 239 | 155.8
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 192 | 239 | 151.8
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 192 | 239 | 150.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3230 | 192 | 239 | 147.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:77&78 | 192 | 239 | 144.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:77&78 | 192 | 239 | 144.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:77&78 | 192 | 239 | 144.79
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:77&78 | 192 | 239 | 144.75
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:77&78 | 192 | 239 | 144.74
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | DCT:230:79+80+ELM1-2 | 192 | 239 | 143.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | T:77&78 | 192 | 239 | 142.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:61&64 | 192 | 239 | 142.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:79&80 | 192 | 239 | 141.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 141.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | T:77&78 | 192 | 239 | 141.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3230 | 192 | 239 | 140.36
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 192 | 239 | 140.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 192 | 239 | 140.06
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R506 | 192 | 239 | 140.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:79&80 | 192 | 239 | 139.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | T:77&78 | 192 | 239 | 138.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | T:77&78 | 192 | 239 | 137.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | T:77&78 | 192 | 239 | 136.82
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | T:77&78 | 192 | 239 | 135.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:61&64 | 192 | 239 | 135.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R304 | 192 | 239 | 135.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:PA230_R3230 | 192 | 239 | 135.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:PA230_R3230 | 192 | 239 | 135.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:PA230_R3230 | 192 | 239 | 135.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:PA230_R3230 | 192 | 239 | 135.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | T:77&78 | 192 | 239 | 134.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:PA230_R3230 | 192 | 239 | 134.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | T:77&78 | 192 | 239 | 134.74
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | B:PACKT3 | 192 | 239 | 134.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 134.07
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 134.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | T:77&78 | 192 | 239 | 133.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 133.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:ROBI230 | 192 | 239 | 133.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:61&64 | 192 | 239 | 132.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | T:77&78 | 192 | 239 | 132.74
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:79&80 | 192 | 239 | 132.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:PA230_R3230 | 192 | 239 | 132.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 192 | 239 | 131.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | T:77&78 | 192 | 239 | 131.39
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:77&78 | 192 | 239 | 131.35
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | T:77&78 | 192 | 239 | 131.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:NIAG345_3308 | 192 | 239 | 131.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | T:77&78 | 192 | 239 | 130.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | T:77&78 | 192 | 239 | 130.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | T:77&78 | 192 | 239 | 130.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:77&78 | 192 | 239 | 130.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R304 | 192 | 239 | 130.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | PACKARD 230/115 3TR | 192 | 239 | 130.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:255_345B302 | 192 | 239 | 129.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 192 | 239 | 129.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:NIAG345_3108 | 192 | 239 | 129.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV-HC | T:77&78 | 192 | 239 | 129.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | NIAG - NEWROCH 1 345 | 192 | 239 | 129.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | SB:PA230_R3230 | 192 | 239 | 129.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 129.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | T:77&78 | 192 | 239 | 129.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:79&80 | 192 | 239 | 129.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:NI2 | T:77&78 | 192 | 239 | 129.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | T:77&78 | 192 | 239 | 129.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_104 | T:77&78 | 192 | 239 | 128.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | T:77&78 | 192 | 239 | 128.88
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV | T:77&78 | 192 | 239 | 128.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | NIAGARA - ROBINSON 64 345 | 192 | 239 | 128.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:AMERT | T:77&78 | 192 | 239 | 128.36
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:PK4 | T:77&78 | 192 | 239 | 128.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | T:77&78 | 192 | 239 | 128.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R3230 | 192 | 239 | 127.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_103 | T:77&78 | 192 | 239 | 127.74
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:BLISS1 | T:77&78 | 192 | 239 | 127.72
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 127.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:77&80 | 192 | 239 | 127.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | B:Hunt68 | 192 | 239 | 127.53
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | DCT:230:79+80+ELM1-2 | 192 | 239 | 127.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | DCT:230:79+80+ELM1-2 | 192 | 239 | 127.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | DCT:230:79+80+ELM1-2 | 192 | 239 | 127.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | DCT:230:79+80+ELM1-2 | 192 | 239 | 127.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1502 | 192 | 239 | 127.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:ROBI230 | 192 | 239 | 127.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:78&79 | 192 | 239 | 127.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1402 | 192 | 239 | 127.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 192 | 239 | 126.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 192 | 239 | 126.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 192 | 239 | 126.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 192 | 239 | 126.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:61&64 | 192 | 239 | 126.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:61&64 | 192 | 239 | 126.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:61&64 | 192 | 239 | 126.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:61&64 | 192 | 239 | 126.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | PACKARD 230/115 3TR | 192 | 239 | 126.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:ROBI230 | 192 | 239 | 126.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | Base Case | 192 | 239 | 126.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:79&80 | 192 | 239 | 126
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:79&80 | 192 | 239 | 126
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:79&80 | 192 | 239 | 126
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:79&80 | 192 | 239 | 125.94
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:79&80 | 192 | 239 | 125.75
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | T:77&80 | 192 | 239 | 125.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | T:78&79 | 192 | 239 | 125.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | T:61&64 | 192 | 239 | 125.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | T:61&64 | 192 | 239 | 125.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | DCT:230:79+80+ELM1-2 | 192 | 239 | 125.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:255_345B202 | 192 | 239 | 125.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 124.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | SB:255_345B302 | 192 | 239 | 124.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | NIAG - NEWROCH 1 345 | 192 | 239 | 124.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R304 | 192 | 239 | 124.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | SB:PA230_R3230 | 192 | 239 | 124.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | SB:PA230_R3230 | 192 | 239 | 124.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 192 | 239 | 124.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | Base Case | 192 | 239 | 124.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | SB:NIAG345_3108 | 192 | 239 | 124.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_NEW | 192 | 239 | 123.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | T:79&80 | 192 | 239 | 123.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | DCT:230:79+80+ELM1-2 | 192 | 239 | 123.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R3230 | 192 | 239 | 123.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | T:77&78 | 192 | 239 | 123.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | T:77&78 | 192 | 239 | 123.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 7-9 | T:77&78 | 192 | 239 | 123.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 10-12 | T:77&78 | 192 | 239 | 123.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 1-3 | T:77&78 | 192 | 239 | 123.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 4-6 | T:77&78 | 192 | 239 | 123.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:OSWEGO 5 | T:77&78 | 192 | 239 | 123.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | B:Hunt67 | 192 | 239 | 123.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | T:77&78 | 192 | 239 | 123.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R3230 | 192 | 239 | 123.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 1 | T:77&78 | 192 | 239 | 122.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 2 | T:77&78 | 192 | 239 | 122.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 3 | T:77&78 | 192 | 239 | 122.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:OSWEGO 6 | T:77&78 | 192 | 239 | 122.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1202 | 192 | 239 | 122.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CAP:115:GV1 | T:77&78 | 192 | 239 | 122.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CAP:115:GV2 | T:77&78 | 192 | 239 | 122.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:9MIPT1 | T:77&78 | 192 | 239 | 122.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3430 | 192 | 239 | 122.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | T:79&80 | 192 | 239 | 122.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:HUNT230_R1302 | 192 | 239 | 122.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:FITZPATR | T:77&78 | 192 | 239 | 122.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | SB:PA230_R3230 | 192 | 239 | 121.88
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:GINNA | T:77&78 | 192 | 239 | 121.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:GINNA | T:77&78 | 192 | 239 | 121.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:114 | T:77&78 | 192 | 239 | 121.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:113 | T:77&78 | 192 | 239 | 121.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:111 | T:77&78 | 192 | 239 | 121.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:119 | T:77&78 | 192 | 239 | 121.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | SB:PA230_R3230 | 192 | 239 | 121.45
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | T:62&BP76 | 192 | 239 | 121.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:255_345B302 | 192 | 239 | 121.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | LN:115:908 NY | 192 | 239 | 121.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | PACKARD 230/115 3TR | 192 | 239 | 121.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | DCT:230:79+80+ELM1-2 | 192 | 239 | 120.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | SB:PA230_R3230 | 192 | 239 | 120.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:NIAG345_3108 | 192 | 239 | 120.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:PA230_R304 | 192 | 239 | 120.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:PA230_R304 | 192 | 239 | 120.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:PA230_R304 | 192 | 239 | 120.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:PA230_R304 | 192 | 239 | 120.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R3430 | 192 | 239 | 120.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | NIAG - NEWROCH 1 345 | 192 | 239 | 120.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | T:77&78 | 192 | 239 | 120.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | SB:PA230_R3230 | 192 | 239 | 120.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | B:PACKT3 | 192 | 239 | 120.31
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | B:PACKT3 | 192 | 239 | 120.31
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | B:PACKT3 | 192 | 239 | 120.31
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | T:77&78 | 192 | 239 | 120.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | B:PACKT3 | 192 | 239 | 120.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | LN:115:100 | 192 | 239 | 119.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL77 | 192 | 239 | 119.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCWC/NWES | T:77&78 | 192 | 239 | 119.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:MBWC/NWES | T:77&78 | 192 | 239 | 119.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | T:77&78 | 192 | 239 | 119.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 78 230 | 192 | 239 | 119.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL78 | 192 | 239 | 119.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | T:79&80 | 192 | 239 | 119.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - PACKARD 77 230 | 192 | 239 | 119.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:PA230_R304 | 192 | 239 | 119.63
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 119.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 119.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 119.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 119.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | SB:PA230_R3230 | 192 | 239 | 119.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lancaster_922 | T:77&78 | 192 | 239 | 119.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 119.37
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:77&78 | 192 | 239 | 119.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:9 MI PT2 | T:77&78 | 192 | 239 | 119.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 119.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | B:PACKT3 | 192 | 239 | 119.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | B:PACKT3 | 192 | 239 | 119.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | DCT:230:79+80+ELM1-2 | 192 | 239 | 118.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | T:77&78 | 192 | 239 | 118.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | Base Case | 192 | 239 | 118.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | T:61&64 | 192 | 239 | 118.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | T:61&64 | 192 | 239 | 118.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCMB/NWES | T:77&78 | 192 | 239 | 118.53
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | DCT:230:79+80+ELM1-2 | 192 | 239 | 118.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:ROBI230 | 192 | 239 | 118.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:ROBI230 | 192 | 239 | 118.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:ROBI230 | 192 | 239 | 118.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:Hunt68 | 192 | 239 | 118.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:ROBI230 | 192 | 239 | 118.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | T:77&78 | 192 | 239 | 118.36
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | SB:PA230_R3430 | 192 | 239 | 118.3
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 118.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:77&80 | 192 | 239 | 118.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1502 | 192 | 239 | 118.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:GARD230_R823 | 192 | 239 | 118.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1402 | 192 | 239 | 118.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:78&79 | 192 | 239 | 118.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:GARD230_R833 | 192 | 239 | 117.59
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | DCT:230:79+80+ELM1-2 | 192 | 239 | 117.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | PACKARD 230/115 3TR | 192 | 239 | 117.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | PACKARD 230/115 3TR | 192 | 239 | 117.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | PACKARD 230/115 3TR | 192 | 239 | 117.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | PACKARD 230/115 3TR | 192 | 239 | 117.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | DCT:230:79+80+ELM1-2 | 192 | 239 | 117.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | DCT:230:79+80+ELM1-2 | 192 | 239 | 117.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | TB:2/1:ROB | 192 | 239 | 117.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 11 | T:77&78 | 192 | 239 | 117.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 12 | T:77&78 | 192 | 239 | 117.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 13 | T:77&78 | 192 | 239 | 117.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | T:79&80 | 192 | 239 | 117.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 8 | T:77&78 | 192 | 239 | 117.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 9 | T:77&78 | 192 | 239 | 117.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_NEW | 192 | 239 | 117.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 10 | T:77&78 | 192 | 239 | 117.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1302 | 192 | 239 | 117.16
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:HUNT230_R1202 | 192 | 239 | 117.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:PA230_R304 | 192 | 239 | 117.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1402 | 192 | 239 | 117.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:HUNT230_R1502 | 192 | 239 | 117.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | B:Hunt68 | 192 | 239 | 117.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:255_345B202 | 192 | 239 | 116.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | Base Case | 192 | 239 | 116.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R3230 | 192 | 239 | 116.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | T:79&80 | 192 | 239 | 116.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:77&80 | 192 | 239 | 116.88
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SOMERSET - NEWROCH 1 345 | 192 | 239 | 116.82
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 192 | 239 | 116.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | B:PACKT3 | 192 | 239 | 116.75
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 192 | 239 | 116.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | T:61&64 | 192 | 239 | 116.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R3230 | 192 | 239 | 116.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | T:61&64 | 192 | 239 | 116.43
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:ROBI230 | 192 | 239 | 116.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | SB:PA230_R3230 | 192 | 239 | 116.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | LN:115:908 NY | 192 | 239 | 116.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:ROBI230 | 192 | 239 | 116.28
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:77&78 | 192 | 239 | 116.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | PACKARD 230/115 3TR | 192 | 239 | 116.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:HUNT230_R1502 | 192 | 239 | 116.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | T:79&80 | 192 | 239 | 116.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R3230 | 192 | 239 | 116.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | T:61&64 | 192 | 239 | 116.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | T:79&80 | 192 | 239 | 116.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | T:79&80 | 192 | 239 | 115.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_NEW | 192 | 239 | 115.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 115.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:255_345B302 | 192 | 239 | 115.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | T:78&79 | 192 | 239 | 115.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:HUNT230_R1402 | 192 | 239 | 115.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:AMERT | SB:PA230_R3230 | 192 | 239 | 115.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_104 | SB:PA230_R3230 | 192 | 239 | 115.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | B:PACKT4 | 192 | 239 | 115.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | LN:115:908 NY | 192 | 239 | 115.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:NIAG345_3108 | 192 | 239 | 115.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R3430 | 192 | 239 | 115.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | SB:PA230_R3230 | 192 | 239 | 115.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | NIAG - NEWROCH 1 345 | 192 | 239 | 115.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | DCT:230:79+80+ELM1-2 | 192 | 239 | 115.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | Base Case | 192 | 239 | 115.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | Base Case | 192 | 239 | 115.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | Base Case | 192 | 239 | 115.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | T:62&PA27 | 192 | 239 | 115.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | Base Case | 192 | 239 | 115.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | T:61&64 | 192 | 239 | 115.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:Hunt67 | 192 | 239 | 115.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1202 | 192 | 239 | 115.07
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:120 | T:77&78 | 192 | 239 | 115.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | T:61&64 | 192 | 239 | 114.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:HUNT230_R1302 | 192 | 239 | 114.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_103 | SB:PA230_R3230 | 192 | 239 | 114.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R3230 | 192 | 239 | 114.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R3230 | 192 | 239 | 114.63
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | LN:115:100 | 192 | 239 | 114.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:102 | T:77&78 | 192 | 239 | 114.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | NIAGARA - PACKARD 62 230 | 192 | 239 | 114.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - PACKARD 61 230 | 192 | 239 | 114.57
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:79&80 | 192 | 239 | 114.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | T:79&80 | 192 | 239 | 114.45
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:255_345B302 | 192 | 239 | 114.36
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:110 | SB:PA230_R3230 | 192 | 239 | 114.31
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | SB:PA230_R3230 | 192 | 239 | 114.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | SB:PA230_R3230 | 192 | 239 | 114.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV-HC | SB:PA230_R3230 | 192 | 239 | 114.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:NI2 | SB:PA230_R3230 | 192 | 239 | 114.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | SB:PA230_R3230 | 192 | 239 | 114.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | SB:PA230_R304 | 192 | 239 | 114.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | T:79&80 | 192 | 239 | 114.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:NIAG345_3108 | 192 | 239 | 114
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 113.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:101 | T:77&78 | 192 | 239 | 113.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | LN:115:100 | 192 | 239 | 113.82
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | NIAG - NEWROCH 1 345 | 192 | 239 | 113.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | SB:PA230_R3230 | 192 | 239 | 113.75
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | B:PACKT3 | 192 | 239 | 113.74
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | PACKARD 230/115 3TR | 192 | 239 | 113.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:MODERNLF | SB:PA230_R3230 | 192 | 239 | 113.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:HOORKN85 | SB:PA230_R3230 | 192 | 239 | 113.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:HOORKN86 | SB:PA230_R3230 | 192 | 239 | 113.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - ELM 70 230 | T:79&80 | 192 | 239 | 113.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:BLISS1 | SB:PA230_R3230 | 192 | 239 | 113.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:HUNT230_NEW | 192 | 239 | 113.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | S:HNT_GRD80 | 192 | 239 | 113.36
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 192 | 239 | 113.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL78 | 192 | 239 | 113.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | S:PA_HNTL77 | 192 | 239 | 113.31
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 192 | 239 | 113.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:255_345B302 | 192 | 239 | 113.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:255_345B302 | 192 | 239 | 113.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:255_345B302 | 192 | 239 | 113.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - GARDENVILL 79 230 | 192 | 239 | 113.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:255_345B302 | 192 | 239 | 113.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | B:GARD72&79 | 192 | 239 | 113.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | HUNTLEY - GARDENVILL 80 230 | 192 | 239 | 113.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | DCT:230:79+80+ELM1-2 | 192 | 239 | 113.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 113.16
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:PA230_R304 | 192 | 239 | 113.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | LN:115:907 NY | 192 | 239 | 113.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | B:PACKT3 | 192 | 239 | 113.02
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R304 | 192 | 239 | 112.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | First:Lockport_907 | 192 | 239 | 112.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | DCT:230:79+80+ELM1-2 | 192 | 239 | 112.94
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | B:PACKT3 | 192 | 239 | 112.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | NIAG - NEWROCH 1 345 | 192 | 239 | 112.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | NIAG - NEWROCH 1 345 | 192 | 239 | 112.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | NIAG - NEWROCH 1 345 | 192 | 239 | 112.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:NIAG345_3108 | 192 | 239 | 112.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:NIAG345_3108 | 192 | 239 | 112.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:NIAG345_3108 | 192 | 239 | 112.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | NIAG - NEWROCH 1 345 | 192 | 239 | 112.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:NIAG345_3108 | 192 | 239 | 112.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1502 | 192 | 239 | 112.72
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:GARD230_R873 | 192 | 239 | 112.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | B:Hunt67 | 192 | 239 | 112.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:Hunt68 | 192 | 239 | 112.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1402 | 192 | 239 | 112.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:78&79 | 192 | 239 | 112.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | T:79&80 | 192 | 239 | 112.35
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | T:61&64 | 192 | 239 | 112.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:77&80 | 192 | 239 | 112.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 112.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 112.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:PK3 | T:77&78 | 192 | 239 | 112.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | Base Case | 192 | 239 | 112.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_NEW | 192 | 239 | 112.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | G:LOCKPORT | 192 | 239 | 112
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:255_345B202 | 192 | 239 | 111.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | B:GARD73&80 | 192 | 239 | 111.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | TB:2/1:ROB | 192 | 239 | 111.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:HUNT230_R1202 | 192 | 239 | 111.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SOMERSET - NEWROCH 1 345 | 192 | 239 | 111.81
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:61&64 | 192 | 239 | 111.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:HUNT230_R1302 | 192 | 239 | 111.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | SB:255_345B302 | 192 | 239 | 111.77
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | T:79&80 | 192 | 239 | 111.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_104 | DCT:230:79+80+ELM1-2 | 192 | 239 | 111.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:79&80 | 192 | 239 | 111.59
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | DCT:230:79+80+ELM1-2 | 192 | 239 | 111.56
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | DCT:230:79+80+ELM1-2 | 192 | 239 | 111.56
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | DCT:230:79+80+ELM1-2 | 192 | 239 | 111.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | T:79&80 | 192 | 239 | 111.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | T:61&64 | 192 | 239 | 111.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | SB:NIAG345_3108 | 192 | 239 | 111.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_104 | T:61&64 | 192 | 239 | 111.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lancaster_GRDN_GRDN_230 | T:61&64 | 192 | 239 | 111.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R506 | 192 | 239 | 111.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | NIAG - NEWROCH 1 345 | 192 | 239 | 111.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:345:SOMERSET | T:77&78 | 192 | 239 | 111.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:KINTIGH | T:77&78 | 192 | 239 | 111.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | PACKARD 230/115 3TR | 192 | 239 | 111.06
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:77&78 | 192 | 239 | 111.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:AMERT | DCT:230:79+80+ELM1-2 | 192 | 239 | 111
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | PACKARD 230/115 3TR | 192 | 239 | 110.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV-HC | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | TB:2/1:ROB | 192 | 239 | 110.9
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:77&78 | 192 | 239 | 110.9
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:77&78 | 192 | 239 | 110.9
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:77&78 | 192 | 239 | 110.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:NI2 | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - ELM 70 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.87
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:62&BP76 | 192 | 239 | 110.84
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:77&78 | 192 | 239 | 110.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | T:61&64 | 192 | 239 | 110.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R3430 | 192 | 239 | 110.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | LN:115:908 NY | 192 | 239 | 110.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | LN:115:908 NY | 192 | 239 | 110.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | LN:115:908 NY | 192 | 239 | 110.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | PACKARD 230/115 3TR | 192 | 239 | 110.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | T:61&64 | 192 | 239 | 110.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | LN:115:908 NY | 192 | 239 | 110.64
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_NEW | 192 | 239 | 110.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | T:61&64 | 192 | 239 | 110.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | LN:115:133 | 192 | 239 | 110.56
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:182S | T:77&78 | 192 | 239 | 110.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:BLISS1 | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:NI2 | T:61&64 | 192 | 239 | 110.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | T:61&64 | 192 | 239 | 110.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_104 | T:79&80 | 192 | 239 | 110.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_103 | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:255_345B202 | 192 | 239 | 110.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:255_345B202 | 192 | 239 | 110.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:255_345B202 | 192 | 239 | 110.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:PK4 | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.28
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.28
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 192 | 239 | 110.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:255_345B202 | 192 | 239 | 110.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 110.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 110.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 110.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:255_345B202 | 192 | 239 | 110.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | T:79&80 | 192 | 239 | 110.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 110.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-SR_37&W-F_171 | T:79&80 | 192 | 239 | 110.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:FV-5M_37&W-F_171 | T:79&80 | 192 | 239 | 110.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 110.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | S:PA_HNTL77 | 192 | 239 | 110.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:AMERT | T:61&64 | 192 | 239 | 110.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 110.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_103 | T:61&64 | 192 | 239 | 110.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1202 | 192 | 239 | 109.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | T:61&64 | 192 | 239 | 109.94
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | S:PA_HNTL78 | 192 | 239 | 109.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 78 230 | 192 | 239 | 109.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | HUNTLEY - PACKARD 77 230 | 192 | 239 | 109.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:ROBI230 | 192 | 239 | 109.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | SB:ROBI230 | 192 | 239 | 109.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:ROBI230 | 192 | 239 | 109.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:GARD230_R823 | 192 | 239 | 109.75
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:AMERT | T:79&80 | 192 | 239 | 109.74
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:HUNT230_R1302 | 192 | 239 | 109.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:110 | T:61&64 | 192 | 239 | 109.72
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:181/922 | T:77&78 | 192 | 239 | 109.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV-HC | T:79&80 | 192 | 239 | 109.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:NI2 | T:79&80 | 192 | 239 | 109.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | T:79&80 | 192 | 239 | 109.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | Base Case | 192 | 239 | 109.48
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | T:77&78 | 192 | 239 | 109.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B302 | 192 | 239 | 109.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:Hunt67 | 192 | 239 | 109.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:GARD230_R833 | 192 | 239 | 109.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | SB:PA230_R3230 | 192 | 239 | 109.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:182N | T:77&78 | 192 | 239 | 109.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | SB:PA230_R304 | 192 | 239 | 109.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | LN:115:129 | 192 | 239 | 109.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:255_345B302 | 192 | 239 | 109.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:3/2:FV | SB:PA230_R3230 | 192 | 239 | 109.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | NIAGARA - ROBINSON 64 345 | 192 | 239 | 109.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - 5MILE 345 | T:79&80 | 192 | 239 | 109.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - FARMVLY | SB:PA230_R3230 | 192 | 239 | 109.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV-HC | T:61&64 | 192 | 239 | 109.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | SB:PA230_R3230 | 192 | 239 | 109.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:107 | SB:PA230_R3230 | 192 | 239 | 109.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CAP:115:GV1 | SB:PA230_R3230 | 192 | 239 | 109.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CAP:115:GV2 | SB:PA230_R3230 | 192 | 239 | 109.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 109.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | SB:PA230_R304 | 192 | 239 | 109.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:NIAG345_3108 | 192 | 239 | 109.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_103 | T:79&80 | 192 | 239 | 109.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:BLISS1 | T:79&80 | 192 | 239 | 109.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | T:61&64 | 192 | 239 | 109.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | B:PACKT4 | 192 | 239 | 109.07
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:NIAG345_3108 | 192 | 239 | 109.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | B:Hunt68 | 192 | 239 | 109.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | B:Hunt68 | 192 | 239 | 109.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | B:Hunt68 | 192 | 239 | 109.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | B:Hunt68 | 192 | 239 | 109.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 7-9 | SB:PA230_R3230 | 192 | 239 | 109.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 10-12 | SB:PA230_R3230 | 192 | 239 | 109.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 1-3 | SB:PA230_R3230 | 192 | 239 | 109
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | T:79&80 | 192 | 239 | 108.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | T:79&80 | 192 | 239 | 108.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 4-6 | SB:PA230_R3230 | 192 | 239 | 108.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:PA230_R3430 | 192 | 239 | 108.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | NIAG - NEWROCH 1 345 | 192 | 239 | 108.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | B:PACKT3 | 192 | 239 | 108.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | T:79&80 | 192 | 239 | 108.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:79&80 | 192 | 239 | 108.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:PK4 | T:79&80 | 192 | 239 | 108.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 4TR | T:79&80 | 192 | 239 | 108.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | NIAG - NEWROCH 1 345 | 192 | 239 | 108.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:77&80 | 192 | 239 | 108.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:77&80 | 192 | 239 | 108.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:77&80 | 192 | 239 | 108.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:77&80 | 192 | 239 | 108.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 108.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | B:PACKT3 | 192 | 239 | 108.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:GARD72&79 | 192 | 239 | 108.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 1 | SB:PA230_R3230 | 192 | 239 | 108.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 2 | SB:PA230_R3230 | 192 | 239 | 108.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 3 | SB:PA230_R3230 | 192 | 239 | 108.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | LN:115:100 | 192 | 239 | 108.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | LN:115:100 | 192 | 239 | 108.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | LN:115:100 | 192 | 239 | 108.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:OSWEGO 5 | SB:PA230_R3230 | 192 | 239 | 108.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:KINT_39-B112 | 192 | 239 | 108.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | NIAGARA - PACKARD 61 230 | 192 | 239 | 108.59
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | LN:115:100 | 192 | 239 | 108.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | S:HNT_GRD80 | 192 | 239 | 108.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:HUNT230_R1502 | 192 | 239 | 108.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:HUNT230_R1502 | 192 | 239 | 108.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:HUNT230_R1502 | 192 | 239 | 108.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:NIAG345_3308 | 192 | 239 | 108.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:ROCH_2T8082 | 192 | 239 | 108.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:KINT_B1-3812 | 192 | 239 | 108.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:HUNT230_R1502 | 192 | 239 | 108.43
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - GARDENVILL 79 230 | 192 | 239 | 108.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | T:78&79 | 192 | 239 | 108.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | HUNTLEY - GARDENVILL 80 230 | 192 | 239 | 108.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R823 | 192 | 239 | 108.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:GINNA | SB:PA230_R3230 | 192 | 239 | 108.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | NIAGARA - PACKARD 62 230 | 192 | 239 | 108.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:GINNA | SB:PA230_R3230 | 192 | 239 | 108.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | T:77&80 | 192 | 239 | 108.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:OSWEGO 6 | SB:PA230_R3230 | 192 | 239 | 108.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 78 230 | 192 | 239 | 108.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL78 | 192 | 239 | 108.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - PACKARD 77 230 | 192 | 239 | 108.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:PA230_R506 | 192 | 239 | 108.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | T:78&79 | 192 | 239 | 108.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:HUNT230_R1402 | 192 | 239 | 108.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | T:78&79 | 192 | 239 | 108.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:HUNT230_R1402 | 192 | 239 | 108.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | T:78&79 | 192 | 239 | 108.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:HUNT230_R1402 | 192 | 239 | 108.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | S:PA_HNTL77 | 192 | 239 | 108.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:9MIPT1 | SB:PA230_R3230 | 192 | 239 | 108.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | T:78&79 | 192 | 239 | 108.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:HUNT230_R1402 | 192 | 239 | 108.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | SB:PA230_R3230 | 192 | 239 | 108.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:GARD230_R873 | 192 | 239 | 108.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | NIAG - KINTIGH 345 | 192 | 239 | 108.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | SB:ROBI230 | 192 | 239 | 107.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 107.87
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | T:61&191 | 192 | 239 | 107.87
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:GARD230_R833 | 192 | 239 | 107.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | B:GARD72&79 | 192 | 239 | 107.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:62&BP76 | 192 | 239 | 107.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | LN:115:907 NY | 192 | 239 | 107.82
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_R1202 | 192 | 239 | 107.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1402 | 192 | 239 | 107.77
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | First:Lockport_907 | 192 | 239 | 107.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:GARD73&80 | 192 | 239 | 107.75
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:ROCH_34XC | 192 | 239 | 107.72
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | S:HNT_GRD80 | 192 | 239 | 107.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | HUNTLEY - GARDENVILL 80 230 | 192 | 239 | 107.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | HUNTLEY - GARDENVILL 79 230 | 192 | 239 | 107.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | LN:115:133 | 192 | 239 | 107.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | SB:255_345B202 | 192 | 239 | 107.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:LOCKPORT | 192 | 239 | 107.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:FITZPATR | SB:PA230_R3230 | 192 | 239 | 107.63
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | FARMVLY - HOMERCTY | 192 | 239 | 107.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | SB:255_345B302 | 192 | 239 | 107.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | R:HC-FV_37&W-F_171 | 192 | 239 | 107.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | SB:ROBI230 | 192 | 239 | 107.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | SOMERSET - NEWROCH 1 345 | 192 | 239 | 107.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:62&PA27 | 192 | 239 | 107.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 107.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | SB:255_345B302 | 192 | 239 | 107.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 192 | 239 | 107.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:114 | SB:PA230_R3230 | 192 | 239 | 107.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | SB:NIAG345_3108 | 192 | 239 | 107.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:113 | SB:PA230_R3230 | 192 | 239 | 107.13
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | NIAG - NEWROCH 1 345 | 192 | 239 | 107.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:111 | SB:PA230_R3230 | 192 | 239 | 107.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | SB:NIAG345_3108 | 192 | 239 | 107.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 106.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | B:Hunt68 | 192 | 239 | 106.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | NIAG - NEWROCH 1 345 | 192 | 239 | 106.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:PA230_R304 | 192 | 239 | 106.8
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 106.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:GARD230_R873 | 192 | 239 | 106.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:PA230_R304 | 192 | 239 | 106.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | B:PACKT3 | 192 | 239 | 106.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | T:77&80 | 192 | 239 | 106.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | B:PACKT3 | 192 | 239 | 106.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lancaster_922 | SB:PA230_R3230 | 192 | 239 | 106.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | B:Hunt67 | 192 | 239 | 106.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | B:Hunt68 | 192 | 239 | 106.64
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:ROCH_3414 | 192 | 239 | 106.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:ROCH_3514 | 192 | 239 | 106.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | SB:ROBI230 | 192 | 239 | 106.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | LN:115:129 | 192 | 239 | 106.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | Base Case | 192 | 239 | 106.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:HUNT230_NEW | 192 | 239 | 106.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:HUNT230_NEW | 192 | 239 | 106.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:HUNT230_NEW | 192 | 239 | 106.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:119 | SB:PA230_R3230 | 192 | 239 | 106.45
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | Base Case | 192 | 239 | 106.44
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:HUNT230_NEW | 192 | 239 | 106.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | First:Lancaster_GRDN_GRDN_230 | 192 | 239 | 106.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | Base Case | 192 | 239 | 106.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:HUNT230_R1302 | 192 | 239 | 106.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:HUNT230_R1502 | 192 | 239 | 106.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | SB:PA230_R3230 | 192 | 239 | 106.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | First:Lockport_104 | 192 | 239 | 106.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:GARD230_T7-12 | 192 | 239 | 106.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | B:GARD73&80 | 192 | 239 | 106.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | SB:PA230_R304 | 192 | 239 | 106.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | SB:PA230_R3230 | 192 | 239 | 106.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCWC/NWES | SB:PA230_R3230 | 192 | 239 | 106.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:MBWC/NWES | SB:PA230_R3230 | 192 | 239 | 106.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:40&41 | 192 | 239 | 106.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:HUNT230_R1502 | 192 | 239 | 106.16
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | LN:115:907 NY | 192 | 239 | 106.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | SB:ROBI230 | 192 | 239 | 105.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | First:Lockport_907 | 192 | 239 | 105.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SB:255_345B202 | 192 | 239 | 105.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:PACKT4 | 192 | 239 | 105.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | PACKARD 230/115 3TR | 192 | 239 | 105.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | B:Hunt67 | 192 | 239 | 105.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | B:Hunt67 | 192 | 239 | 105.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | B:Hunt67 | 192 | 239 | 105.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:255_345B202 | 192 | 239 | 105.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | T:78&79 | 192 | 239 | 105.88
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:HUNT230_R1402 | 192 | 239 | 105.88
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | TB:2/1:ROB | 192 | 239 | 105.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | TB:2/1:ROB | 192 | 239 | 105.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | TB:2/1:ROB | 192 | 239 | 105.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | B:Hunt67 | 192 | 239 | 105.85
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 105.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | SB:PA230_R304 | 192 | 239 | 105.8
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | TB:2/1:ROB | 192 | 239 | 105.8
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | B:PACKT3 | 192 | 239 | 105.77
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.77
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | PACKARD 230/115 3TR | 192 | 239 | 105.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 105.75
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:OSWEGO 5 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:PA230_R3430 | 192 | 239 | 105.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:PA230_R3430 | 192 | 239 | 105.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:PA230_R3430 | 192 | 239 | 105.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 7-9 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 10-12 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:PA230_R3430 | 192 | 239 | 105.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 1-3 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 4-6 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAGARA - PACKARD 61 230 | 192 | 239 | 105.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:OSWEGO 6 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:LAFA_ELB | 192 | 239 | 105.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | ROBINSON - STOLLRD 65 230 | 192 | 239 | 105.45
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | B:PACKT3 | 192 | 239 | 105.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:GARD230_R823 | 192 | 239 | 105.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | SB:PA230_R304 | 192 | 239 | 105.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAGARA - PACKARD 62 230 | 192 | 239 | 105.35
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:PA230_R3230 | 192 | 239 | 105.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:MSU1_7202>7214>7208>7214 | 192 | 239 | 105.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:MARC_765_7402 | 192 | 239 | 105.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:HUNT230_R1302 | 192 | 239 | 105.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:HUNT230_R1302 | 192 | 239 | 105.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:HUNT230_R1302 | 192 | 239 | 105.32
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:HUNT230_R1202 | 192 | 239 | 105.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:HUNT230_R1202 | 192 | 239 | 105.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:HUNT230_R1202 | 192 | 239 | 105.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | SB:ROBI230 | 192 | 239 | 105.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | HQ-NY 765 | 192 | 239 | 105.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:HUNT230_R1302 | 192 | 239 | 105.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 1 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 2 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 3 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:HUNT230_R1202 | 192 | 239 | 105.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:9MIPT1 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.21
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:PA230_R304 | 192 | 239 | 105.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | ROCH 345/115 5TR | 192 | 239 | 105.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | SB:PA230_R3230 | 192 | 239 | 105.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCMB/NWES | SB:PA230_R3230 | 192 | 239 | 105.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:ROBI230 | 192 | 239 | 105.07
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CAP:115:GV1 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CAP:115:GV2 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | B:PACKT3 | 192 | 239 | 105.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:GINNA | 192 | 239 | 105.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | GEN:115:GINNA | 192 | 239 | 105.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 105.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:STOLE230 | 192 | 239 | 104.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | SB:PA230_R3230 | 192 | 239 | 104.94
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:FITZPATR | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | First:Lockport_103 | 192 | 239 | 104.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:GARD230_R833 | 192 | 239 | 104.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | GEN:115:AMERT | 192 | 239 | 104.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:5MILE_B | 192 | 239 | 104.82
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:107 | T:61&64 | 192 | 239 | 104.77
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CAP:115:GV1 | T:61&64 | 192 | 239 | 104.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CAP:115:GV2 | T:61&64 | 192 | 239 | 104.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | T:79&80 | 192 | 239 | 104.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 104.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:9 MI PT2 | SB:PA230_R3230 | 192 | 239 | 104.75
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | B:Hunt68 | 192 | 239 | 104.74
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:180 | T:77&78 | 192 | 239 | 104.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:ROCH_1X8082 | 192 | 239 | 104.72
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:GARD230_R823 | 192 | 239 | 104.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lancaster_GRDN_GRDN_230 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 104.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | T:61&64 | 192 | 239 | 104.64
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:GINNA | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | LN:345:37S-FM-FV-HC | 192 | 239 | 104.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:GINNA | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.59
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | T:77&80 | 192 | 239 | 104.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | G:SUSQ1 | 192 | 239 | 104.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | SB:PA230_R304 | 192 | 239 | 104.53
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | PACKARD 230/115 3TR | 192 | 239 | 104.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 7-9 | T:79&80 | 192 | 239 | 104.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 10-12 | T:79&80 | 192 | 239 | 104.51
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | SB:PA230_R3230 | 192 | 239 | 104.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | PACKARD 230/115 3TR | 192 | 239 | 104.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 1-3 | T:79&80 | 192 | 239 | 104.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:OSWEGO 5 | T:79&80 | 192 | 239 | 104.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 4-6 | T:79&80 | 192 | 239 | 104.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:GARD230_R833 | 192 | 239 | 104.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:LAPER_345_2 | 192 | 239 | 104.45
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:LAPER_345_1 | 192 | 239 | 104.45
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | LFYTE - CLARKCRNS 36A 345 | 192 | 239 | 104.43
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | SB:PA230_R304 | 192 | 239 | 104.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | G:LOCKPORT | 192 | 239 | 104.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 1-3 | T:61&64 | 192 | 239 | 104.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 7-9 | T:61&64 | 192 | 239 | 104.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 10-12 | T:61&64 | 192 | 239 | 104.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LEW 4-6 | T:61&64 | 192 | 239 | 104.36
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:LAFAYETT | 192 | 239 | 104.35
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | GEN:9 MI PT2 | 192 | 239 | 104.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:SCRIBA_R925 | 192 | 239 | 104.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:SCRIBA_R230 | 192 | 239 | 104.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDL - FRASER 32 345 | T:79&80 | 192 | 239 | 104.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 1 | T:61&64 | 192 | 239 | 104.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 2 | T:61&64 | 192 | 239 | 104.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 3 | T:61&64 | 192 | 239 | 104.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:113 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:114 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:OSWEGO 6 | T:79&80 | 192 | 239 | 104.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SANDY_DC | 192 | 239 | 104.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SANDY_DC&OMS | 192 | 239 | 104.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | LN:115:110 | 192 | 239 | 104.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | B:GARD72&79 | 192 | 239 | 104.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | SB:PA230_R304 | 192 | 239 | 104.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:OSWEGO 5 | T:61&64 | 192 | 239 | 104.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:62&PA27 | 192 | 239 | 104.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | S:PA_HNTL77 | 192 | 239 | 104.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | S:PA_HNTL77 | 192 | 239 | 104.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | S:PA_HNTL77 | 192 | 239 | 104.18
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_104 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 104.16
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | B:PACKT3 | 192 | 239 | 104.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:HUNT230_NEW | 192 | 239 | 104.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:111 | DCT:230:79+80+ELM1-2 | 192 | 239 | 104.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | SB:PA230_R304 | 192 | 239 | 104.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | S:PA_HNTL77 | 192 | 239 | 104.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | FARMVLY - HOMERCTY | 192 | 239 | 104.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:41&33 | 192 | 239 | 104.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 1 | T:79&80 | 192 | 239 | 104.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 2 | T:79&80 | 192 | 239 | 104.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 3 | T:79&80 | 192 | 239 | 104.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | S:HNT_GRD80 | 192 | 239 | 104.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:255_345B302 | 192 | 239 | 104.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | T:79&80 | 192 | 239 | 104.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | HUNTLEY - PACKARD 78 230 | 192 | 239 | 104.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | S:PA_HNTL78 | 192 | 239 | 104.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | HUNTLEY - PACKARD 78 230 | 192 | 239 | 104.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | S:PA_HNTL78 | 192 | 239 | 104.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | HUNTLEY - PACKARD 78 230 | 192 | 239 | 104.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | S:PA_HNTL78 | 192 | 239 | 104.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:255_345B302 | 192 | 239 | 104.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:HUNT230_R1502 | 192 | 239 | 104.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:9MIPT1 | T:79&80 | 192 | 239 | 104.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | R:HC-FV_37&W-F_171 | 192 | 239 | 103.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | HUNTLEY - PACKARD 77 230 | 192 | 239 | 103.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | HUNTLEY - PACKARD 77 230 | 192 | 239 | 103.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | HUNTLEY - PACKARD 77 230 | 192 | 239 | 103.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | HUNTLEY - PACKARD 78 230 | 192 | 239 | 103.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | S:PA_HNTL78 | 192 | 239 | 103.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CAP:115:GV1 | T:79&80 | 192 | 239 | 103.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CAP:115:GV2 | T:79&80 | 192 | 239 | 103.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | HUNTLEY - GARDENVILL 79 230 | 192 | 239 | 103.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:OSWEGO 6 | T:61&64 | 192 | 239 | 103.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:PA230_R3430 | 192 | 239 | 103.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | G:LIMERCK2 | 192 | 239 | 103.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | HUNTLEY - GARDENVILL 80 230 | 192 | 239 | 103.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | G:PECHBTM2 | 192 | 239 | 103.94
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | HUNTLEY - PACKARD 77 230 | 192 | 239 | 103.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | G:HOPECG1 | 192 | 239 | 103.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | G:SALEMG1 | 192 | 239 | 103.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 103.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:GINNA | T:61&64 | 192 | 239 | 103.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:GINNA | T:61&64 | 192 | 239 | 103.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | TB:2/1:NI2 | 192 | 239 | 103.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | NIAGARA 230/115 2TR | 192 | 239 | 103.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:GARD72&79 | 192 | 239 | 103.83
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | B:PACKT3 | 192 | 239 | 103.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | T:61&64 | 192 | 239 | 103.8
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:LAPER_345_3 | 192 | 239 | 103.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:LAPER_345_4 | 192 | 239 | 103.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:NIAG345_3108 | 192 | 239 | 103.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:9MIPT1 | T:61&64 | 192 | 239 | 103.77
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | T:78&79 | 192 | 239 | 103.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:HUNT230_R1402 | 192 | 239 | 103.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:NIAG345_3108 | 192 | 239 | 103.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:119 | DCT:230:79+80+ELM1-2 | 192 | 239 | 103.75
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | LN:115:908 NY | 192 | 239 | 103.75
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - GARDENVILL 79 230 | 192 | 239 | 103.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:MLS3&OMS | 192 | 239 | 103.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:MILLST3 | 192 | 239 | 103.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SIN:250 | 192 | 239 | 103.73
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | HUNTLEY - GARDENVILL 80 230 | 192 | 239 | 103.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | S:HNT_GRD80 | 192 | 239 | 103.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:FITZPATR | T:79&80 | 192 | 239 | 103.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:SUSQ1 | 192 | 239 | 103.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | T:61&64 | 192 | 239 | 103.68
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:ROCH_2T8082 | 192 | 239 | 103.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:SEABROOK | 192 | 239 | 103.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:SEAB&OMS | 192 | 239 | 103.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:OAKD345_B5 | 192 | 239 | 103.64
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:GARD230_R873 | 192 | 239 | 103.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | NIAG - NEWROCH 1 345 | 192 | 239 | 103.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | OAKDLE - CLARKCRNS 36B 345 | 192 | 239 | 103.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:OAKD345_B6 | 192 | 239 | 103.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | NIAG - NEWROCH 1 345 | 192 | 239 | 103.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | B:Hunt67 | 192 | 239 | 103.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | B:PACKT3 | 192 | 239 | 103.58
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | LN:115:908 NY | 192 | 239 | 103.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | SB:255_345B202 | 192 | 239 | 103.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_104 | SB:ROBI230 | 192 | 239 | 103.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:PA230_R506 | 192 | 239 | 103.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | STOLLRD - GARDENVILL 66 230 | 192 | 239 | 103.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SB:MARC345_3208 | 192 | 239 | 103.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:GINNA | T:79&80 | 192 | 239 | 103.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | First:Lockport_104 | 192 | 239 | 103.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | NIAGARA - ROBINSON 64 345 | 192 | 239 | 103.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:34&42 | 192 | 239 | 103.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | B:PACKT3 | 192 | 239 | 103.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | T:61&64 | 192 | 239 | 103.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:GINNA | T:79&80 | 192 | 239 | 103.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:GARD230_T7-12 | 192 | 239 | 103.44
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | SOMERSET - NEWROCH 1 345 | 192 | 239 | 103.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | T:31&41 | 192 | 239 | 103.4
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:67&68&BW | 192 | 239 | 103.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | SB:255_345B202 | 192 | 239 | 103.36
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:FITZPATR | T:61&64 | 192 | 239 | 103.35
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | B:STOLE230 | 192 | 239 | 103.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | T:62&BP76 | 192 | 239 | 103.28
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 103.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:ROCH_34XC | 192 | 239 | 103.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 103.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:114 | T:61&64 | 192 | 239 | 103.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | LN:115:133 | 192 | 239 | 103.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:GARD230_R873 | 192 | 239 | 103.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | NIAGARA - ROBINSON 64 345 | 192 | 239 | 103.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | G:LOCKPORT | 192 | 239 | 103.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:GARD230_T7-12 | 192 | 239 | 103.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:113 | T:61&64 | 192 | 239 | 103.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lancaster_922 | T:61&64 | 192 | 239 | 103.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | GEN: IND PT 3 | 192 | 239 | 103.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:BUCHS_3 | 192 | 239 | 103.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:BUCHS_1 | 192 | 239 | 103.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:111 | T:61&64 | 192 | 239 | 103.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | B:GARD73&80 | 192 | 239 | 103.03
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:114 | T:79&80 | 192 | 239 | 103.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lancaster_922 | DCT:230:79+80+ELM1-2 | 192 | 239 | 103.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:GARD73&80 | 192 | 239 | 103.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SIN:120_130 | 192 | 239 | 103.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SIN:130 | 192 | 239 | 103.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | T:W97&W98 | 192 | 239 | 103.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:LIMERCK2 | 192 | 239 | 103
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | GEN:115:AMERT | 192 | 239 | 102.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | GEN: IND PT 2 | 192 | 239 | 102.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:HOPECG1 | 192 | 239 | 102.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:113 | T:79&80 | 192 | 239 | 102.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:HUNT230_R1302 | 192 | 239 | 102.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | PACKARD 230/115 3TR | 192 | 239 | 102.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:SALEMG1 | 192 | 239 | 102.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | SB:255_345B302 | 192 | 239 | 102.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:BUCHN_9 | 192 | 239 | 102.92
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | SB:HUNT230_R1202 | 192 | 239 | 102.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:BUCHN_7 | 192 | 239 | 102.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:111 | T:79&80 | 192 | 239 | 102.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | LN:115:130 | 192 | 239 | 102.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:AMERT | NIAGARA - ROBINSON 64 345 | 192 | 239 | 102.89
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:BUCHN_11 | 192 | 239 | 102.88
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_103 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 102.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STONYCR - WTHRS 230 | T:61&64 | 192 | 239 | 102.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | ROBINSON - STOLLRD 65 230 | 192 | 239 | 102.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | LN:115:908 NY | 192 | 239 | 102.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | PACKARD 230/115 3TR | 192 | 239 | 102.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:PECHBTM2 | 192 | 239 | 102.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | LN:115:908 NY | 192 | 239 | 102.63
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | SB:NIAG345_3108 | 192 | 239 | 102.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | LN:115:133 | 192 | 239 | 102.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:ROCH_3414 | 192 | 239 | 102.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:ROCH_3514 | 192 | 239 | 102.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | T:61&64 | 192 | 239 | 102.56
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | SB:255_345B302 | 192 | 239 | 102.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:119 | T:61&64 | 192 | 239 | 102.53
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | First:Lockport_103 | 192 | 239 | 102.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:119 | T:79&80 | 192 | 239 | 102.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | DCT:230:79+80+ELM1-2 | 192 | 239 | 102.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:RAIN345_9W | 192 | 239 | 102.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:133 | NIAG - NEWROCH 1 345 | 192 | 239 | 102.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | T:61&64 | 192 | 239 | 102.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCWC/NWES | T:61&64 | 192 | 239 | 102.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:MBWC/NWES | T:61&64 | 192 | 239 | 102.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:110 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 102.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lancaster_GRDN_GRDN_230 | SB:ROBI230 | 192 | 239 | 102.44
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 11 | SB:PA230_R3230 | 192 | 239 | 102.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 12 | SB:PA230_R3230 | 192 | 239 | 102.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 13 | SB:PA230_R3230 | 192 | 239 | 102.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 8 | SB:PA230_R3230 | 192 | 239 | 102.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 9 | SB:PA230_R3230 | 192 | 239 | 102.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:OSWE_R935 | 192 | 239 | 102.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | GEN: RAVENSWOOD | 192 | 239 | 102.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 10 | SB:PA230_R3230 | 192 | 239 | 102.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:RAIN345_1W | 192 | 239 | 102.36
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:OSWE_R925 | 192 | 239 | 102.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | DCT:230:79+80+ELM1-2 | 192 | 239 | 102.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | LN:115:130 | 192 | 239 | 102.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | GEN:OSWEGO 6 | 192 | 239 | 102.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | B:Hunt68 | 192 | 239 | 102.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:FITZPATR | 192 | 239 | 102.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:ROBI230 | 192 | 239 | 102.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | PACKARD 230/115 3TR | 192 | 239 | 102.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | SB:NIAG345_3108 | 192 | 239 | 102.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:9MIPT1 | 192 | 239 | 102.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | SB:ROBI230 | 192 | 239 | 102.21
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:NI2 | NIAGARA - ROBINSON 64 345 | 192 | 239 | 102.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | NIAGARA - ROBINSON 64 345 | 192 | 239 | 102.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | SB:GARD230_T7-12 | 192 | 239 | 102.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | G:MARTNCK4 | 192 | 239 | 102.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | NIAGARA - ROBINSON 64 345 | 192 | 239 | 102.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:OSWE_R965 | 192 | 239 | 102.14
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:130 | NIAG - NEWROCH 1 345 | 192 | 239 | 102.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:RAIN345_8W | 192 | 239 | 102.09
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | T:77&80 | 192 | 239 | 102.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | LN:115:129 | 192 | 239 | 102.08
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:OSWE_R955 | 192 | 239 | 102.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | GEN:OSWEGO 5 | 192 | 239 | 102.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | LN:115:100 | 192 | 239 | 102.04
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:HUNT230_NEW | 192 | 239 | 102.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 102.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCWC/NWES | DCT:230:79+80+ELM1-2 | 192 | 239 | 102.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:MBWC/NWES | DCT:230:79+80+ELM1-2 | 192 | 239 | 102.01
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | LN:115:907 NY | 192 | 239 | 101.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | LN:115:907 NY | 192 | 239 | 101.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | LN:115:907 NY | 192 | 239 | 101.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:9 MI PT2 | DCT:230:79+80+ELM1-2 | 192 | 239 | 101.96
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:KINT_39-B112 | 192 | 239 | 101.94
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_103 | SB:ROBI230 | 192 | 239 | 101.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | First:Lockport_907 | 192 | 239 | 101.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | First:Lockport_907 | 192 | 239 | 101.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | First:Lockport_907 | 192 | 239 | 101.91
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | LN:115:907 NY | 192 | 239 | 101.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV-HC | NIAGARA - ROBINSON 64 345 | 192 | 239 | 101.86
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | First:Lockport_907 | 192 | 239 | 101.84
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | S:PA_HNTL77 | 192 | 239 | 101.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTHRS - MEYER 230 | T:79&80 | 192 | 239 | 101.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:PA230_R3430 | 192 | 239 | 101.8
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | Base Case | 192 | 239 | 101.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAGARA 230/115 2TR | 192 | 239 | 101.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | TB:2/1:NI2 | 192 | 239 | 101.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | SB:255_345B302 | 192 | 239 | 101.74
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SB:KINT_B1-3812 | 192 | 239 | 101.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lancaster_922 | T:79&80 | 192 | 239 | 101.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | S:PA_HNTL78 | 192 | 239 | 101.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | HUNTLEY - PACKARD 78 230 | 192 | 239 | 101.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | Base Case | 192 | 239 | 101.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | HUNTLEY - PACKARD 77 230 | 192 | 239 | 101.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | SB:ROBI230 | 192 | 239 | 101.61
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | SB:HUNT230_R1502 | 192 | 239 | 101.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | B:STOLE230 | 192 | 239 | 101.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:GARD230_T7-12 | 192 | 239 | 101.56
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:ROBI230 | 192 | 239 | 101.56
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCMB/NWES | T:61&64 | 192 | 239 | 101.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | SB:ROBI230 | 192 | 239 | 101.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | T:61&64 | 192 | 239 | 101.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | B:Hunt67 | 192 | 239 | 101.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | SB:255_345B302 | 192 | 239 | 101.44
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | T:61&64 | 192 | 239 | 101.44
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | SB:NIAG345_3108 | 192 | 239 | 101.43
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | SB:255_345B302 | 192 | 239 | 101.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | SB:PA230_R304 | 192 | 239 | 101.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | LN:115:129 | 192 | 239 | 101.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-WC_30&W-F_171 | T:79&80 | 192 | 239 | 101.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | G:LOCKPORT | 192 | 239 | 101.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | G:LOCKPORT | 192 | 239 | 101.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | G:LOCKPORT | 192 | 239 | 101.38
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:AMERT | SB:ROBI230 | 192 | 239 | 101.37
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | PACKARD 230/115 3TR | 192 | 239 | 101.36
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | G:LOCKPORT | 192 | 239 | 101.31
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:129 | NIAG - NEWROCH 1 345 | 192 | 239 | 101.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | T:78&79 | 192 | 239 | 101.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | SB:HUNT230_R1402 | 192 | 239 | 101.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT4 | 192 | 239 | 101.25
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | SB:NIAG345_3108 | 192 | 239 | 101.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:AMERT | SB:PA230_R304 | 192 | 239 | 101.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_104 | SB:PA230_R304 | 192 | 239 | 101.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | SB:PA230_R304 | 192 | 239 | 101.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | ROBINSON - STOLLRD 65 230 | 192 | 239 | 101.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | WTRCR - MAINSBRG 30A 345 | T:79&80 | 192 | 239 | 101.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCWC/NWES | T:79&80 | 192 | 239 | 101.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:MBWC/NWES | T:79&80 | 192 | 239 | 101.12
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | SB:PA230_R304 | 192 | 239 | 101.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:110 | SB:ROBI230 | 192 | 239 | 101.1
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | NIAG - NEWROCH 1 345 | 192 | 239 | 101
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | NIAG - NEWROCH 1 345 | 192 | 239 | 101
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:ROCH_2T8082 | 192 | 239 | 100.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | SB:NIAG345_3108 | 192 | 239 | 100.98
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | ROBINSON - STOLLRD 65 230 | 192 | 239 | 100.95
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAGARA - PACKARD 61 230 | 192 | 239 | 100.94
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LFYTE - CLARKCRNS 36A 345 | B:PACKT3 | 192 | 239 | 100.93
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | LN:115:908 NY | 192 | 239 | 100.9
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:HUNT230_R1302 | 192 | 239 | 100.82
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:9 MI PT2 | T:79&80 | 192 | 239 | 100.81
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAGARA - PACKARD 62 230 | 192 | 239 | 100.79
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:HUNT230_R1202 | 192 | 239 | 100.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | SB:PA230_R304 | 192 | 239 | 100.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-MB_30&W-F_171 | DCT:230:79+80+ELM1-2 | 192 | 239 | 100.76
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | SB:PA230_R304 | 192 | 239 | 100.74
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:115:AMERT | B:PACKT3 | 192 | 239 | 100.72
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_104 | B:PACKT3 | 192 | 239 | 100.72
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | FARMVLY - HOMERCTY | 192 | 239 | 100.7
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | GEN:9 MI PT2 | T:61&64 | 192 | 239 | 100.67
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:NI2 | SB:ROBI230 | 192 | 239 | 100.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA 230/115 2TR | SB:ROBI230 | 192 | 239 | 100.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | SB:255_345B302 | 192 | 239 | 100.66
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:KINT_39-B112 | 192 | 239 | 100.65
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | R:HC-FV_37&W-F_171 | 192 | 239 | 100.63
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HCMB/NWES | DCT:230:79+80+ELM1-2 | 192 | 239 | 100.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | PACKARD 230/115 3TR | 192 | 239 | 100.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | STOLLRD - GARDENVILL 66 230 | 192 | 239 | 100.6
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | R:HC-FV_37&W-F_171 | B:PACKT3 | 192 | 239 | 100.59
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | LN:115:100 | 192 | 239 | 100.59
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 100.57
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | FARMVLY - HOMERCTY | B:PACKT3 | 192 | 239 | 100.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:GARD230_R823 | 192 | 239 | 100.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:GARD230_R823 | 192 | 239 | 100.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:GARD230_R823 | 192 | 239 | 100.55
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | LN:115:100 | 192 | 239 | 100.52
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:KINT_B1-3812 | 192 | 239 | 100.51
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | SB:NIAG345_3108 | 192 | 239 | 100.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:255_345B302 | 192 | 239 | 100.49
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | Base Case | 192 | 239 | 100.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:GARD230_R823 | 192 | 239 | 100.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | Base Case | 192 | 239 | 100.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | MAINSBRG - HOMERCITY 30B 345 | DCT:230:79+80+ELM1-2 | 192 | 239 | 100.45
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SB:255_345B202 | 192 | 239 | 100.43
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SB:255_345B202 | 192 | 239 | 100.42
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:STOLE230 | 192 | 239 | 100.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | SB:ROBI230 | 192 | 239 | 100.39
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | SB:NIAG345_3108 | 192 | 239 | 100.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROBINSON - STOLLRD 65 230 | PACKARD 230/115 3TR | 192 | 239 | 100.31
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 100.3
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:120 | SB:PA230_R3230 | 192 | 239 | 100.29
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | SOMERSET - NEWROCH 1 345 | 192 | 239 | 100.28
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | ROCH 345/115 5TR | B:PACKT3 | 192 | 239 | 100.28
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:345:37S-FM-FV-HC | SB:ROBI230 | 192 | 239 | 100.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | Base Case | 192 | 239 | 100.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | FARMVLY - HOMERCTY | 192 | 239 | 100.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | OAKDLE - CLARKCRNS 36B 345 | B:PACKT3 | 192 | 239 | 100.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:ROCH_34XC | 192 | 239 | 100.24
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 61 230 | NIAG - NEWROCH 1 345 | 192 | 239 | 100.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | B:Hunt68 | 192 | 239 | 100.22
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | STOLLRD - GARDENVILL 66 230 | T:77&80 | 192 | 239 | 100.19
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | SB:GARD230_R833 | 192 | 239 | 100.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | SB:GARD230_R833 | 192 | 239 | 100.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | SB:GARD230_R833 | 192 | 239 | 100.17
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | SB:GARD230_R833 | 192 | 239 | 100.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_103 | SB:PA230_R304 | 192 | 239 | 100.07
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAG - NEWROCH 1 345 | 192 | 239 | 100.06
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | SB:NIAG345_3308 | 192 | 239 | 100.05
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | B:STOLE230 | 192 | 239 | 100.01
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 Max |  |  |  |  | 192.27
| Grand Max |  |  |  |  | 192.27

## N-2_ETC_OH_1000_Fixed
SERIES REACTORS ON 77 & 78 LINES IN-SERVICE
Niagara Dispatch | Monitored Facility | First Level Scenario | Cont Name | Rate Base (MVA) | Rate Cont (MVA) | Final AC %Loading
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | MEYER - CANDQUA 60 230 | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | MEYER - CANDQUA 60 230 | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | STOLLRD - SHLDON 67 230 | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | STOLLRD - SHLDON 67 230 | 474 | 478 | NConv
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 474 | 478 | NConv
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | STNYRDG - HILLSIDE 68B 230 | MEYER - CANDQUA 60 230 | 474 | 478 | NConv
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HILLSIDE 230/115 4TR | MEYER - CANDQUA 60 230 | 474 | 478 | NConv
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 115.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 115.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 115.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 115.34
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | TB:2/1:MEYER | 474 | 478 | 114.21
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | CANDQUA - STNYRDG 68A 230 | 474 | 478 | 113.55
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | S:AVOCA | 474 | 478 | 113.55
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | CANDQUA - STNYRDG 68A 230 | TB:2/1:MEYER | 474 | 478 | 112.12
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | CANDQUA - STNYRDG 68A 230 | 474 | 478 | 111.46
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:MEYER | S:AVOCA | 474 | 478 | 111.46
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt68 | 474 | 478 | 111.31
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 474 | 478 | 110.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 110.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 474 | 478 | 110.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 110.57
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | LN:115:908 NY | 474 | 478 | 109
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | WTHRS - MEYER 230 | 474 | 478 | 108.6
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | B:MEYER | 474 | 478 | 108.57
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt68 | 474 | 478 | 108.44
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt67 | 474 | 478 | 108.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | LN:115:100 | 474 | 478 | 107.73
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | WTHRS - MEYER 230 | 474 | 478 | 107.63
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:MEYER | 474 | 478 | 107.58
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | WTHRS - MEYER 230 | 474 | 478 | 107.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:MEYER | 474 | 478 | 107.51
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | S:PA_HNTL77 | 474 | 478 | 107.37
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | WTHRS - MEYER 230 | 474 | 478 | 107.33
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | S:PA_HNTL78 | 474 | 478 | 107.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 107.31
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | B:MEYER | 474 | 478 | 107.29
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 107.25
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | TB:2/1:ROB | 474 | 478 | 106.16
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:ROB | WTHRS - MEYER 230 | 474 | 478 | 105.73
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:ROB | B:MEYER | 474 | 478 | 105.69
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:Hunt67 | 474 | 478 | 105.53
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | LN:115:908 NY | 474 | 478 | 105.39
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | WTHRS - MEYER 230 | 474 | 478 | 104.99
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | WTHRS - MEYER 230 | 474 | 478 | 104.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:908 NY | B:MEYER | 474 | 478 | 104.95
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:MEYER | 474 | 478 | 104.91
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | WTHRS - MEYER 230 | 474 | 478 | 104.9
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:MEYER | 474 | 478 | 104.85
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | S:PA_HNTL77 | 474 | 478 | 104.73
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | S:PA_HNTL78 | 474 | 478 | 104.67
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 78 230 | 474 | 478 | 104.67
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - PACKARD 77 230 | 474 | 478 | 104.62
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | LN:115:907 NY | 474 | 478 | 103.96
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | LN:115:100 | 474 | 478 | 103.95
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | WTHRS - MEYER 230 | 474 | 478 | 103.56
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:907 NY | WTHRS - MEYER 230 | 474 | 478 | 103.55
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | First:Lockport_907 | 474 | 478 | 103.53
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:100 | B:MEYER | 474 | 478 | 103.52
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | LN:115:907 NY | B:MEYER | 474 | 478 | 103.51
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 78 230 | B:Hunt67 | 474 | 478 | 103.19
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_907 | WTHRS - MEYER 230 | 474 | 478 | 103.14
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | First:Lockport_907 | B:MEYER | 474 | 478 | 103.1
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - PACKARD 77 230 | B:Hunt68 | 474 | 478 | 103.08
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | S:HNT_GRD80 | 474 | 478 | 102.87
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | WTHRS - MEYER 230 | 474 | 478 | 102.86
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | WTHRS - MEYER 230 | 474 | 478 | 102.85
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | B:MEYER | 474 | 478 | 102.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - GARDENVILL 79 230 | 474 | 478 | 102.81
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | B:MEYER | 474 | 478 | 102.8
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - GARDENVILL 80 230 | 474 | 478 | 102.8
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | TB:2/1:ROB | 474 | 478 | 102.38
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:ROB | WTHRS - MEYER 230 | 474 | 478 | 101.95
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | TB:2/1:ROB | B:MEYER | 474 | 478 | 101.91
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:GARD72&79 | 474 | 478 | 101.89
Dispatch 1 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | B:GARD73&80 | 474 | 478 | 100.64
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | LN:115:907 NY | 474 | 478 | 100.35
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | S:HNT_GRD80 | 474 | 478 | 100.33
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | WTHRS - MEYER 230 | 474 | 478 | 100.3
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | WTHRS - MEYER 230 | 474 | 478 | 100.29
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - GARDENVILL 79 230 | 474 | 478 | 100.27
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | WTHRS - MEYER 230 | HUNTLEY - GARDENVILL 80 230 | 474 | 478 | 100.26
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 79 230 | B:MEYER | 474 | 478 | 100.25
Dispatch 2 | 130762 GARDV230 230 130767 STOLE230 230 1 | HUNTLEY - GARDENVILL 80 230 | B:MEYER | 474 | 478 | 100.24
| 130762 GARDV230 230 130767 STOLE230 230 1 Max |  |  |  |  | 115.34
Dispatch 1 | 130766 ROBIN230 230 130767 STOLE230 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 550 | 717 | NConv
| 130766 ROBIN230 230 130767 STOLE230 230 1 Max |  |  |  |  | 0
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 496 | 657 | NConv
Dispatch 1 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 496 | 657 | NConv
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 496 | 657 | NConv
Dispatch 2 | 130766 ROBIN230 230 147841 NIAGAR2E 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 496 | 657 | NConv
| 130766 ROBIN230 230 147841 NIAGAR2E 230 1 Max |  |  |  |  | 0
Dispatch 1 | 130766 ROBIN230 230 999989 STAR9 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 297 | 420 | NConv
Dispatch 1 | 130766 ROBIN230 230 999989 STAR9 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 297 | 420 | NConv
Dispatch 2 | 130766 ROBIN230 230 999989 STAR9 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 297 | 420 | NConv
Dispatch 2 | 130766 ROBIN230 230 999989 STAR9 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 297 | 420 | NConv
| 130766 ROBIN230 230 999989 STAR9 115 1 Max |  |  |  |  | 0
Dispatch 1 | 130775 BIGTR115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 183 | NConv
Dispatch 1 | 130775 BIGTR115 115 131467 LANGN115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 183 | NConv
Dispatch 2 | 130775 BIGTR115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 183 | NConv
Dispatch 2 | 130775 BIGTR115 115 131467 LANGN115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 183 | NConv
| 130775 BIGTR115 115 131467 LANGN115 115 1 Max |  |  |  |  | 0
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 119 | 119 | NConv
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 119 | 119 | NConv
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 119 | 119 | NConv
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 119 | 119 | NConv
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_705 | 119 | 119 | 125.4
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:705 NY | 119 | 119 | 125.4
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | LN:115:181/922 | 119 | 119 | 125.11
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | LN:115:181/922 | 119 | 119 | 125.11
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:705 NY | 119 | 119 | 124.45
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_705 | 119 | 119 | 124.45
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:705 NY | LN:115:181/922 | 119 | 119 | 124.21
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_705 | LN:115:181/922 | 119 | 119 | 124.21
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-FV_37&W-F_171 | 119 | 119 | 121.49
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - HOMERCTY | 119 | 119 | 121.35
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-FV_37&W-F_171 | 119 | 119 | 120.92
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - HOMERCTY | 119 | 119 | 120.82
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_926B | LN:115:181/922 | 119 | 119 | 119.57
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_926B | LN:115:181/922 | 119 | 119 | 119.46
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-FV_37&W-F_171 | LN:115:181/922 | 119 | 119 | 118.39
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_926B | 119 | 119 | 118.3
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_926B | 119 | 119 | 118.26
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - HOMERCTY | LN:115:181/922 | 119 | 119 | 118.24
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-FV_37&W-F_171 | LN:115:181/922 | 119 | 119 | 117.85
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - HOMERCTY | LN:115:181/922 | 119 | 119 | 117.71
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV-HC | 119 | 119 | 116.56
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:5M-SR_37&W-F_171 | 119 | 119 | 116.22
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV-HC | 119 | 119 | 116
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | 5 MILE - STOLLE 37A 345 | 119 | 119 | 116
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_STOL_HOMER_345 | 119 | 119 | 116
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | HOMERCTY - STOLLRD 37 345 | 119 | 119 | 116
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:STOLE345 | 119 | 119 | 116
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:5MILE | 119 | 119 | 115.96
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV | 119 | 119 | 115.96
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:5M-SR_37&W-F_171 | 119 | 119 | 115.82
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_STOL_HOMER_345 | 119 | 119 | 115.62
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | 5 MILE - STOLLE 37A 345 | 119 | 119 | 115.62
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:STOLE345 | 119 | 119 | 115.62
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | HOMERCTY - STOLLRD 37 345 | 119 | 119 | 115.62
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | S:STOLLE345 | 119 | 119 | 115.6
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:5MILE | 119 | 119 | 115.46
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:345:37S-FM-FV | 119 | 119 | 115.46
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:5M-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 115.33
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV-HC | LN:115:181/922 | 119 | 119 | 115.27
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | S:STOLLE345 | 119 | 119 | 115.15
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_STOL_HOMER_345 | LN:115:181/922 | 119 | 119 | 115.14
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | 5 MILE - STOLLE 37A 345 | LN:115:181/922 | 119 | 119 | 115.14
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | HOMERCTY - STOLLRD 37 345 | LN:115:181/922 | 119 | 119 | 115.14
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV | LN:115:181/922 | 119 | 119 | 114.97
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:903 NY | LN:115:181/922 | 119 | 119 | 114.88
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:903 NY | 119 | 119 | 114.72
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:5M-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 114.25
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV-HC | LN:115:181/922 | 119 | 119 | 114.2
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:903 NY | LN:115:181/922 | 119 | 119 | 114.2
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_STOL_HOMER_345 | LN:115:181/922 | 119 | 119 | 114.06
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | 5 MILE - STOLLE 37A 345 | LN:115:181/922 | 119 | 119 | 114.06
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | HOMERCTY - STOLLRD 37 345 | LN:115:181/922 | 119 | 119 | 114.06
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:903 NY | 119 | 119 | 114.01
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:345:37S-FM-FV | LN:115:181/922 | 119 | 119 | 113.83
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:926 NY | LN:115:181/922 | 119 | 119 | 113.66
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:926 NY | LN:115:181/922 | 119 | 119 | 113.45
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:926 NY | 119 | 119 | 112.45
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:926 NY | 119 | 119 | 112.23
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_706 | 119 | 119 | 112.02
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:706 NY | 119 | 119 | 112.02
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:706 NY | LN:115:181/922 | 119 | 119 | 111.71
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_706 | LN:115:181/922 | 119 | 119 | 111.71
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:706 NY | 119 | 119 | 111.08
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_706 | 119 | 119 | 111.08
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:706 NY | LN:115:181/922 | 119 | 119 | 110.79
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_706 | LN:115:181/922 | 119 | 119 | 110.79
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | DUNKIRK - SRIPL 68 230 | LN:115:181/922 | 119 | 119 | 108.61
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SRIPL - ERIE E 69 230 | LN:115:181/922 | 119 | 119 | 108.5
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:5MILE_B | 119 | 119 | 108.37
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SB:5MILE_B | 119 | 119 | 108.1
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SRIPL - ERIE E 69 230 | LN:115:181/922 | 119 | 119 | 107.72
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | DUNKIRK - SRIPL 68 230 | LN:115:181/922 | 119 | 119 | 107.7
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | ERIE E - 4 MILE 230 | LN:115:181/922 | 119 | 119 | 106.73
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:FV-5M_37&W-F_171 | 119 | 119 | 106.52
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-SR_37&W-F_171 | 119 | 119 | 106.52
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 106.35
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:FV-5M_37&W-F_171 | LN:115:181/922 | 119 | 119 | 106.35
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:HC-SR_37&W-F_171 | 119 | 119 | 106.29
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:FV-5M_37&W-F_171 | 119 | 119 | 106.29
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - 5MILE 345 | 119 | 119 | 106.22
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | ERIE E - 4 MILE 230 | LN:115:181/922 | 119 | 119 | 106.09
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:HC-SR_37&W-F_171 | LN:115:181/922 | 119 | 119 | 106.02
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | R:FV-5M_37&W-F_171 | LN:115:181/922 | 119 | 119 | 106.02
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:DUNKG4 | 119 | 119 | 105.99
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | FARMVLY - 5MILE 345 | 119 | 119 | 105.91
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | WTHRS - MEYER 230 | LN:115:181/922 | 119 | 119 | 105.78
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - 5MILE 345 | LN:115:181/922 | 119 | 119 | 105.77
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | FARMVLY - 5MILE 345 | LN:115:181/922 | 119 | 119 | 105.53
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | WTHRS - MEYER 230 | 119 | 119 | 105.52
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:MEYER | 119 | 119 | 105.4
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:DUNKG4 | 119 | 119 | 105.34
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:EESR/WF/NWES | 119 | 119 | 105.33
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:DKSR/WRFL | 119 | 119 | 105.18
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | WTHRS - MEYER 230 | LN:115:181/922 | 119 | 119 | 105.15
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:EESR/WRFL | 119 | 119 | 105.06
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | WTHRS - MEYER 230 | 119 | 119 | 104.85
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | B:MEYER | 119 | 119 | 104.74
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:EESR/WF/NWES | 119 | 119 | 104.66
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:DKSR/WRFL | 119 | 119 | 104.51
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:EESR/WRFL | 119 | 119 | 104.39
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:EESR/NWES | 119 | 119 | 104.29
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | DUNKIRK - SRIPL 68 230 | 119 | 119 | 104.16
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SRIPL - ERIE E 69 230 | 119 | 119 | 104.04
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | R:EESR/NWES | 119 | 119 | 103.64
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | CANDQUA - STNYRDG 68A 230 | LN:115:181/922 | 119 | 119 | 103.53
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | DUNKIRK - SRIPL 68 230 | 119 | 119 | 103.5
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | NIAG - NEWROCH 1 345 | LN:115:181/922 | 119 | 119 | 103.45
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SRIPL - ERIE E 69 230 | 119 | 119 | 103.38
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:904 NY | 119 | 119 | 103.22
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_904 | 119 | 119 | 103.22
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:181/922 | 119 | 119 | 103.08
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | ERIE E - 4 MILE 230 | 119 | 119 | 103.01
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | NIAG - NEWROCH 1 345 | 119 | 119 | 102.98
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | CANDQUA - STNYRDG 68A 230 | 119 | 119 | 102.93
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | S:AVOCA | 119 | 119 | 102.93
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | CANDQUA - STNYRDG 68A 230 | LN:115:181/922 | 119 | 119 | 102.88
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:181/922 | 119 | 119 | 102.74
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:904 NY | LN:115:181/922 | 119 | 119 | 102.7
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_904 | LN:115:181/922 | 119 | 119 | 102.7
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | NIAG - NEWROCH 1 345 | LN:115:181/922 | 119 | 119 | 102.65
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:904 NY | 119 | 119 | 102.48
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | First:Lancaster_904 | 119 | 119 | 102.48
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:181/922 | 119 | 119 | 102.44
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | ERIE E - 4 MILE 230 | 119 | 119 | 102.35
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | NIAG - NEWROCH 1 345 | 119 | 119 | 102.34
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | CANDQUA - STNYRDG 68A 230 | 119 | 119 | 102.28
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | S:AVOCA | 119 | 119 | 102.28
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:181/922 | 119 | 119 | 102.17
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | STONYCR - WTHRS 230 | LN:115:181/922 | 119 | 119 | 102.15
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | STONYCR - WTHRS 230 | 119 | 119 | 102.07
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:904 NY | LN:115:181/922 | 119 | 119 | 102.02
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | First:Lancaster_904 | LN:115:181/922 | 119 | 119 | 102.02
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:167 | 119 | 119 | 101.94
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SOMERSET - NEWROCH 1 345 | 119 | 119 | 101.9
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:167 | LN:115:181/922 | 119 | 119 | 101.73
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:181/922 | 119 | 119 | 101.6
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | STONYCR - WTHRS 230 | LN:115:181/922 | 119 | 119 | 101.51
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | STONYCR - WTHRS 230 | 119 | 119 | 101.4
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LN:115:167 | 119 | 119 | 101.24
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | SOMERSET - NEWROCH 1 345 | 119 | 119 | 101.22
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:181/922 | 119 | 119 | 101.07
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:167 | LN:115:181/922 | 119 | 119 | 101.06
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LFYTE - CLARKCRNS 36A 345 | 119 | 119 | 100.92
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | HILLSIDE 230/115 4TR | LN:115:181/922 | 119 | 119 | 100.73
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | OAKDLE - CLARKCRNS 36B 345 | 119 | 119 | 100.7
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | MEYER - CANDQUA 60 230 | LN:115:181/922 | 119 | 119 | 100.61
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | MARCY - COOPERS 345 SC | 119 | 119 | 100.45
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | MEYER - CANDQUA 60 230 | 119 | 119 | 100.34
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | LFYTE - CLARKCRNS 36A 345 | 119 | 119 | 100.29
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | GARDENVILL - DUNKIRK 74 230 | LN:115:181/922 | 119 | 119 | 100.29
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | GARDENVILL - DUNKIRK 73 230 | LN:115:181/922 | 119 | 119 | 100.25
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | HILLSIDE 230/115 4TR | LN:115:181/922 | 119 | 119 | 100.15
Dispatch 1 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | LN:115:181/922 | OAKDLE - CLARKCRNS 36B 345 | 119 | 119 | 100.06
Dispatch 2 | 130795 DEPEW115 115 130799 ERIE 115 115 1 | G:INDEK-OL | LN:115:181/922 | 119 | 119 | 100.01
| 130795 DEPEW115 115 130799 ERIE 115 115 1 Max |  |  |  |  | 125.4
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 124 | 159 | NConv
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 124 | 159 | NConv
Dispatch 2 | 130799 ERIE 115 115 130834 N.BRW115 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 124 | 159 | NConv
| 130799 ERIE 115 115 130834 N.BRW115 115 1 Max |  |  |  |  | 0
Dispatch 1 | 130806 GARDV115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 183 | NConv
Dispatch 1 | 130806 GARDV115 115 131467 LANGN115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 183 | NConv
Dispatch 2 | 130806 GARDV115 115 131467 LANGN115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 183 | NConv
Dispatch 2 | 130806 GARDV115 115 131467 LANGN115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 183 | NConv
| 130806 GARDV115 115 131467 LANGN115 115 1 Max |  |  |  |  | 0
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 238 | 306 | NConv
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 238 | 306 | NConv
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 238 | 306 | NConv
Dispatch 2 | 130815 HINMN115 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 238 | 306 | NConv
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 238 | 306 | 105.58
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | B:MEYER | 238 | 306 | 104.79
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | STOLLRD - GARDENVILL 66 230 | WTHRS - MEYER 230 | 238 | 306 | 104.75
Dispatch 1 | 130815 HINMN115 115 131611 HARIS115 115 1 | ROBINSON - STOLLRD 65 230 | Base Case | 238 | 306 | 103.94
| 130815 HINMN115 115 131611 HARIS115 115 1 Max |  |  |  |  | 105.58
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 220 | 280 | NConv
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 220 | 280 | NConv
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 220 | 280 | NConv
Dispatch 2 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 220 | 280 | NConv
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | WTHRS - MEYER 230 | STOLLRD - GARDENVILL 66 230 | 220 | 280 | 104.35
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STOLLRD - GARDENVILL 66 230 | B:MEYER | 220 | 280 | 103.48
Dispatch 1 | 130815 HINMN115 115 135452 LOCKPORT 115 1 | STOLLRD - GARDENVILL 66 230 | WTHRS - MEYER 230 | 220 | 280 | 103.43
| 130815 HINMN115 115 135452 LOCKPORT 115 1 Max |  |  |  |  | 104.35
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 139 | 181 | NConv
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 181 | NConv
Dispatch 1 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 181 | NConv
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 181 | NConv
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 181 | NConv
Dispatch 2 | 130834 N.BRW115 115 135437 CLSP-181 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 139 | 181 | NConv
| 130834 N.BRW115 115 135437 CLSP-181 115 1 Max |  |  |  |  | 0
Dispatch 1 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 215 | 275 | NConv
Dispatch 1 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 215 | 275 | NConv
Dispatch 2 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 215 | 275 | NConv
Dispatch 2 | 130846 ROBIN115 115 130853 A.LUD TP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 215 | 275 | NConv
| 130846 ROBIN115 115 130853 A.LUD TP 115 1 Max |  |  |  |  | 0
Dispatch 1 | 130846 ROBIN115 115 999989 STAR9 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 297 | 420 | NConv
Dispatch 1 | 130846 ROBIN115 115 999989 STAR9 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 297 | 420 | NConv
Dispatch 2 | 130846 ROBIN115 115 999989 STAR9 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 297 | 420 | NConv
Dispatch 2 | 130846 ROBIN115 115 999989 STAR9 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 297 | 420 | NConv
| 130846 ROBIN115 115 999989 STAR9 115 1 Max |  |  |  |  | 0
Dispatch 1 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 215 | 275 | NConv
Dispatch 1 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 215 | 275 | NConv
Dispatch 2 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 215 | 275 | NConv
Dispatch 2 | 130853 A.LUD TP 115 131611 HARIS115 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 215 | 275 | NConv
| 130853 A.LUD TP 115 131611 HARIS115 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | HILLSIDE 230/115 4TR | B:MEYER | 444 | 444 | NConv
Dispatch 1 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 444 | 444 | NConv
Dispatch 1 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 444 | 444 | NConv
Dispatch 2 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 444 | 444 | NConv
Dispatch 2 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 444 | 444 | NConv
Dispatch 2 | 135250 DUNKIRK 230 135251 S RIPLEY 230 1 | HILLSIDE 230/115 4TR | B:MEYER | 444 | 444 | NConv
| 135250 DUNKIRK 230 135251 S RIPLEY 230 1 Max |  |  |  |  | 0
Dispatch 1 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 148 | 148 | NConv
Dispatch 1 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 148 | 148 | NConv
Dispatch 2 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 148 | 148 | NConv
Dispatch 2 | 135254 S224-37 115 135451 HUNTLEY1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 148 | 148 | NConv
| 135254 S224-37 115 135451 HUNTLEY1 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 176 | NConv
Dispatch 1 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 176 | NConv
Dispatch 2 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 176 | NConv
Dispatch 2 | 135256 S214-36 115 135451 HUNTLEY1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 176 | NConv
| 135256 S214-36 115 135451 HUNTLEY1 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 1 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135268 CLVB-141 115 135292 SHALTNTP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
| 135268 CLVB-141 115 135292 SHALTNTP 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 1 | 135268 CLVB-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135268 CLVB-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
| 135268 CLVB-141 115 135483 S55-141 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 1 | 135269 CLVB-142 115 135445 FORD-142 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135269 CLVB-142 115 135445 FORD-142 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
| 135269 CLVB-142 115 135445 FORD-142 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 1 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135269 CLVB-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
| 135269 CLVB-142 115 135569 LAKEVIEW 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 1 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135271 DLTR-142 115 135569 LAKEVIEW 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
| 135271 DLTR-142 115 135569 LAKEVIEW 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 755 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 755 | NConv
Dispatch 1 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | Base Case | 566 | 755 | 108.18
Dispatch 2 | 135303 SAWYER77 230 135414 HUNTLEY2 230 1 | HUNTLEY - PACKARD 78 230 | Base Case | 566 | 755 | 102.65
| 135303 SAWYER77 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 108.18
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 755 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | STOLLRD - SHLDON 67 230 | 566 | 755 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE 230/115 4TR | STOLLRD - SHLDON 67 230 | 566 | 755 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 566 | 755 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | STOLLRD - SHLDON 67 230 | 566 | 755 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | CANDQUA - STNYRDG 68A 230 | SHLDON - STONYCR 230 | 566 | 755 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 755 | NConv
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HILLSIDE 230/115 4TR | STOLLRD - SHLDON 67 230 | 566 | 755 | NConv
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | Base Case | 566 | 755 | 108.12
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | NIAGARA - ROBINSON 64 345 | S:PA_HNTL77 | 566 | 755 | 104.33
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | STOLLRD - GARDENVILL 66 230 | S:PA_HNTL77 | 566 | 755 | 103.69
Dispatch 2 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | HUNTLEY - PACKARD 77 230 | Base Case | 566 | 755 | 102.59
Dispatch 1 | 135304 SAWYER78 230 135414 HUNTLEY2 230 2 | ROBINSON - STOLLRD 65 230 | S:PA_HNTL77 | 566 | 755 | 102.27
| 135304 SAWYER78 230 135414 HUNTLEY2 230 2 Max |  |  |  |  | 108.12
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 755 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 1 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
Dispatch 2 | 135305 SAWYER80 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 755 | NConv
| 135305 SAWYER80 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 0
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 1 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135305 SAWYER80 230 135419 SUNY-80 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 755 | NConv
| 135305 SAWYER80 230 135419 SUNY-80 230 1 Max |  |  |  |  | 0
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 755 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 1 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 755 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 755 | NConv
Dispatch 2 | 135306 SAWYER79 230 135414 HUNTLEY2 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 755 | NConv
| 135306 SAWYER79 230 135414 HUNTLEY2 230 1 Max |  |  |  |  | 0
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 710 | NConv
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 710 | NConv
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 710 | NConv
Dispatch 1 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 710 | NConv
Dispatch 2 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 710 | NConv
Dispatch 2 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 710 | NConv
Dispatch 2 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 710 | NConv
Dispatch 2 | 135306 SAWYER79 230 135418 SUNY-79 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 710 | NConv
| 135306 SAWYER79 230 135418 SUNY-79 230 1 Max |  |  |  |  | 0
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 129 | 236 | NConv
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 129 | 236 | NConv
Dispatch 2 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | Base Case | 129 | 236 | 121.89
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:181/922 | Base Case | 129 | 236 | 121.49
Dispatch 1 | 135327 AM.S-54 115 135450 GRDNVL1 115 1 | LN:115:182S | Base Case | 129 | 236 | 100.09
| 135327 AM.S-54 115 135450 GRDNVL1 115 1 Max |  |  |  |  | 121.89
Dispatch 1 | 135327 AM.S-54 115 135493 LUDWIG 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 187 | 236 | NConv
Dispatch 1 | 135327 AM.S-54 115 135493 LUDWIG 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 187 | 236 | NConv
| 135327 AM.S-54 115 135493 LUDWIG 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 699 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 699 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 699 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 699 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 699 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135418 SUNY-79 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 699 | NConv
| 135413 GRDNVL2 230 135418 SUNY-79 230 1 Max |  |  |  |  | 0
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 566 | 722 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 566 | 722 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 722 | NConv
Dispatch 1 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 722 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 566 | 722 | NConv
Dispatch 2 | 135413 GRDNVL2 230 135419 SUNY-80 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 566 | 722 | NConv
| 135413 GRDNVL2 230 135419 SUNY-80 230 1 Max |  |  |  |  | 0
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 189 | 250 | NConv
Dispatch 1 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 189 | 250 | NConv
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 189 | 250 | NConv
Dispatch 2 | 135415 PACKARD2 230 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 189 | 250 | NConv
| 135415 PACKARD2 230 135460 PACK(N)E 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | HILLSIDE 230/115 4TR | B:STOLE230 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | Base Case | 620 | 841 | 114.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 62 230 | 620 | 841 | 109.43
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | BECK - PACKARD BP76 230 | 620 | 841 | 109.09
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | BECK - PACKARD BP76 230 | B:PACKT4 | 620 | 841 | 108.34
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | NIAGARA - PACKARD 62 230 | 620 | 841 | 104.48
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - ROBINSON 64 345 | 620 | 841 | 103.69
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | B:PACKT4 | 620 | 841 | 101.83
| 135415 PACKARD2 230 147842 NIAGAR2W 230 1 Max |  |  |  |  | 114.3
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | HILLSIDE 230/115 4TR | B:STOLE230 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 2 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 620 | 841 | NConv
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | Base Case | 620 | 841 | 113.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | NIAGARA - PACKARD 61 230 | 620 | 841 | 109.21
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | BECK - PACKARD BP76 230 | 620 | 841 | 108.87
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - ROBINSON 64 345 | NIAGARA - PACKARD 61 230 | 620 | 841 | 104.11
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | NIAGARA - PACKARD 61 230 | NIAGARA - ROBINSON 64 345 | 620 | 841 | 103.32
Dispatch 1 | 135415 PACKARD2 230 147842 NIAGAR2W 230 2 | BECK - PACKARD BP76 230 | B:PACKT3 | 620 | 841 | 100.78
| 135415 PACKARD2 230 147842 NIAGAR2W 230 2 Max |  |  |  |  | 113.87
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | B:PACKT4 | 500 | 587 | 113.93
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | NIAGARA - PACKARD 61 230 | 500 | 587 | 107.94
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | NIAGARA - PACKARD 62 230 | 500 | 587 | 107.94
Dispatch 1 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 62 230 | B:PACKT3 | 500 | 587 | 105.43
Dispatch 2 | 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 | NIAGARA - PACKARD 61 230 | B:PACKT4 | 500 | 587 | 103.61
| 135415 PACKARD2 230 157062 BECK_#2_BP76 230 1 Max |  |  |  |  | 113.93
Dispatch 1 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 283 | NConv
Dispatch 1 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 283 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 283 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 283 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | Base Case | 239 | 283 | 107.89
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | NIAGARA 230/115 2TR | 239 | 283 | 104.82
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | TB:2/1:NI2 | 239 | 283 | 104.82
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | TB:2/1:NI2 | LN:115:130 | 239 | 283 | 104.71
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAGARA 230/115 2TR | LN:115:130 | 239 | 283 | 104.71
Dispatch 1 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | Base Case | 239 | 283 | 101.49
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 239 | 283 | 101.26
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 239 | 283 | 100.94
Dispatch 2 | 135435 SUMIT PK 115 135454 MLPN-129 115 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 239 | 283 | 100.72
| 135435 SUMIT PK 115 135454 MLPN-129 115 1 Max |  |  |  |  | 107.89
Dispatch 1 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 1 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
| 135435 SUMIT PK 115 135552 OXBOWNUG 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | CANDQUA - STNYRDG 68A 230 | B:STOLE230 | 139 | 183 | NConv
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 183 | NConv
Dispatch 1 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 183 | NConv
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 139 | 183 | NConv
Dispatch 2 | 135437 CLSP-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 139 | 183 | NConv
| 135437 CLSP-181 115 135495 YNG-181 115 1 Max |  |  |  |  | 0
Dispatch 2 | 135438 CLSP-54 115 135439 TUNGSTEN 115 1 | LN:115:181/922 | Base Case | 129 | 239 | 100.68
Dispatch 1 | 135438 CLSP-54 115 135439 TUNGSTEN 115 1 | LN:115:181/922 | Base Case | 129 | 239 | 100.07
| 135438 CLSP-54 115 135439 TUNGSTEN 115 1 Max |  |  |  |  | 100.68
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 1 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 2 | 135442 ECWA-181 115 135458 NI.B-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 226 | NConv
| 135442 ECWA-181 115 135458 NI.B-181 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 1 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 2 | 135442 ECWA-181 115 135495 YNG-181 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 226 | NConv
| 135442 ECWA-181 115 135495 YNG-181 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 1 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 2 | 135443 ECWA-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 226 | NConv
| 135443 ECWA-182 115 135459 NI.B-182 115 1 Max |  |  |  |  | 0
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 2 | 135443 ECWA-182 115 135496 YNG-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 226 | NConv
| 135443 ECWA-182 115 135496 YNG-182 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 1 | 135445 FORD-142 115 135484 S55-142 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135445 FORD-142 115 135484 S55-142 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
| 135445 FORD-142 115 135484 S55-142 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 1 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 226 | NConv
Dispatch 2 | 135449 GR.I-182 115 135459 NI.B-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 226 | NConv
| 135449 GR.I-182 115 135459 NI.B-182 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 200 | 265 | NConv
Dispatch 1 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 200 | 265 | NConv
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 200 | 265 | NConv
Dispatch 2 | 135449 GR.I-182 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 200 | 265 | NConv
| 135449 GR.I-182 115 135538 LONG-182 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 160 | 206 | NConv
Dispatch 1 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 160 | 206 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 160 | 206 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135453 LONG-180 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 160 | 206 | NConv
| 135450 GRDNVL1 115 135453 LONG-180 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 1 | 135450 GRDNVL1 115 135475 S139-141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135450 GRDNVL1 115 135475 S139-141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
| 135450 GRDNVL1 115 135475 S139-141 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | Base Case | 168 | 206 | 119.38
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAGARA 230/115 2TR | 168 | 206 | 117.26
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | TB:2/1:NI2 | 168 | 206 | 117.26
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | LN:115:133 | 168 | 206 | 117.14
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | LN:115:133 | 168 | 206 | 117.14
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:133 | 168 | 206 | 111.26
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAGARA - ROBINSON 64 345 | 168 | 206 | 110.55
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | Base Case | 168 | 206 | 110.29
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | LN:115:133 | 168 | 206 | 110.03
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | Base Case | 168 | 206 | 109.31
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:Hunt68 | 168 | 206 | 108.65
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:PACKT4 | 168 | 206 | 108.33
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:133 | 168 | 206 | 107.77
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAG - NEWROCH 1 345 | 168 | 206 | 107.63
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | PACKARD 230/115 4TR | 168 | 206 | 106.95
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | TB:2/1:PK4 | 168 | 206 | 106.95
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:PK4 | LN:115:133 | 168 | 206 | 106.82
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | PACKARD 230/115 4TR | LN:115:133 | 168 | 206 | 106.82
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:Hunt67 | 168 | 206 | 106.63
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | TB:2/1:NI2 | 168 | 206 | 106.43
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | NIAGARA 230/115 2TR | 168 | 206 | 106.43
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI2 | LN:115:129 | 168 | 206 | 106.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 2TR | LN:115:129 | 168 | 206 | 106.27
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:133 | 168 | 206 | 106.25
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:133 | 168 | 206 | 106.2
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | SOMERSET - NEWROCH 1 345 | 168 | 206 | 106.18
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | S:PA_HNTL77 | 168 | 206 | 105.82
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | S:PA_HNTL78 | 168 | 206 | 105.72
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | HUNTLEY - PACKARD 78 230 | 168 | 206 | 105.72
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | HUNTLEY - PACKARD 77 230 | 168 | 206 | 105.68
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:133 | 168 | 206 | 105.28
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAGARA - ROBINSON 64 345 | 168 | 206 | 104.46
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:908 NY | 168 | 206 | 104.46
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:908 NY | LN:115:133 | 168 | 206 | 104.39
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:100 | 168 | 206 | 103.38
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:100 | LN:115:133 | 168 | 206 | 103.3
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | LN:115:133 | 168 | 206 | 103.23
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:133 | 168 | 206 | 102.76
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:133 | 168 | 206 | 102.75
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:GARD72&79 | 168 | 206 | 102.67
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | S:HNT_GRD80 | 168 | 206 | 102.59
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | HUNTLEY - GARDENVILL 79 230 | 168 | 206 | 102.51
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | HUNTLEY - GARDENVILL 80 230 | 168 | 206 | 102.5
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | TB:2/1:ROB | 168 | 206 | 102.36
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:ROB | LN:115:133 | 168 | 206 | 102.24
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:Hunt68 | 168 | 206 | 102.11
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:GARD73&80 | 168 | 206 | 101.95
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:129 | 168 | 206 | 101.82
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:133 | 168 | 206 | 101.28
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | B:STOLE230 | 168 | 206 | 101.21
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | G:LOCKPORT | 168 | 206 | 101.2
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | LN:115:129 | 168 | 206 | 101.18
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | NIAGARA - ROBINSON 64 345 | 168 | 206 | 101.16
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:133 | 168 | 206 | 101.08
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:101 | 168 | 206 | 101.07
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:133 | 168 | 206 | 101.04
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | STOLLRD - GARDENVILL 66 230 | 168 | 206 | 101
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:129 | Base Case | 168 | 206 | 100.95
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:LOCKPORT | LN:115:133 | 168 | 206 | 100.94
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:101 | LN:115:133 | 168 | 206 | 100.91
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAGARA 230/115 1TR | 168 | 206 | 100.87
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | TB:2/1:NI1 | 168 | 206 | 100.87
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | TB:2/1:NI1 | LN:115:133 | 168 | 206 | 100.86
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | NIAGARA 230/115 1TR | LN:115:133 | 168 | 206 | 100.86
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | ROBINSON - STOLLRD 65 230 | 168 | 206 | 100.85
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:102 | 168 | 206 | 100.84
Dispatch 1 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | NIAG - NEWROCH 1 345 | 168 | 206 | 100.82
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:102 | LN:115:133 | 168 | 206 | 100.69
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:907 NY | 168 | 206 | 100.67
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | First:Lockport_907 | 168 | 206 | 100.64
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | FARMVLY - HOMERCTY | 168 | 206 | 100.59
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:907 NY | LN:115:133 | 168 | 206 | 100.56
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | R:HC-FV_37&W-F_171 | 168 | 206 | 100.55
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:120 | 168 | 206 | 100.53
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | First:Lockport_907 | LN:115:133 | 168 | 206 | 100.52
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:120 | LN:115:133 | 168 | 206 | 100.4
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:37 | 168 | 206 | 100.3
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:37 | LN:115:133 | 168 | 206 | 100.15
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | G:DUPONT46 | LN:115:133 | 168 | 206 | 100.13
Dispatch 2 | 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 | LN:115:133 | LN:115:36 | 168 | 206 | 100.05
| 135451 HUNTLEY1 115 135498 ZRMN-130 115 1 Max |  |  |  |  | 119.38
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | Base Case | 168 | 206 | 118.77
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA 230/115 2TR | 168 | 206 | 116.2
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:NI2 | 168 | 206 | 116.2
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI2 | LN:115:130 | 168 | 206 | 116.09
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | LN:115:130 | 168 | 206 | 116.09
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 168 | 206 | 110.65
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 168 | 206 | 109.91
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | Base Case | 168 | 206 | 109.76
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 168 | 206 | 109.73
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt68 | 168 | 206 | 108.35
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:130 | 168 | 206 | 107.49
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:PACKT4 | 168 | 206 | 107.32
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAG - NEWROCH 1 345 | 168 | 206 | 107.3
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt67 | 168 | 206 | 106.05
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | PACKARD 230/115 4TR | 168 | 206 | 105.95
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:PK4 | 168 | 206 | 105.95
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | SOMERSET - NEWROCH 1 345 | 168 | 206 | 105.86
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:PK4 | LN:115:130 | 168 | 206 | 105.84
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | LN:115:130 | 168 | 206 | 105.84
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:130 | 168 | 206 | 105.7
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:130 | 168 | 206 | 105.65
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL77 | 168 | 206 | 105.24
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL78 | 168 | 206 | 105.15
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 78 230 | 168 | 206 | 105.15
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 77 230 | 168 | 206 | 105.1
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 168 | 206 | 104.73
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:908 NY | 168 | 206 | 103.9
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 168 | 206 | 103.88
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:908 NY | LN:115:130 | 168 | 206 | 103.86
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 168 | 206 | 102.95
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:100 | 168 | 206 | 102.83
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:100 | LN:115:130 | 168 | 206 | 102.78
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:130 | 168 | 206 | 102.24
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:130 | 168 | 206 | 102.23
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:GARD72&79 | 168 | 206 | 102.13
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | S:HNT_GRD80 | 168 | 206 | 102.05
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - GARDENVILL 79 230 | 168 | 206 | 101.97
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - GARDENVILL 80 230 | 168 | 206 | 101.96
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:ROB | 168 | 206 | 101.81
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:ROB | LN:115:130 | 168 | 206 | 101.73
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt68 | 168 | 206 | 101.57
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:GARD73&80 | 168 | 206 | 101.41
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:130 | 168 | 206 | 100.81
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:130 | 168 | 206 | 100.78
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | G:LOCKPORT | 168 | 206 | 100.69
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | B:STOLE230 | 168 | 206 | 100.69
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | G:LOCKPORT | LN:115:130 | 168 | 206 | 100.59
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:101 | 168 | 206 | 100.55
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:130 | 168 | 206 | 100.55
Dispatch 1 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAG - NEWROCH 1 345 | 168 | 206 | 100.54
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | STOLLRD - GARDENVILL 66 230 | 168 | 206 | 100.48
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:101 | LN:115:130 | 168 | 206 | 100.42
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | TB:2/1:NI1 | LN:115:130 | 168 | 206 | 100.34
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | LN:115:130 | 168 | 206 | 100.34
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | ROBINSON - STOLLRD 65 230 | 168 | 206 | 100.33
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA 230/115 1TR | 168 | 206 | 100.32
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:NI1 | 168 | 206 | 100.32
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:102 | 168 | 206 | 100.32
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:102 | LN:115:130 | 168 | 206 | 100.2
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:907 NY | 168 | 206 | 100.13
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | First:Lockport_907 | 168 | 206 | 100.1
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | FARMVLY - HOMERCTY | 168 | 206 | 100.08
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:907 NY | LN:115:130 | 168 | 206 | 100.06
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | R:HC-FV_37&W-F_171 | 168 | 206 | 100.04
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | LN:115:130 | LN:115:120 | 168 | 206 | 100.02
Dispatch 2 | 135451 HUNTLEY1 115 135562 S214-133 115 1 | First:Lockport_907 | LN:115:130 | 168 | 206 | 100.02
| 135451 HUNTLEY1 115 135562 S214-133 115 1 Max |  |  |  |  | 118.77
Dispatch 1 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 233 | 318 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 233 | 318 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 233 | 318 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135464 SANBORNT 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 233 | 318 | NConv
| 135452 LOCKPORT 115 135464 SANBORNT 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 199 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 199 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 174 | 199 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 174 | 199 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | LN:115:101 | LN:115:102 | 174 | 199 | 103.88
Dispatch 2 | 135452 LOCKPORT 115 135467 SHAW-103 115 1 | LN:115:102 | LN:115:101 | 174 | 199 | 103.87
| 135452 LOCKPORT 115 135467 SHAW-103 115 1 Max |  |  |  |  | 103.88
Dispatch 1 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 233 | 318 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 233 | 318 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 233 | 318 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135510 SHAW-102 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 233 | 318 | NConv
| 135452 LOCKPORT 115 135510 SHAW-102 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 180 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 143 | 180 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 180 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135851 SHEL-113 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 143 | 180 | NConv
| 135452 LOCKPORT 115 135851 SHEL-113 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 130 | 165 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 130 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 130 | 165 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135865 NAKR-108 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 130 | 165 | NConv
| 135452 LOCKPORT 115 135865 NAKR-108 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 131 | 158 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 131 | 158 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 131 | 158 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 131 | 158 | NConv
| 135452 LOCKPORT 115 135867 OAKFLDTP 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 199 | 199 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 199 | 199 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 199 | 199 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135872 SOUR-111 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 199 | 199 | NConv
| 135452 LOCKPORT 115 135872 SOUR-111 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 220 | 280 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 220 | 280 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135875 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 220 | 280 | NConv
| 135452 LOCKPORT 115 135875 TELRDTP1 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 180 | NConv
Dispatch 1 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 143 | 180 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 143 | 180 | NConv
Dispatch 2 | 135452 LOCKPORT 115 135876 TELRDTP1 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 143 | 180 | NConv
| 135452 LOCKPORT 115 135876 TELRDTP1 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 1 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | Base Case | 239 | 298 | 116.54
Dispatch 1 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | Base Case | 239 | 298 | 110.14
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | NIAGARA 230/115 2TR | 239 | 298 | 106.48
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | TB:2/1:NI2 | 239 | 298 | 106.48
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | TB:2/1:NI2 | LN:115:130 | 239 | 298 | 106.37
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAGARA 230/115 2TR | LN:115:130 | 239 | 298 | 106.37
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 239 | 298 | 103.13
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 239 | 298 | 102.91
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 239 | 298 | 102.62
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | B:Hunt68 | 239 | 298 | 101.56
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:130 | 239 | 298 | 101.22
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | NIAG - NEWROCH 1 345 | 239 | 298 | 101.05
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | B:PACKT4 | 239 | 298 | 100.65
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | G:OXBOWNUG | LN:115:130 | 239 | 298 | 100.54
Dispatch 2 | 135454 MLPN-129 115 135461 PACK(S)W 115 1 | LN:115:130 | SOMERSET - NEWROCH 1 345 | 239 | 298 | 100.01
| 135454 MLPN-129 115 135461 PACK(S)W 115 1 Max |  |  |  |  | 116.54
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | Base Case | 239 | 298 | 120.54
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | Base Case | 239 | 298 | 113.91
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | Base Case | 239 | 298 | 109.74
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | TB:2/1:NI2 | 239 | 298 | 109.56
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | NIAGARA 230/115 2TR | 239 | 298 | 109.56
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | TB:2/1:NI2 | LN:115:129 | 239 | 298 | 109.45
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAGARA 230/115 2TR | LN:115:129 | 239 | 298 | 109.45
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:129 | 239 | 298 | 106.61
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | LN:115:129 | 239 | 298 | 106.49
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | NIAGARA - ROBINSON 64 345 | 239 | 298 | 106.09
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | B:Hunt68 | 239 | 298 | 105.03
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:129 | 239 | 298 | 104.72
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | NIAG - NEWROCH 1 345 | 239 | 298 | 104.54
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | B:PACKT4 | 239 | 298 | 103.66
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | Base Case | 239 | 298 | 103.5
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | SOMERSET - NEWROCH 1 345 | 239 | 298 | 103.46
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | B:Hunt67 | 239 | 298 | 103.33
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:129 | 239 | 298 | 103.07
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:129 | 239 | 298 | 103.03
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | S:PA_HNTL77 | 239 | 298 | 102.76
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | HUNTLEY - PACKARD 78 230 | 239 | 298 | 102.68
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | S:PA_HNTL78 | 239 | 298 | 102.68
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | PACKARD 230/115 4TR | 239 | 298 | 102.68
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | TB:2/1:PK4 | 239 | 298 | 102.68
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | HUNTLEY - PACKARD 77 230 | 239 | 298 | 102.65
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | TB:2/1:PK4 | LN:115:129 | 239 | 298 | 102.58
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | PACKARD 230/115 4TR | LN:115:129 | 239 | 298 | 102.58
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:129 | 239 | 298 | 102.32
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | LN:115:908 NY | 239 | 298 | 101.77
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:908 NY | LN:115:129 | 239 | 298 | 101.72
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | NIAGARA - ROBINSON 64 345 | 239 | 298 | 101.71
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAG - NEWROCH 1 345 | LN:115:129 | 239 | 298 | 101.3
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | NIAGARA 230/115 2TR | 239 | 298 | 101.01
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | TB:2/1:NI2 | 239 | 298 | 101.01
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | LN:115:100 | 239 | 298 | 100.96
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | TB:2/1:NI2 | LN:115:133 | 239 | 298 | 100.92
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | NIAGARA 230/115 2TR | LN:115:133 | 239 | 298 | 100.92
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:100 | LN:115:129 | 239 | 298 | 100.9
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:129 | 239 | 298 | 100.58
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:129 | 239 | 298 | 100.58
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | B:GARD72&79 | 239 | 298 | 100.52
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:133 | LN:115:129 | 239 | 298 | 100.47
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | LN:115:133 | 239 | 298 | 100.46
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | S:HNT_GRD80 | 239 | 298 | 100.46
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | HUNTLEY - GARDENVILL 79 230 | 239 | 298 | 100.4
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | HUNTLEY - GARDENVILL 80 230 | 239 | 298 | 100.39
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | TB:2/1:ROB | 239 | 298 | 100.23
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | TB:2/1:ROB | LN:115:129 | 239 | 298 | 100.16
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | G:OXBOWNUG | LN:115:129 | 239 | 298 | 100.13
Dispatch 1 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | B:Hunt68 | 239 | 298 | 100.11
Dispatch 2 | 135455 MLPN-130 115 135461 PACK(S)W 115 1 | LN:115:129 | B:GARD73&80 | 239 | 298 | 100
| 135455 MLPN-130 115 135461 PACK(S)W 115 1 Max |  |  |  |  | 120.54
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | Base Case | 239 | 298 | 111.87
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:133 | Base Case | 239 | 298 | 106.8
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | Base Case | 239 | 298 | 105.24
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | TB:2/1:NI2 | 239 | 298 | 102.68
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:129 | NIAGARA 230/115 2TR | 239 | 298 | 102.68
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | TB:2/1:NI2 | LN:115:129 | 239 | 298 | 102.55
Dispatch 2 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | NIAGARA 230/115 2TR | LN:115:129 | 239 | 298 | 102.55
Dispatch 1 | 135455 MLPN-130 115 135469 SUMIT PK 115 1 | LN:115:133 | Base Case | 239 | 298 | 100.49
| 135455 MLPN-130 115 135469 SUMIT PK 115 1 Max |  |  |  |  | 111.87
Dispatch 1 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 176 | 240 | NConv
Dispatch 1 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 176 | 240 | NConv
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 176 | 240 | NConv
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 176 | 240 | NConv
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | LN:115:101 | LN:115:102 | 176 | 240 | 100.52
Dispatch 2 | 135456 MTNS-120 115 135470 SWAN-103 115 1 | LN:115:102 | LN:115:101 | 176 | 240 | 100.52
| 135456 MTNS-120 115 135470 SWAN-103 115 1 Max |  |  |  |  | 100.52
Dispatch 1 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 176 | 258 | NConv
Dispatch 1 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 176 | 258 | NConv
Dispatch 2 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 176 | 258 | NConv
Dispatch 2 | 135456 MTNS-120 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 176 | 258 | NConv
| 135456 MTNS-120 115 147850 NIAG115E 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 160 | 206 | NConv
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 160 | 206 | NConv
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 160 | 206 | NConv
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 160 | 206 | NConv
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | Base Case | 160 | 206 | 119.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | Base Case | 160 | 206 | 119.1
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | Base Case | 160 | 206 | 111.5
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | Base Case | 160 | 206 | 110.89
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | Base Case | 160 | 206 | 106.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 160 | 206 | 105.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 160 | 206 | 105.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 160 | 206 | 105.24
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 160 | 206 | 105.23
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | LN:115:180 | 160 | 206 | 105.06
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:182N | 160 | 206 | 104.99
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | Base Case | 160 | 206 | 104.87
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:Hunt68 | 160 | 206 | 104.86
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | Base Case | 160 | 206 | 104.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:195 | Base Case | 160 | 206 | 104.72
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | TB:2/1:PK3 | Base Case | 160 | 206 | 104.58
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | Base Case | 160 | 206 | 103.82
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:191 | Base Case | 160 | 206 | 103.67
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:192 | Base Case | 160 | 206 | 103.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | Base Case | 160 | 206 | 103.12
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:Hunt68 | 160 | 206 | 103.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:54/921 | Base Case | 160 | 206 | 102.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:Hunt67 | 160 | 206 | 102.39
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:180 | LN:115:182S | 160 | 206 | 102.25
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | LN:115:180 | 160 | 206 | 102.21
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | R:HC-FV_37&W-F_171 | Base Case | 160 | 206 | 102.05
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | FARMVLY - HOMERCTY | Base Case | 160 | 206 | 102.04
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:182N | 160 | 206 | 101.95
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:182N | 160 | 206 | 101.9
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | S:PA_HNTL77 | 160 | 206 | 101.52
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 79 230 | Base Case | 160 | 206 | 101.42
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - GARDENVILL 80 230 | Base Case | 160 | 206 | 101.41
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | HUNTLEY - PACKARD 78 230 | 160 | 206 | 101.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | S:PA_HNTL78 | 160 | 206 | 101.4
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | HUNTLEY - PACKARD 77 230 | 160 | 206 | 101.33
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | B:STOLE230 | 160 | 206 | 101.18
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 160 | 206 | 101.17
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 160 | 206 | 101.17
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 160 | 206 | 101.17
Dispatch 1 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 160 | 206 | 101.16
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:182N | 160 | 206 | 100.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LFYTE - CLARKCRNS 36A 345 | Base Case | 160 | 206 | 100.92
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | B:Hunt67 | 160 | 206 | 100.79
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:182S | 160 | 206 | 100.56
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:182S | 160 | 206 | 100.51
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:182N | 160 | 206 | 100.47
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | OAKDLE - CLARKCRNS 36B 345 | Base Case | 160 | 206 | 100.46
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | ROBINSON - STOLLRD 65 230 | 160 | 206 | 100.43
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | STOLLRD - GARDENVILL 66 230 | 160 | 206 | 100.34
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:101 | Base Case | 160 | 206 | 100.09
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182S | S:PA_HNTL77 | 160 | 206 | 100.07
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | FARMVLY - HOMERCTY | 160 | 206 | 100.02
Dispatch 2 | 135458 NI.B-181 115 135460 PACK(N)E 115 1 | LN:115:182N | R:HC-FV_37&W-F_171 | 160 | 206 | 100.01
| 135458 NI.B-181 115 135460 PACK(N)E 115 1 Max |  |  |  |  | 119.42
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 200 | 265 | NConv
Dispatch 1 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 200 | 265 | NConv
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 200 | 265 | NConv
Dispatch 2 | 135460 PACK(N)E 115 135538 LONG-182 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 200 | 265 | NConv
| 135460 PACK(N)E 115 135538 LONG-182 115 1 Max |  |  |  |  | 0
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:194 | LN:115:195 | 273 | 351 | 139.06
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:195 | LN:115:194 | 273 | 351 | 139
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:194 | LN:115:195 | 273 | 351 | 119.76
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:195 | LN:115:194 | 273 | 351 | 119.7
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 1 | LN:115:195 | Base Case | 273 | 351 | 100.6
| 135461 PACK(S)W 115 147851 NIAG115W 115 1 Max |  |  |  |  | 139.06
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:193 | LN:115:195 | 273 | 351 | 139.06
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:195 | LN:115:193 | 273 | 351 | 139
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:193 | LN:115:195 | 273 | 351 | 119.76
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:195 | LN:115:193 | 273 | 351 | 119.7
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 2 | LN:115:195 | Base Case | 273 | 351 | 100.6
| 135461 PACK(S)W 115 147851 NIAG115W 115 2 Max |  |  |  |  | 139.06
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 273 | 351 | NConv
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:193 | LN:115:194 | 273 | 351 | 129.48
Dispatch 2 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:194 | LN:115:193 | 273 | 351 | 129.48
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:193 | LN:115:194 | 273 | 351 | 109.94
Dispatch 1 | 135461 PACK(S)W 115 147851 NIAG115W 115 3 | LN:115:194 | LN:115:193 | 273 | 351 | 109.94
| 135461 PACK(S)W 115 147851 NIAG115W 115 3 Max |  |  |  |  | 129.48
Dispatch 1 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 247 | 328 | NConv
Dispatch 1 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 247 | 328 | NConv
Dispatch 2 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 247 | 328 | NConv
Dispatch 2 | 135464 SANBORNT 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 247 | 328 | NConv
| 135464 SANBORNT 115 147850 NIAG115E 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 1 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:101 | LN:115:102 | 168 | 206 | 107.75
Dispatch 2 | 135467 SHAW-103 115 135470 SWAN-103 115 1 | LN:115:102 | LN:115:101 | 168 | 206 | 107.74
| 135467 SHAW-103 115 135470 SWAN-103 115 1 Max |  |  |  |  | 107.75
Dispatch 1 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 275 | 354 | NConv
Dispatch 1 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 275 | 354 | NConv
Dispatch 2 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 275 | 354 | NConv
Dispatch 2 | 135468 SNBRN102 115 135510 SHAW-102 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 275 | 354 | NConv
| 135468 SNBRN102 115 135510 SHAW-102 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 247 | 328 | NConv
Dispatch 1 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 247 | 328 | NConv
Dispatch 2 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 247 | 328 | NConv
Dispatch 2 | 135468 SNBRN102 115 147850 NIAG115E 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 247 | 328 | NConv
| 135468 SNBRN102 115 147850 NIAG115E 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 1 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135469 SUMIT PK 115 135498 ZRMN-130 115 1 | LN:115:133 | Base Case | 239 | 298 | 105.53
| 135469 SUMIT PK 115 135498 ZRMN-130 115 1 Max |  |  |  |  | 105.53
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 1 | 135475 S139-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 88 | 108 | NConv
Dispatch 2 | 135475 S139-141 115 135483 S55-141 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 88 | 108 | NConv
| 135475 S139-141 115 135483 S55-141 115 1 Max |  |  |  |  | 0
Dispatch 1 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 1 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 239 | 298 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | LN:115:130 | Base Case | 239 | 298 | 107.93
Dispatch 1 | 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 | LN:115:130 | Base Case | 239 | 298 | 101.58
| 135497 ZRMN-133 115 135552 OXBOWNUG 115 1 Max |  |  |  |  | 107.93
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 168 | 206 | NConv
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | Base Case | 168 | 206 | 121.94
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA 230/115 2TR | 168 | 206 | 118.71
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:NI2 | 168 | 206 | 118.71
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | LN:115:130 | 168 | 206 | 118.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | LN:115:130 | 168 | 206 | 118.59
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 168 | 206 | 113.25
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | Base Case | 168 | 206 | 112.92
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 168 | 206 | 112.51
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 168 | 206 | 112.39
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt68 | 168 | 206 | 110.96
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:130 | 168 | 206 | 110.13
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAG - NEWROCH 1 345 | 168 | 206 | 109.93
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:PACKT4 | 168 | 206 | 109.9
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt67 | 168 | 206 | 108.64
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | PACKARD 230/115 4TR | 168 | 206 | 108.52
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:PK4 | 168 | 206 | 108.52
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SOMERSET - NEWROCH 1 345 | 168 | 206 | 108.49
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:PK4 | LN:115:130 | 168 | 206 | 108.41
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | LN:115:130 | 168 | 206 | 108.41
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:130 | 168 | 206 | 108.3
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:130 | 168 | 206 | 108.25
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL77 | 168 | 206 | 107.84
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL78 | 168 | 206 | 107.75
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 78 230 | 168 | 206 | 107.75
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 77 230 | 168 | 206 | 107.7
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | LN:115:130 | 168 | 206 | 107.33
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:908 NY | 168 | 206 | 106.5
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA - ROBINSON 64 345 | 168 | 206 | 106.47
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:908 NY | LN:115:130 | 168 | 206 | 106.46
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | LN:115:130 | 168 | 206 | 105.57
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:100 | 168 | 206 | 105.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:100 | LN:115:130 | 168 | 206 | 105.37
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 79 230 | LN:115:130 | 168 | 206 | 104.84
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - GARDENVILL 80 230 | LN:115:130 | 168 | 206 | 104.83
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:GARD72&79 | 168 | 206 | 104.73
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | S:HNT_GRD80 | 168 | 206 | 104.64
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - GARDENVILL 79 230 | 168 | 206 | 104.56
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - GARDENVILL 80 230 | 168 | 206 | 104.55
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:ROB | 168 | 206 | 104.41
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:ROB | LN:115:130 | 168 | 206 | 104.32
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt68 | 168 | 206 | 104.17
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:GARD73&80 | 168 | 206 | 104.01
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | LN:115:130 | 168 | 206 | 103.42
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | ROBINSON - STOLLRD 65 230 | LN:115:130 | 168 | 206 | 103.37
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | G:LOCKPORT | 168 | 206 | 103.29
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:STOLE230 | 168 | 206 | 103.28
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:LOCKPORT | LN:115:130 | 168 | 206 | 103.19
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAG - NEWROCH 1 345 | 168 | 206 | 103.14
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:101 | 168 | 206 | 103.14
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | STOLLRD - GARDENVILL 66 230 | LN:115:130 | 168 | 206 | 103.14
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | STOLLRD - GARDENVILL 66 230 | 168 | 206 | 103.07
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:101 | LN:115:130 | 168 | 206 | 103.02
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA - ROBINSON 64 345 | Base Case | 168 | 206 | 102.99
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI1 | LN:115:130 | 168 | 206 | 102.93
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 1TR | LN:115:130 | 168 | 206 | 102.93
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | ROBINSON - STOLLRD 65 230 | 168 | 206 | 102.92
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:102 | 168 | 206 | 102.91
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAGARA 230/115 1TR | 168 | 206 | 102.91
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | TB:2/1:NI1 | 168 | 206 | 102.91
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - NEWROCH 1 345 | Base Case | 168 | 206 | 102.83
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:102 | LN:115:130 | 168 | 206 | 102.79
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:907 NY | 168 | 206 | 102.72
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | First:Lockport_907 | 168 | 206 | 102.69
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | FARMVLY - HOMERCTY | 168 | 206 | 102.68
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:907 NY | LN:115:130 | 168 | 206 | 102.65
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | R:HC-FV_37&W-F_171 | 168 | 206 | 102.63
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:120 | 168 | 206 | 102.61
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | First:Lockport_907 | LN:115:130 | 168 | 206 | 102.61
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:DUPONT46 | LN:115:130 | 168 | 206 | 102.6
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:120 | LN:115:130 | 168 | 206 | 102.51
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:37 | 168 | 206 | 102.33
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:37 | LN:115:130 | 168 | 206 | 102.21
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:36 | 168 | 206 | 102.08
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAG - KINTIGH 345 | LN:115:130 | 168 | 206 | 102.01
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:36 | LN:115:130 | 168 | 206 | 101.95
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | PACKARD 230/115 3TR | 168 | 206 | 101.91
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 3TR | LN:115:130 | 168 | 206 | 101.89
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:Hunt67 | 168 | 206 | 101.77
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LFYTE - CLARKCRNS 36A 345 | LN:115:130 | 168 | 206 | 101.7
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | B:PACKT3 | 168 | 206 | 101.69
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | NIAG - KINTIGH 345 | 168 | 206 | 101.67
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | SOMERSET - NEWROCH 1 345 | 168 | 206 | 101.56
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 4 | LN:115:130 | 168 | 206 | 101.5
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 5 | LN:115:130 | 168 | 206 | 101.5
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 6 | LN:115:130 | 168 | 206 | 101.5
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | G:NIAG. 7 | LN:115:130 | 168 | 206 | 101.49
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | LN:115:130 | 168 | 206 | 101.38
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | OAKDLE - CLARKCRNS 36B 345 | LN:115:130 | 168 | 206 | 101.36
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | LN:115:130 | 168 | 206 | 101.32
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 168 | 206 | 100.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 168 | 206 | 100.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 168 | 206 | 100.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 168 | 206 | 100.98
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | SOMERSET - NEWROCH 1 345 | Base Case | 168 | 206 | 100.88
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL77 | 168 | 206 | 100.87
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | S:PA_HNTL78 | 168 | 206 | 100.77
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 78 230 | 168 | 206 | 100.77
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | HUNTLEY - PACKARD 77 230 | 168 | 206 | 100.73
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:130 | LN:115:908 NY | 168 | 206 | 100.18
Dispatch 1 | 135497 ZRMN-133 115 135562 S214-133 115 1 | LN:115:908 NY | LN:115:130 | 168 | 206 | 100.16
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | B:PACKT4 | 168 | 206 | 100.11
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | B:PACKT4 | 168 | 206 | 100.11
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:PK4 | TB:2/1:NI2 | 168 | 206 | 100.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:PK4 | NIAGARA 230/115 2TR | 168 | 206 | 100.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | PACKARD 230/115 4TR | 168 | 206 | 100.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | TB:2/1:NI2 | TB:2/1:PK4 | 168 | 206 | 100.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | PACKARD 230/115 4TR | 168 | 206 | 100.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | NIAGARA 230/115 2TR | TB:2/1:PK4 | 168 | 206 | 100.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | TB:2/1:NI2 | 168 | 206 | 100.06
Dispatch 2 | 135497 ZRMN-133 115 135562 S214-133 115 1 | PACKARD 230/115 4TR | NIAGARA 230/115 2TR | 168 | 206 | 100.06
| 135497 ZRMN-133 115 135562 S214-133 115 1 Max |  |  |  |  | 121.94
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 192 | 288 | NConv
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 192 | 288 | NConv
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAG - NEWROCH 1 345 | 192 | 288 | NConv
Dispatch 2 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | SOMERSET - NEWROCH 1 345 | 192 | 288 | NConv
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | Base Case | 192 | 288 | 126.2
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | Base Case | 192 | 288 | 124.11
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | Base Case | 192 | 288 | 118.69
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | Base Case | 192 | 288 | 116.97
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 4 | Base Case | 192 | 288 | 115.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 5 | Base Case | 192 | 288 | 115.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 6 | Base Case | 192 | 288 | 115.23
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:NIAG. 7 | Base Case | 192 | 288 | 115.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:908 NY | Base Case | 192 | 288 | 112.15
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | B:PACKT3 | 192 | 288 | 111.74
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAGARA - ROBINSON 64 345 | 192 | 288 | 111.26
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:100 | Base Case | 192 | 288 | 109.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | NIAG - KINTIGH 345 | 192 | 288 | 109.16
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | PACKARD 230/115 3TR | 192 | 288 | 107.96
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | B:PACKT3 | 192 | 288 | 107.72
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | NIAG - NEWROCH 1 345 | 192 | 288 | 107.45
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | NIAGARA - ROBINSON 64 345 | 192 | 288 | 106.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | Base Case | 192 | 288 | 106.5
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | TB:2/1:ROB | Base Case | 192 | 288 | 106.44
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | Base Case | 192 | 288 | 106.41
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | NIAGARA - ROBINSON 64 345 | 192 | 288 | 105.88
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | B:Hunt68 | 192 | 288 | 105.54
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | S:PA_HNTL77 | 192 | 288 | 105.34
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | S:PA_HNTL78 | 192 | 288 | 105.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 77 230 | HUNTLEY - PACKARD 78 230 | 192 | 288 | 105.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - PACKARD 78 230 | HUNTLEY - PACKARD 77 230 | 192 | 288 | 105.33
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | PACKARD 230/115 3TR | 192 | 288 | 105.07
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | SOMERSET - NEWROCH 1 345 | 192 | 288 | 103.71
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - KINTIGH 345 | NIAG - NEWROCH 1 345 | 192 | 288 | 103.53
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | B:PACKT3 | 192 | 288 | 102.99
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | LN:115:907 NY | Base Case | 192 | 288 | 101.78
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | First:Lockport_907 | Base Case | 192 | 288 | 101.62
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAGARA - ROBINSON 64 345 | B:Hunt67 | 192 | 288 | 101.46
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | NIAG - NEWROCH 1 345 | LN:115:908 NY | 192 | 288 | 100.56
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 79 230 | Base Case | 192 | 288 | 100.48
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | HUNTLEY - GARDENVILL 80 230 | Base Case | 192 | 288 | 100.47
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | SOMERSET - NEWROCH 1 345 | PACKARD 230/115 3TR | 192 | 288 | 100.45
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | G:LOCKPORT | Base Case | 192 | 288 | 100.27
Dispatch 1 | 147850 NIAG115E 115 147842 NIAGAR2W 230 1 | PACKARD 230/115 3TR | NIAG - NEWROCH 1 345 | 192 | 288 | 100.12
| 147850 NIAG115E 115 147842 NIAGAR2W 230 1 Max |  |  |  |  | 126.2
| Grand Max |  |  |  |  | 139.06

## Ratings_Minimum_Criteria
SERIES REACTORS ON 77 & 78 LINES IN-SERVICE
N-1 (Emergency Transfer Criteria) - 1000 MW Ontario Import
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
135497 | ZRMN-133 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135498 | ZRMN-130 | 115 | 1 | Not Available
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
N-1 Thermal Normal - 0 MW Ontario Import
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
135458 | NI.B-181 | 115 | 135460 | PACK(N)E | 115 | 1 | LN | 181 | A - Conductor | A - Conductor | A - Conductor
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
130847 | ROLL | 115 | 130857 | STOLE115 | 115 | 1 | Not Available
135461 | PACK (S)W | 115 | 147851 | NIAG115W | 115 | 3 | LN | 195 | A - Conductor | A - Conductor | A - Conductor
135449 | GR.I-182 | 115 | 135459 | NI.B-182 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135498 | ZRMN-130 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135460 | PACK(N)E | 115 | 135538 | LONG-182 | 115 | 1 | Not Available
135460 | PACK(N)E | 115 | 147850 | NIAG115E | 115 | 2 | LN | 192 | A - Conductor | A - Conductor | A - Conductor
135497 | ZRMN-133 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
N-1-0 Thermal Overloads (Normal Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
135327 | AM.S-54 | 115 | 135450 | GRDNVL1 | 115 | 1 | Not Available
135458 | NI.B-181 | 115 | 135460 | PACK(N)E | 115 | 1 | LN | 181-2 | A - Conductor | A - Conductor | A - Conductor
135454 | MLPN-129 | 115 | 135461 | PACK(S)W | 115 | 1 | Not Available
N-1-1 (Normal Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
147850 | NIAG115E | 115 | 147842 | NIAGAR2W | 230 | 1 | TR | BK T1 | F - Transformer | F - Transformer | F - Transformer
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
130795 | DEPEW115 | 115 | 130799 | ERIE 115 | 115 | 1 | LN | 921 | I - Relay | I - Relay | I - Relay
135461 | PACK(S)W | 115 | 147851 | NIAG115W | 115 | 1 | LN | 193 | A - Conductor | A - Conductor | A - Conductor
135461 | PACK(S)W | 115 | 147851 | NIAG115W | 115 | 2 | LN | 194 | A - Conductor | A - Conductor | A - Conductor
135461 | PACK (S)W | 115 | 147851 | NIAG115W | 115 | 3 | LN | 195 | A - Conductor | A - Conductor | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 2 | LN | 62 | A - Conductor | G - CT | A - Conductor
135303 | SAWYER77 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 1 | LN | 61 | A - Conductor | G - CT | A - Conductor
135455 | MLPN-130 | 115 | 135461 | PACK(S)W | 115 | 1 | Not Available
135497 | ZRMN-133 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135498 | ZRMN-130 | 115 | 1 | Not Available
135454 | MLPN-129 | 115 | 135461 | PACK(S)W | 115 | 1 | Not Available
N-1-0 Thermal Overloads (Emergency Transfer Criteria) - Ontario Allowed to Move Between 1000 MW and 0 MW
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
135327 | AM.S-54 | 115 | 135450 | GRDNVL1 | 115 | 1 | Not Available
135458 | NI.B-181 | 115 | 135460 | PACK(N)E | 115 | 1 | LN | 181-2 | A - Conductor | A - Conductor | A - Conductor
147850 | NIAG115E | 115 | 147842 | NIAGAR2W | 230 | 1 | TR | BK T1 | F - Transformer | F - Transformer | F - Transformer
N-1-1 (Emergency) - Ontario Allowed to Move Between 1000 MW and 0 MW
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
130795 | DEPEW115 | 115 | 130799 | ERIE 115 | 115 | 1 | LN | 921 | I - Relay | I - Relay | I - Relay
135461 | PACK(S)W | 115 | 147851 | NIAG115W | 115 | 1 | LN | 193 | A - Conductor | A - Conductor | A - Conductor
135461 | PACK(S)W | 115 | 147851 | NIAG115W | 115 | 2 | LN | 194 | A - Conductor | A - Conductor | A - Conductor
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
135461 | PACK (S)W | 115 | 147851 | NIAG115W | 115 | 3 | LN | 195 | A - Conductor | A - Conductor | A - Conductor
130815 | HINMN115 | 115 | 131611 | HARIS115 | 115 | 1 | LN | 908 | L - Bus Work | A - Conductor | G - CT
147850 | NIAG115E | 115 | 147842 | NIAGAR2W | 230 | 1 | TR | BK T1 | F - Transformer | F - Transformer | F - Transformer
135451 | HUNTLEY1 | 115 | 135498 | ZRMN-130 | 115 | 1 | Not Available
135452 | LOCKPORT | 115 | 135876 | TELRDTP1 | 115 | 1 | LN | 114-1 | A - Conductor | A - Conductor | A - Conductor
135455 | MLPN-130 | 115 | 135461 | PACK(S)W | 115 | 1 | Not Available
135467 | SHAW-103 | 115 | 135470 | SWAN-103 | 115 | 1 | Not Available
135497 | ZRMN-133 | 115 | 135562 | S214-133 | 115 | 1 | Not Available

## Ratings_Beyond_Criteria
SERIES REACTORS ON 77 & 78 LINES IN-SERVICE
N-1 (NTC) - 1000 MW Ontario Import
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
147850 | NIAG115E | 115 | 147842 | NIAGAR2W | 230 | 1 | TR | BK T1 | F - Transformer | F - Transformer | F - Transformer
135458 | NI.B-181 | 115 | 135460 | PACK(N)E | 115 | 1 | LN | 181-1 | A - Conductor | A - Conductor | A - Conductor
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
135461 | PACK (S)W | 115 | 147851 | NIAG115W | 115 | 3 | LN | 195 | A - Conductor | A - Conductor | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 1 | LN | 61 | A - Conductor | G - CT | A - Conductor
135451 | HUNTLEY1 | 115 | 135498 | ZRMN-130 | 115 | 1 | Not Available
135460 | PACK(N)E | 115 | 135538 | LONG-182 | 115 | 1 | Not Available
130795 | DEPEW115 | 115 | 130799 | ERIE 115 | 115 | 1 | LN | 921 | I - Relay | I - Relay | I - Relay
135449 | GR.I-182 | 115 | 135459 | NI.B-182 | 115 | 1 | Not Available
135497 | ZRMN-133 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135442 | ECWA-181 | 115 | 135458 | NI.B-181 | 115 | 1 | Not Available
135442 | ECWA-181 | 115 | 135495 | YNG-181 | 115 | 1 | Not Available
135449 | GR.I-182 | 115 | 135538 | LONG-182 | 115 | 1 | Not Available
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 2 | LN | 62 | A - Conductor | G - CT | A - Conductor
135437 | CLSP-181 | 115 | 135495 | YNG-181 | 115 | 1 | Not Available
130847 | ROLL | 115 | 130857 | STOLE115 | 115 | 1 | Not Available
135443 | ECWA-182 | 115 | 135496 | YNG-182 | 115 | 1 | Not Available
135443 | ECWA-182 | 115 | 135459 | NI.B-182 | 115 | 1 | Not Available
130834 | N.BRW115 | 115 | 135437 | CLSP-181 | 115 | 1 | Not Available
135304 | SAWYER78 | 230 | 135414 | HUNTLEY2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135433 | AMHST-38 | 115 | 135472 | S129-38 | 115 | 1 | Not Available
135441 | FMC-39 | 115 | 135473 | S129-39 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135472 | S129-38 | 115 | 1 | LN | 39-1 | D - Disconnect | A - Conductor | A - Conductor
135452 | LOCKPORT | 115 | 135510 | SHAW-102 | 115 | 1 | Not Available
135455 | MLPN-130 | 115 | 135461 | PACK(S)W | 115 | 1 | Not Available
135460 | PACK(N)E | 115 | 147850 | NIAG115E | 115 | 2 | LN | 192 | A - Conductor | A - Conductor | A - Conductor
130815 | HINMN115 | 115 | 135452 | LOCKPORT | 115 | 1 | LN | 100 | A - Conductor | A - Conductor | A - Conductor
N-2 Normal - Locked Dispatch - 1000 MW Ontario Import
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
130754 | SOMERSET345 | 345 | 149690 | NEWROCH345 | 345 | 1 | Not Available
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
130766 | ROBIN230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 65 | A - Conductor | A - Conductor | I - Relay
130766 | ROBIN230 | 230 | 147841 | NIAGAR2E | 230 | 1 | LN | 64 | L - Bus Work | L - Bus Work | L - Bus Work
130775 | BIGTR115 | 115 | 131467 | LANGN115 | 115 | 1 | Not Available
130795 | DEPEW115 | 115 | 130799 | ERIE 115 | 115 | 1 | LN | 921 | I - Relay | I - Relay | I - Relay
130799 | ERIE 115 | 115 | 130834 | N.BRW115 | 115 | 1 | LN | 922 | G - CT | G - CT | G - CT
130806 | GARDV115 | 115 | 131467 | LANGN115 | 115 | 1 | Not Available
130815 | HINMN115 | 115 | 131611 | HARIS115 | 115 | 1 | LN | 908 | L - Bus Work | A - Conductor | G - CT
130815 | HINMN115 | 115 | 135452 | LOCKPORT | 115 | 1 | LN | 100 | A - Conductor | A - Conductor | A - Conductor
130834 | N.BRW115 | 115 | 135437 | CLSP-181 | 115 | 1 | Not Available
130846 | ROBIN115 | 115 | 130853 | A.LUD TP | 115 | 1 | Not Available
130853 | A.LUD TP | 115 | 131611 | HARIS115 | 115 | 1 | Not Available
135250 | DUNKIRK | 230 | 135251 | S RIPLEY | 230 | 1 | LN | 68 | J - TRAP | J - TRAP | G - CT
135253 | S224-36 | 115 | 135256 | S214-36 | 115 | 1 | Not Available
135254 | S224-37 | 115 | 135451 | HUNTLEY1 | 115 | 1 | Not Available
135253 | S224-36 | 115 | 135451 | HUNTLEY1 | 115 | 1 | Not Available
135268 | CLVB-141 | 115 | 135292 | SHALTNTP | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135268 | CLVB-141 | 115 | 135483 | S55-141 | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135269 | CLVB-142 | 115 | 135445 | FORD-142 | 115 | 1 | Not Available
135269 | CLVB-142 | 115 | 135569 | LAKEVIEW | 115 | 1 | LN | 142 | A - Conductor | A - Conductor | A - Conductor
135270 | DELMTR-1 | 115 | 135287 | NANG-141 | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135270 | DELMTR-1 | 115 | 135579 | LAKEV141 | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135271 | DLTR-142 | 115 | 135569 | LAKEVIEW | 115 | 1 | Not Available
135277 | FALCONER | 115 | 200579 | 26WARREN | 115 | 1 | LN | 171 | I - Relay | I - Relay | I - Relay
135284 | MCHS-151 | 115 | 135401 | GERNATT | 115 | 1 | Not Available
135292 | SHALTNTP | 115 | 135579 | LAKEV141 | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135303 | SAWYER77 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | A - Conductor
135304 | SAWYER78 | 230 | 135414 | HUNTLEY2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135305 | SAWYER80 | 230 | 135309 | SAWYERB3 | 230 | 1 | Not Available
135305 | SAWYER80 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 80 | A - Conductor | A - Conductor | A - Conductor
135305 | SAWYER80 | 230 | 135419 | SUNY-80 | 230 | 1 | LN | 80 | A - Conductor | A - Conductor | A - Conductor
135306 | SAWYER79 | 230 | 135308 | SAWYERB2 | 230 | 1 | Not Available
135306 | SAWYER79 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 79 | A - Conductor | A - Conductor | A - Conductor
135306 | SAWYER79 | 230 | 135418 | SUNY-79 | 230 | 1 | LN | 79 | A - Conductor | A - Conductor | B - Clearance
135327 | AM.S-54 | 115 | 135450 | GRDNVL1 | 115 | 1 | Not Available
135327 | AM.S-54 | 115 | 135493 | LUDWIG | 115 | 1 | Not Available
135383 | S219-182 | 115 | 135496 | YNG-182 | 115 | 1 | Not Available
135383 | S219-182 | 115 | 135505 | WALDENTP | 115 | 1 | Not Available
135401 | GERNATT | 115 | 147875 | ARCADE | 115 | 1 | Not Available
135413 | GRDNVL2 | 230 | 135418 | SUNY-79 | 230 | 1 | LN | 79-1 | A - Conductor | A - Conductor | B - Clearance
135413 | GRDNVL2 | 230 | 135419 | SUNY-80 | 230 | 1 | LN | 80-1 | A - Conductor | A - Conductor | B - Clearance
135415 | PACKARD2 | 230 | 135460 | PACK(N)E | 115 | 1 | TR | BK 3 | F - Transformer | F - Transformer | F - Transformer
135415 | PACKARD2 | 230 | 135461 | PACK(S)W | 115 | 2 | TR | BK 4 | F - Transformer | F - Transformer | F - Transformer
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 1 | LN | 61 | A - Conductor | G - CT | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 2 | LN | 62 | A - Conductor | G - CT | A - Conductor
135415 | PACKARD2 | 230 | 157062 | BECK_#2_BP76 | 230 | 1 | LN | BP76 | M - Voltage Regulator | A - Conductor | A - Conductor
135432 | AM.S-182 | 115 | 135450 | GRDNVL1 | 115 | 1 | LN | 182-3 | D - Disconnect | A - Conductor | A - Conductor
135432 | AM.S-182 | 115 | 135505 | WALDENTP | 115 | 1 | Not Available
135433 | AMHST-38 | 115 | 135472 | S129-38 | 115 | 1 | Not Available
135433 | AMHST-38 | 115 | 135477 | S140-38 | 115 | 1 | Not Available
135434 | AMHST-39 | 115 | 135473 | S129-39 | 115 | 1 | Not Available
135434 | AMHST-39 | 115 | 135478 | S140-39 | 115 | 1 | Not Available
135435 | SUMIT PK | 115 | 135454 | MLPN-129 | 115 | 1 | Not Available
135435 | SUMIT PK | 115 | 135552 | OXBOWNUG | 115 | 1 | Not Available
135437 | CLSP-181 | 115 | 135495 | YNG-181 | 115 | 1 | Not Available
135438 | CLSP-54 | 115 | 135439 | TUNGSTEN | 115 | 1 | Not Available
135441 | FMC-39 | 115 | 135451 | HUNTLEY1 | 115 | 1 | Not Available
135441 | FMC-39 | 115 | 135473 | S129-39 | 115 | 1 | Not Available
135442 | ECWA-181 | 115 | 135458 | NI.B-181 | 115 | 1 | Not Available
135442 | ECWA-181 | 115 | 135495 | YNG-181 | 115 | 1 | Not Available
135443 | ECWA-182 | 115 | 135459 | NI.B-182 | 115 | 1 | Not Available
135443 | ECWA-182 | 115 | 135496 | YNG-182 | 115 | 1 | Not Available
135445 | FORD-142 | 115 | 135484 | S55-142 | 115 | 1 | Not Available
135449 | GR.I-182 | 115 | 135459 | NI.B-182 | 115 | 1 | Not Available
135449 | GR.I-182 | 115 | 135538 | LONG-182 | 115 | 1 | Not Available
135450 | GRDNVL1 | 115 | 135453 | LONG-180 | 115 | 1 | Not Available
135450 | GRDNVL1 | 115 | 135475 | S139-141 | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135450 | GRDNV1 | 115 | 135503 | DALE-38 | 115 | 1 | Not Available
135450 | GRDNV1 | 115 | 135504 | DALE-39 | 115 | 1 | Not Available
135451 | HUNTLEY1 | 115 | 135472 | S129-38 | 115 | 1 | LN | 39-1 | D - Disconnect | A - Conductor | A - Conductor
135451 | HUNTLEY1 | 115 | 135498 | ZRMN-130 | 115 | 1 | LN | 130-1 | A - Conductor | L - Bus Work | A - Conductor
135451 | HUNTLEY1 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135452 | LOCKPORT | 115 | 135464 | SANBORNT | 115 | 1 | LN | 102-1 | L - Bus Work | L - Bus Work | G - CT
135452 | LOCKPORT | 115 | 135467 | SHAW-103 | 115 | 1 | Not Available
135452 | LOCKPORT | 115 | 135510 | SHAW-102 | 115 | 1 | Not Available
135452 | LOCKPORT | 115 | 135851 | SHEL-113 | 115 | 1 | Not Available
135452 | LOCKPORT | 115 | 135865 | NAKR-108 | 115 | 1 | LN | 108-2 | A - Conductor | A - Conductor | A - Conductor
135452 | LOCKPORT | 115 | 135867 | OAKFLDTP | 115 | 1 | Not Available
135452 | LOCKPORT | 115 | 135872 | SOUR-111 | 115 | 1 | LN | 111 | G - CT | G - CT | G - CT
135452 | LOCKPORT | 115 | 135875 | TELRDTP1 | 115 | 1 | LN | 107-1 | A - Conductor | A - Conductor | A - Conductor
135452 | LOCKPORT | 115 | 135876 | TELRDTP1 | 115 | 1 | LN | 114-1 | A - Conductor | A - Conductor | A - Conductor
135453 | LONG-180 | 115 | 147850 | NIAG115E | 115 | 1 | Not Available
135454 | MLPN-129 | 115 | 135461 | PACK(S)W | 115 | 1 | Not Available
135455 | MLPN-130 | 115 | 135461 | PACK(S)W | 115 | 1 | Not Available
135455 | MLPN-130 | 115 | 135469 | SUMIT PK | 115 | 1 | Not Available
135456 | MTNS-120 | 115 | 135470 | SWAN-103 | 115 | 1 | LN | 103-2 | L - Bus Work | L - Bus Work | A - Conductor
135456 | MTNS-120 | 115 | 147850 | NIAG115E | 115 | 1 | Not Available
135458 | NI.B-181 | 115 | 135460 | PACK(N)E | 115 | 1 | LN | 181-1 | A - Conductor | A - Conductor | A - Conductor
135460 | PACK(N)E | 115 | 135538 | LONG-182 | 115 | 1 | Not Available
135460 | PACK(N)E | 115 | 147850 | NIAG115E | 115 | 2 | LN | 192 | A - Conductor | A - Conductor | A - Conductor
135461 | PACK(S)W | 115 | 147851 | NIAG115W | 115 | 1 | LN | 193 | A - Conductor | A - Conductor | A - Conductor
135461 | PACK(S)W | 115 | 147851 | NIAG115W | 115 | 2 | LN | 194 | A - Conductor | A - Conductor | A - Conductor
135461 | PACK(S)W | 115 | 147851 | NIAG115W | 115 | 3 | LN | 195 | A - Conductor | A - Conductor | A - Conductor
135464 | SANBORNT | 115 | 147850 | NIAG115E | 115 | 1 | Not Available
135467 | SHAW-103 | 115 | 135470 | SWAN-103 | 115 | 1 | Not Available
135468 | SNBRN102 | 115 | 135510 | SHAW-102 | 115 | 1 | Not Available
135468 | SNBRN102 | 115 | 147850 | NIAG115E | 115 | 1 | LN | 102-2 | L - Bus Work | L - Bus Work | L - Bus Work
135469 | SUMIT PK | 115 | 135498 | ZRMN-130 | 115 | 1 | Not Available
135475 | S139-141 | 115 | 135483 | S55-141 | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135477 | S140-38 | 115 | 135481 | S54-38 | 115 | 1 | Not Available
135478 | S140-39 | 115 | 135482 | S54-39 | 115 | 1 | Not Available
135479 | S154-38 | 115 | 135485 | S61-38 | 115 | 1 | Not Available
135479 | S154-38 | 115 | 135492 | WALDENTP | 115 | 1 | Not Available
135480 | S154-39 | 115 | 135486 | S61-39 | 115 | 1 | Not Available
135480 | S154-39 | 115 | 135504 | DALE-39 | 115 | 1 | Not Available
135482 | S54-39 | 115 | 135486 | S61-39 | 115 | 1 | Not Available
135492 | WALDENTP | 115 | 135503 | DALE-38 | 115 | 1 | Not Available
135497 | ZRMN-133 | 115 | 135552 | OXBOWNUG | 115 | 1 | Not Available
135497 | ZRMN-133 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
147841 | NIAGAR2E | 230 | 147834 | NIAG 345 | 345 | 1 | TR | BK 3 | F - Transformer | F - Transformer | F - Transformer
147841 | NIAGAR2E | 230 | 147834 | NIAG 345 | 345 | 2 | TR | BK 5 | F - Transformer | F - Transformer | F - Transformer
147850 | NIAG115E | 115 | 147842 | NIAGAR2W | 230 | 1 | TR | BK T1 | F - Transformer | F - Transformer | F - Transformer
N-2 Emergency - Locked Dispatch - 1000 MW Ontario Import
From |  |  | To |  |  | CKT | EQ | ID | S_NOR | S_LTE | S_STE
130762 | GARDV230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 66 | A - Conductor | I - Relay | I - Relay
130766 | ROBIN230 | 230 | 130767 | STOLE230 | 230 | 1 | LN | 65 | A - Conductor | A - Conductor | I - Relay
130766 | ROBIN230 | 230 | 147841 | NIAGAR2E | 230 | 1 | LN | 64 | L - Bus Work | L - Bus Work | L - Bus Work
130775 | BIGTR115 | 115 | 131467 | LANGN115 | 115 | 1 | Not Available
130795 | DEPEW115 | 115 | 130799 | ERIE 115 | 115 | 1 | LN | 921 | I - Relay | I - Relay | I - Relay
130799 | ERIE 115 | 115 | 130834 | N.BRW115 | 115 | 1 | LN | 922 | G - CT | G - CT | G - CT
130806 | GARDV115 | 115 | 131467 | LANGN115 | 115 | 1 | Not Available
130815 | HINMN115 | 115 | 131611 | HARIS115 | 115 | 1 | LN | 908 | L - Bus Work | A - Conductor | G - CT
130815 | HINMN115 | 115 | 135452 | LOCKPORT | 115 | 1 | LN | 100 | A - Conductor | A - Conductor | A - Conductor
130834 | N.BRW115 | 115 | 135437 | CLSP-181 | 115 | 1 | Not Available
130846 | ROBIN115 | 115 | 130853 | A.LUD TP | 115 | 1 | Not Available
130853 | A.LUD TP | 115 | 131611 | HARIS115 | 115 | 1 | Not Available
135250 | DUNKIRK | 230 | 135251 | S RIPLEY | 230 | 1 | LN | 68 | J - TRAP | J - TRAP | G - CT
135254 | S224-37 | 115 | 135451 | HUNTLEY1 | 115 | 1 | Not Available
135256 | S214-36 | 115 | 135451 | HUNTLEY1 | 115 | 1 | Not Available
135268 | CLVB-141 | 115 | 135292 | SHALTNTP | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135268 | CLVB-141 | 115 | 135483 | S55-141 | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135269 | CLVB-142 | 115 | 135445 | FORD-142 | 115 | 1 | Not Available
135269 | CLVB-142 | 115 | 135569 | LAKEVIEW | 115 | 1 | LN | 142 | A - Conductor | A - Conductor | A - Conductor
135271 | DLTR-142 | 115 | 135569 | LAKEVIEW | 115 | 1 | Not Available
135303 | SAWYER77 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 77 | A - Conductor | A - Conductor | A - Conductor
135304 | SAWYER78 | 230 | 135414 | HUNTLEY2 | 230 | 2 | LN | 78 | A - Conductor | A - Conductor | A - Conductor
135305 | SAWYER80 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 80 | A - Conductor | A - Conductor | A - Conductor
135305 | SAWYER80 | 230 | 135419 | SUNY-80 | 230 | 1 | LN | 80 | A - Conductor | A - Conductor | A - Conductor
135306 | SAWYER79 | 230 | 135414 | HUNTLEY2 | 230 | 1 | LN | 79 | A - Conductor | A - Conductor | A - Conductor
135306 | SAWYER79 | 230 | 135418 | SUNY-79 | 230 | 1 | LN | 79 | A - Conductor | A - Conductor | B - Clearance
135327 | AM.S-54 | 115 | 135450 | GRDNVL1 | 115 | 1 | Not Available
135327 | AM.S-54 | 115 | 135493 | LUDWIG | 115 | 1 | Not Available
135413 | GRDNVL2 | 230 | 135418 | SUNY-79 | 230 | 1 | LN | 79-1 | A - Conductor | A - Conductor | B - Clearance
135413 | GRDNVL2 | 230 | 135419 | SUNY-80 | 230 | 1 | LN | 80-1 | A - Conductor | A - Conductor | B - Clearance
135415 | PACKARD2 | 230 | 135460 | PACK(N)E | 115 | 1 | TR | BK 3 | F - Transformer | F - Transformer | F - Transformer
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 1 | LN | 61 | A - Conductor | G - CT | A - Conductor
135415 | PACKARD2 | 230 | 147842 | NIAGAR2W | 230 | 2 | LN | 62 | A - Conductor | G - CT | A - Conductor
135415 | PACKARD2 | 230 | 157062 | BECK_#2_BP76 | 230 | 1 | LN | BP76 | M - Voltage Regulator | A - Conductor | A - Conductor
135435 | SUMIT PK | 115 | 135454 | MLPN-129 | 115 | 1 | Not Available
135435 | SUMIT PK | 115 | 135552 | OXBOWNUG | 115 | 1 | Not Available
135437 | CLSP-181 | 115 | 135495 | YNG-181 | 115 | 1 | Not Available
135438 | CLSP-54 | 115 | 135439 | TUNGSTEN | 115 | 1 | Not Available
135442 | ECWA-181 | 115 | 135458 | NI.B-181 | 115 | 1 | Not Available
135442 | ECWA-181 | 115 | 135495 | YNG-181 | 115 | 1 | Not Available
135443 | ECWA-182 | 115 | 135459 | NI.B-182 | 115 | 1 | Not Available
135443 | ECWA-182 | 115 | 135496 | YNG-182 | 115 | 1 | Not Available
135445 | FORD-142 | 115 | 135484 | S55-142 | 115 | 1 | Not Available
135449 | GR.I-182 | 115 | 135459 | NI.B-182 | 115 | 1 | Not Available
135449 | GR.I-182 | 115 | 135538 | LONG-182 | 115 | 1 | Not Available
135450 | GRDNVL1 | 115 | 135453 | LONG-180 | 115 | 1 | Not Available
135450 | GRDNVL1 | 115 | 135475 | S139-141 | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135451 | HUNTLEY1 | 115 | 135498 | ZRMN-130 | 115 | 1 | LN | 130-1 | A - Conductor | L - Bus Work | A - Conductor
135451 | HUNTLEY1 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
135452 | LOCKPORT | 115 | 135464 | SANBORNT | 115 | 1 | LN | 102-1 | L - Bus Work | L - Bus Work | G - CT
135452 | LOCKPORT | 115 | 135467 | SHAW-103 | 115 | 1 | Not Available
135452 | LOCKPORT | 115 | 135510 | SHAW-102 | 115 | 1 | Not Available
135452 | LOCKPORT | 115 | 135851 | SHEL-113 | 115 | 1 | Not Available
135452 | LOCKPORT | 115 | 135865 | NAKR-108 | 115 | 1 | LN | 108-2 | A - Conductor | A - Conductor | A - Conductor
135452 | LOCKPORT | 115 | 135867 | OAKFLDTP | 115 | 1 | Not Available
135452 | LOCKPORT | 115 | 135872 | SOUR-111 | 115 | 1 | LN | 111 | G - CT | G - CT | G - CT
135452 | LOCKPORT | 115 | 135875 | TELRDTP1 | 115 | 1 | LN | 107-1 | A - Conductor | A - Conductor | A - Conductor
135452 | LOCKPORT | 115 | 135876 | TELRDTP1 | 115 | 1 | LN | 114-1 | A - Conductor | A - Conductor | A - Conductor
135454 | MLPN-129 | 115 | 135461 | PACK(S)W | 115 | 1 | Not Available
135455 | MLPN-130 | 115 | 135461 | PACK(S)W | 115 | 1 | Not Available
135455 | MLPN-130 | 115 | 135469 | SUMIT PK | 115 | 1 | Not Available
135456 | MTNS-120 | 115 | 135470 | SWAN-103 | 115 | 1 | LN | 103-2 | L - Bus Work | L - Bus Work | A - Conductor
135456 | MTNS-120 | 115 | 147850 | NIAG115E | 115 | 1 | Not Available
135458 | NI.B-181 | 115 | 135460 | PACK(N)E | 115 | 1 | LN | 181-1 | A - Conductor | A - Conductor | A - Conductor
135460 | PACK(N)E | 115 | 135538 | LONG-182 | 115 | 1 | Not Available
135461 | PACK(S)W | 115 | 147851 | NIAG115W | 115 | 1 | LN | 193 | A - Conductor | A - Conductor | A - Conductor
135461 | PACK(S)W | 115 | 147851 | NIAG115W | 115 | 2 | LN | 194 | A - Conductor | A - Conductor | A - Conductor
135461 | PACK (S)W | 115 | 147851 | NIAG115W | 115 | 3 | LN | 195 | A - Conductor | A - Conductor | A - Conductor
135464 | SANBORNT | 115 | 147850 | NIAG115E | 115 | 1 | Not Available
135467 | SHAW-103 | 115 | 135470 | SWAN-103 | 115 | 1 | Not Available
135468 | SNBRN102 | 115 | 135510 | SHAW-102 | 115 | 1 | Not Available
135468 | SNBRN102 | 115 | 147850 | NIAG115E | 115 | 1 | LN | 102-2 | L - Bus Work | L - Bus Work | L - Bus Work
135469 | SUMIT PK | 115 | 135498 | ZRMN-130 | 115 | 1 | Not Available
135475 | S139-141 | 115 | 135483 | S55-141 | 115 | 1 | LN | 141 | A - Conductor | A - Conductor | A - Conductor
135497 | ZRMN-133 | 115 | 135552 | OXBOWNUG | 115 | 1 | Not Available
135497 | ZRMN-133 | 115 | 135562 | S214-133 | 115 | 1 | Not Available
147850 | NIAG115E | 115 | 147842 | NIAGAR2W | 230 | 1 | TR | BK T1 | F - Transformer | F - Transformer | F - Transformer