## New Instructions
Version 1.4 of Attachment D
Last Updated on June 14, 2007
Attachment D: Draft
Dependable Maximum Net Capability Audit Forms, the Procedure to Adjust a Resource’s Proven Maximum Production Capability and the Procedure to Weather Adjust DMNC Test Data
The following forms are included in this attachment:
· Steam Generation
· Hydro Generation
· Internal Combustion and Combustion Turbine Generation
· Combined Cycle Generation
· Other
Procedure to Adjust a Resource’s Proven Maximum Production Capability
A Resource’s Proven Maximum Production Capability (PMPC) may be adjusted at any time. Five (5) business days are required to process the PMPC request and to be made available in the Market Information System.
· Provide the appropriate Dependable Maximum Net Capability Audit Form for the type of Resource being reported.
· Check the PMPC box at top left of the Attachment D form and per instructions in the ICAP Automated Market System User's Guide - Section 11.
Procedure to Weather Adjust DMNC Test Data
All DMNC tests on internal combustion, combustion units and combined cycles units must be temperature adjusted. The Average Ambient Temperature to be used for the temperature adjustment is the average of the ambient temperatures recorded at the time of the Transmission District's seasonal peak during the previous four like-Capability Periods (as posted at the link given here), as recorded at the nearest weather station or recorded on an auditable recording device at the generator site. Once the decision is made where the temperature is obtained that location may not change for future test data submittals. The dates and times of the TD peak in each Capability Period are posted on the ISO website at:
http://www.nyiso.com/public/products/icap/index.jsp
under “ICAP Information & Announcements.” The Test Temperature is defined as the temperature measured at the top of the hour at the start of the test period obtained from the location chosen (above) then averaged over the hour from top-of-the-hour to top-of-the-hour for each hour of the test.
· Determine the weather adjusted DMNC rating for the generator using the manufacturer’s provided temperature adjustment curves. Also, determine the weather adjusted DMNC rating using generator specific curves (if applicable) produced from historical experience. Provide both sets of ratings and temperature adjustment curves.
· The higher of the two values may be claimed. The NYISO may lower the value claimed for the weather-adjusted DMNC, if the provided temperature adjustment curves are significantly different.
Submittal of PMPC and DMNC Test Data
PMPC and DMNC test data must be submitted in accordance with Attachment A, and Sections 2.7 and 4.2 of this ICAP Manual, to the NYISO’s Auxiliary Market Operations Department both via this Attachment D form and online via the ICAP Automated Market System. Attachment D submitted via e-mail is preferred. However, delivery by regular mail, courier service or fax is also acceptable. Submittals should be addressed as follows:
Email: generator_test_data@nyiso.com
Manager, Auxiliary Market Operations
c/o New York Independent System Operator
3890 Carman Rd
Schenectady, NY 12303
FAX: (518) 356-6208
Draft - For discussion only

## Fossil or Nuclear Steam
Version 1.4 of Attachment D
Last Updated on June 14, 2007
NEW YORK ISO
DEPENDABLE MAXIMUM NET CAPABILITY (DMNC) TEST
And PROVEN MAXIMUM PRODUCTION CAPABILITY (PMPC) TEST
Fossil or Nuclear Steam Generation
Company: | [10 empty] | Check all that apply:
Average and Post-Test values are truncated at first tenth MW
DMNC/PMPC (MW)
Generator or Station Name |  | PTID Number | Date of Test | Demonstrated PMPC |  |  |  |  | Pre-Test DMNC/PMPC Rating* | Post-Test DMNC/PMPC Rating | Difference (Post-Pre) | Test |  |  | Remarks
|  |  |  | Hourly |  |  |  | Average
|  |  |  | 1 | 2 | 3 | 4 |  |  |  |  | A | B | C
| A. Over Pressure | [5 empty] | Name (if submitted electronically):
B. Top Feed Water Heater OS
| C. Exceptions to Procedure Explained in Remarks Section | [5 empty] | Signed (if submitted by fax/mail):
* From Last Like Capability Period
Title:
Date:

## Hydro
Version 1.4 of Attachment D
Last Updated on June 14, 2007
NEW YORK ISO
DEPENDABLE MAXIMUM NET CAPABILITY (DMNC) TEST
And PROVEN MAXIMUM PRODUCTION CAPABILITY (PMPC) TEST
Hydro Generation
Company: | [10 empty] | Check all that apply:
Average and Post-Test values are truncated at first tenth MW
DMNC/PMPC (MW)
Generator or Station Name |  | PTID Number | Date of Test | Demonstrated PMPC |  |  |  |  | Pre-Test DMNC/PMPC Rating* | Post-Test DMNC/PMPC Rating | Difference (Post-Pre) | Remarks
|  |  |  | Hourly |  |  |  | Average
|  |  |  | 1 | 2 | 3 | 4
| * From Last Like Capability Period | [5 empty] | Name (if submitted electronically):
Signed (if submitted by fax/mail):
Title:
Date:

## Internal Combustion & Turbine
Version 1.4 of Attachment D
Last Updated on June 14, 2007
NEW YORK ISO
DEPENDABLE MAXIMUM NET CAPABILITY (DMNC) TEST
And PROVEN MAXIMUM PRODUCTION CAPABILITY (PMPC) TEST
Internal Combustion and Combustion Turbine Generation
Company: | [9 empty] | Check all that apply:
Post-Test Rating is truncated to tenth of a MW; NO rounding.
Generator or Station Name |  | PTID Number | Date of Test | Capability at Test Temp. (MW) |  |  |  | Avg. Amb Temp. (/F) | DMNC at Average Ambient Temperature (MW) |  | Remarks
|  |  |  | Test Temp. (/F) | Demonstrated PMPC | Per Curve | Excess (+) Deficiency (-) |  | Pre-Test DMNC/PMPC Rating* | Post-Test DMNC/PMPC Rating
| * From Last Like Capability Period |  |  |  | Name (if submitted electronically):
Signed (if submitted by fax/mail):
Title:
Date:

## Combined Cycle
Version 1.4 of Attachment D
Last Updated on June 14, 2007
NEW YORK ISO
DEPENDABLE MAXIMUM NET CAPABILITY (DMNC) TEST
And PROVEN MAXIMUM PRODUCTION CAPABILITY (PMPC) TEST
Combined Cycle Generation
Company: | [12 empty] | Check all that apply:
Average and Post-Test values are truncated at first tenth MW
Generator or Station Name |  | PTID Number | Date of Test | Capability at Test Temperature (MW) | [7 empty] | Avg. Amb Temp. (/F) | DMNC at Average Ambient Temperature (MW) |  | Remarks
|  |  |  | Test Temp. (/F) | Demonstrated PMPC |  |  |  |  | Per Curve | Excess (+) Deficiency (-) |  | Pre-Test DMNC/PMPC Rating* | Post-Test DMNC/PMPC Rating
[5 empty] | Hourly |  |  |  | Aver.
[5 empty] | 1 | 2 | 3 | 4
| * From Last Like Capability Period | [6 empty] | Name (if submitted electronically):
Signed (if submitted by fax/mail):
Title:
Date:

## Other
Version 1.4 of Attachment D
Last Updated on June 14, 2007
NEW YORK ISO
DEPENDABLE MAXIMUM NET CAPABILITY (DMNC) TEST
And PROVEN MAXIMUM PRODUCTION CAPABILITY (PMPC) TEST
Other Generation or Production Data in Lieu of PMPC/DMNC Test Data
Company: | [10 empty] | Check all that apply:
Average and Post-Test values are truncated at first tenth MW
DMNC/PMPC (MW)
Generator or Station Name |  | PTID Number | Date of Test | Demonstrated PMPC |  |  |  |  | Pre-Test DMNC/PMPC Rating* | Post-Test DMNC/PMPC Rating | Difference (Post-Pre) | Test |  |  | Remarks
|  |  |  | Hourly |  |  |  | Average
|  |  |  | 1 | 2 | 3 | 4 |  |  |  |  | A | B | C
| A. Over Pressure | [5 empty] | Name (if submitted electronically):
B. Top Feed Water Heater OS
| C. Exceptions to Procedure Explained in Remarks Section | [5 empty] | Signed (if submitted by fax/mail):
* From Last Like Capability Period
Title:
Date: