## All
List of Project / Facility Changes Submitted to NYISO and Determined to Be Non-Material Under the NYISO Interconnection Procedures (Updated as of 2/3/2026)
Queue Pos. | Project/Facility Name | Owner/Developer | Description of Change(s) | Date NYISO Received Request/Notification | Date of TPAS Notification
807 | Hilltop Solar | SunEast Hilltop Solar LLC | Change inverter configuration from thirty (30) 800 kVA TMEIC inverters to five (5) 5 x 840 KVA string TMEIC inverters and one (1) 4 x 840 KVA string TMEIC inverter configuration. | 2024-07-15 | N/A
564 | Rock District Solar | Rock District Solar, LLC | Change Synchronization Date to 12-2026 Change Initial Backfeed Date to 01-2027 Change Commercial Operation Date to 02-2027 | 2024-07-03 | N/A
565 | Tayandenega Solar | Tayandenega Solar, LLC | COD Extension to 2/2027 | 2024-07-01 | N/A
827 | Arthur Kill Energy Storage 1 | GB Arthur Kill Storage LLC | Change in inverter to Sungrow ST5015UX-4h | 2024-06-14 | N/A
807 | Hilltop Solar | SunEast Hilltop Solar LLC | Change COD from 7-24 to 5-28 | 2024-06-03 | N/A
1227 | 18405 Scotch Ridge | Nexamp Solar | Modify the tie-line length to 169 feet. | 2024-05-22 | N/A
581 | Hills Solar | SunEast Hills Solar LLC | COD Extension to 10/2026 | 2024-05-01 | N/A
1591 | Cuba Solar Farm | Apalachin Solar LLC | Increase inverters by 1 to a total of 6 units x SMA America SC4400 UP-US 4.400MVA, curtailed to 3.333 MW at 0.95 power factor each. | 2024-04-15 | N/A
1575 | Barrington Solar | NJR Clean Energy Ventures III Corporation | Reduce ERIS to 18.4MW, | 2024-04-05 | N/A
863 | Highbanks Solar | Oriden Power | Reduce size of the project from 20 MW to 12.5 MW. | 2024-03-29 | N/A
1410 | Cayuga Solar LLC | Cayuga Solar LLC | Max injection reduced to 19.68MW, and nameplate reduced to 19.888MW and increased to 6.537MVAR | 2024-02-23 | N/A
590 | Scipio Solar | Scipio Solar NY LLC | Change inverter type to SunGrow SG3600UD | 2024-02-09 | N/A
1418 | New Hartford Solar Farm | New Hartford Solar LLC | Change inverter from SMA SC400 UP-US to SMA SC4400 UP-US | 2024-02-05 | N/A
545 | Sky High Solar | Sky High Solar, LLC | Change Initial Sync date from 6/23 to 5/25 Change In-service date from 6/23 to 6/25 Change COD from 6/23 to 6/25 | 2024-01-27 | N/A
591 | Highview Solar | SunEast Highview Solar LLC | COD extension from Dec 2024 to Dec 2026 | 2024-01-10 | N/A
1541 | Stonewall Add-on | Nexamp Solar | ERIS changed from 20.2983MW to 19.71MW and nameplate MW changed from 20.2983MW to 20.0MW | 2023-12-13 | N/A
1035 | NY8 Solar | Boralex | Make changes to the feeder cables and gen. tie line distances from 1.774 miles & 0.019 miles to 1.395 miles & 0.4734 miles respectively. The gen. tie line SUM & WIN ratings changed from 39/44/48 & 47/51/54 MVA to 31.6/31.6/31.6 & 31.6/31.6/31.6 MVA respectively. | 2023-12-08 | N/A
1166 | BR Benson Mines Solar | BR Project 1 LLC | POI location changed from 0.3 mile to 0.0125 miles from Star Lake Substation. Line length from the interconnection station (project recloser) to CTOAF transmission line updated to 1928 ft. | 2023-11-15 | N/A
572 | Greene County 1 | Hecate Energy Greene 1 LLC | Change in Initial Synchronization date from 9/21 to 3/25 Change in In-service date from 9/21 to 3/25 Change in COD from 11/21 to 5/25 | 2023-10-25 | N/A
573 | Greene County 2 | Hecate Energy Greene 2 LLC | Change in Initial Synchronization date from 9/21 to 3/25 Change in In-service date from 9/21 to 3/25 Change in COD from 11/21 to 5/25 | 2023-10-25 | N/A
590 | Scipio Solar | Scipio Solar NY LLC | The number of inverters changed from 8 to 7 with a corresponding change in the output power from 20 MW to 18 MW. | 2023-10-19 | N/A
1226 | 47763 Cayuta | Nexamp Solar | Change Qmax Qmin to +/- 7.9MVAr and reduce ERIS to 19.86MW | 2023-10-06 | N/A
545 | Sky High Solar | Sky High Solar, LLC | Change inverters to Sungrow SG4400UD & SG3150UD. | 2023-10-02 | N/A
827 | Arthur Kill Energy Storage 1 | GB Arthur Kill Storage LLC | Data updated to match derated values provided by the manufacturer. | 2023-08-04 | N/A
806 | Limestone Solar | SED NY Holdings LLC | Move POI from a line tap off the Vail Mills tap line to a new 4 ring bus POI station between Stoner to Rotterdam Line 12. | 2023-08-02 | N/A
1166 | BR Benson Mines Solar | BR Project 1 LLC | Reduction in nameplate from 20MW to 12.13MW and reduction in ERIS from 20MW to 12.1MW | 2023-06-21 | N/A
584 | Dog Corners Solar | SunEast Dog Corners Solar LLC | Inverter change from TEMIC 4200 to SunGrow SG3600UD, update feeder and gen. tie line impedance values, and change gen. tie from overhead to underground. | 2023-06-07 | N/A
591 | Highview Solar | SunEast Highview Solar LLC | Change inverters from TEMIC 4200 to SunGrow SG3600UD, updating feeder and gen. tie line impedance values. | 2023-06-07 | N/A
828 | Valley Solar | SunEast Valley Solar LLC | Change inverter model from TEMIC-4200/3360 to TEMIC-4200/5040/3360. | 2023-06-07 | N/A
1539 | Mulberry Energy Storage Project | GSI Development Corp. | Change existing 1-hour system to 4-hour system. Power rating changed to 20 MW / 80 MWhrs and auxiliary load updated accordingly. | 2023-06-05 | N/A
1395 | Raquette Lake Energy Storage / CAMP | Excelsior Reserve Energy | Addtion of 1 MW aux load, and reduction from 15 to 12 inverters | 2023-05-18 | N/A
1098 | Kingbird Solar | SED NY Holdings LLC | Update inverter and impedance parameters. | 2023-04-14 | N/A
913 | Manchester Solar | SED NY Holdings LLC | Change GSU and PSU modeling parameters as well as gen. tie and feeder lengths. | 2023-02-20 | N/A
1092 | Hampton Corners Solar | SED NY Holding LLC | Shifting the POI to 3.56 miles from RG&E 115kV station 128 and 0.01 miles from RG&E 115kV station 7325 | 2023-02-09 | N/A
1047 | Millers Grove Solar | SED NY Holdings LLC | Change to VCCS short circuit model | 2023-02-03 | N/A
1051 | Transit Solar | SED NY Holding LLC | Change to VCCS short circuit model | 2023-01-12 | N/A
570 | Albany County 1 | Hecate Energy Albany 1 LLC | Change inverter to CHINT, CPS SCH125KTL-DO-US-600 (160) & CHINT, CPS SCA60KTL-DO/US-480 (25) string inverters. | 2023-01-11 | N/A
598 | Albany County 2 | Hecate Energy Albany 2 LLC | Change inverter to CHINT, CPS SCH125KTL-DO-US-600 (160) & CHINT, CPS SCA60KTL-DO/US-480 (25) string inverters. | 2023-01-11 | N/A
565 | Tayandenega | Tayandenega Solar, LLC | Change inverter from Power Electronics FS3350M to Sungrow SG3425UD-MV | 2022-12-20 | N/A
935 | Augustus Solar | SED NY Holdings LLC | Change to VCCS short circuit model. Updates to the collector feeder cables and the gen-tie line impedances. The GSU impedance changed from 5.75% to 6.5%. The POI distance to Oriskany Falls changed from 0.014 miles to 0.3 miles. The POI distance to Brothertown changed from 1.62 miles to 1.33 miles. | 2022-12-12 | N/A
1039 | Morris Solar | SED NY Holdings LLC | Change to VCCS short circuit model | 2022-12-12 | N/A
1212 | Roosevelt Solar | EMEREN US, LLC | Change gen-tie line length from 150 ft. to 528 ft. and adjust feeder impedances | 2022-12-08 | N/A
932 | Hatchery Solar | Hatchery Solar LLC | Change inverters from 160 Chint CPS-SCH100-125KTL-DO-US-600 125 kw to 25 TMEIC Solar Ware -PVU-L0840GR 840 kw. Remove the MPT 34.5 kV – 13.2 kV and change the voltage of the individual unit GSU from 13.2 kV – 0.6 kV to 34.5 kV – 0.63 kV. Change size and number of transformers from ten (10) 2100 kVA transformers to five (5) 5000 kVA transformers. PSU removed and replaced with a 4.181 ohm reactor | 2022-11-22 | N/A
1047 | Millers Grove Solar | SED NY Holdings LLC | Change the POI distance to Watkins Station from 1.85 miles to 1.72 miles; change the POI distance to Porter Station from 9.73 miles to 9.87 miles. | 2022-10-27 | N/A
1119 | Fuller Storage | Granada Solar, LLC | Update short circuit impedances | 2022-10-27 | N/A
1000 | SunEast Flat Stone Solar | SED NY Holdings LLC | Change to VCCS short circuit model. Updates to the generator lead line impedance and length. | 2022-10-20 | N/A
1113 | CLIES 20 MW | Caithness LI Energy Storage, LLC | Change collector feeder length to 1400ft and add 5MVAr capacitor bank. | 2022-10-10 | N/A
1047 | Millers Grove Solar | SED NY Holdings LLC | Change project distance from the POI to the remote stations from 1.85 miles and 9.73 miles for Watkins and Porter to 1.72 miles and 9.87 miles respectively. | 2022-10-07 | N/A
1062 | Hounsfield | ACE DEVCO NC, LLC | Update to the PSU impedance and ratings. | 2022-09-30 | N/A
682 | Grissom Solar | Grissom Solar, LLC | Modifying project data to match the as-built information. | 2022-09-29 | N/A
730 | Darby Solar | Darby Solar, LLC | Modifying project data to match the as-built information. | 2022-09-29 | N/A
731 | Branscomb Solar | Branscomb Solar, LLC | Modifying project data to match the as-built information. | 2022-09-29 | N/A
748 | Regan Solar | Regan Solar, LLC | Modifying project data to match the as-built information. | 2022-09-29 | N/A
1018 | Stone Mill Solar | Naturgy Candela DevCo LLC | Change their POI location within the Churchtown 115kV substation from the breaker position on the Southeast corner to an adjacent breaker position to the North occupied by the Line #984. | 2022-08-23 | N/A
1061 | Teele Solar | ACE DEVCO NC, LLC | Add string optimizers to the solar panels to help maintain required DC voltage levels at the inverters input terminals. | 2022-08-09 | N/A
1000 | SunEast Flat Stone Solar | SED NY Holdings LLC | Change gen tie line length from 100 ft to 153 ft. GSU impedance updated from 5.75% to 6.5%. | 2022-08-04 | N/A
1047 | Millers Grove Solar | SED NY Holdings LLC | Change gen tie line length from 100 ft to 325 ft. | 2022-08-04 | N/A
1061 | Teele Solar | ACE DEVCO NC, LLC | Change inverters from 4300KVA 620V to 4365KVA 690V. Change PSU from 18/24/30 MVA, Z=7% to 15/20/25 MVA, Z=7.5%. | 2022-08-02 | N/A
575 | Little Pond Solar | Little Pond Solar, LLC | Change inverter type from Power Electronics FS3150M to FS3190MU. Addition of feeder cable to the project. | 2022-07-11 | N/A
885 | Grassy Knoll Solar | SunEast Grassy Knoll Solar LLC | Change generator lead line distance from 60 ft. to 285 ft. | 2022-07-05 | N/A
575 | Little Pond Solar | Little Pond Solar, LLC | Change number and type of invertes from 7 x SMA SC-2500EV to 9 x Power Electronics FS3150M; No change to MW output. | 2022-05-10 | N/A
577 | Greene County Energy | Greene County Energy Properties, LLC | POI change from tapping the line between Coxsackie and New Baltimore to connecting directly to the Coxsackie substation. | 2022-05-06 | N/A
1015 | Somers Solar, LLC | Somers Solar, LLC | Shift POI 1.27 miles south of the original location along the same line. | 2022-03-02 | N/A
855 | NY13 Solar | Bald Mountain Solar LLC | Change project size from 19.99MW to 20MW. | 2021-11-09 | N/A
863 | Highbanks Solar | Oriden Power | Construction of two 34.5 kV gen. lead lines from the project facility to the Highbanks Substation which will allow for 10 MW to be connected to the North 34.5 kV bus and 10 MW to be connected to the South 34.5 kV bus at the substation, eliminating the need for a non-local SUF. | 2021-10-21 | N/A
759 | KCE NY 6 | KCE NY 6, LLC | Change inverter from ten (10) SMA SC 2.475 MVA to five (5) 5 MVA Sungrow inverters. | 2021-07-09 | N/A
865 | Flat Hill Solar | Flat Hill Solar NY LLC. | Move POI by one pole to the west (approximately 200 ft) from it's orginal location. | 2021-05-05 | N/A
682 | Grissom Solar | Grissom Solar, LLC | Minor impedance update to the inverters. | 2021-04-16 | N/A
730 | Darby Solar | Darby Solar, LLC | Minor impedance update to the inverters. | 2021-04-16 | N/A
731 | Branscomb Solar | Branscomb Solar, LLC | Minor impedance update to the inverters. | 2021-04-16 | N/A
748 | Regan Solar | Regan Solar, LLC | Minor impedance update to the inverters. | 2021-04-16 | N/A
694 | Sunset Hill Solar | Sunset Hill Solar, LLC | Change POI from New Baltimore – Westerlo 69kV, 7.8 miles from New Baltimore and 6.6 miles from Westerlo to New Baltimore – Westerlo 69kV, 5.4 miles from New Baltimore and 8.6 miles from Westerlo. | 2021-03-26 | N/A
769 | North Country Energy Storage | New York Power Authority | Change PSU from 34.5kV/ 115kV to 13.8kV/ 115kV. Change GSU from 0.69kV/34.5kV to 0.434kV/ 13.8kV. Change inverters from ten (10) 2.2 MVA inverters to ten (10) 2.475 MVA inverters.Change site location from within the NYPA Willis Substation to adjacent to the Willis Substation to the south. | 2021-03-26 | N/A
682 | Grissom Solar | Grissom Solar, LLC | Change inverter from five (5) SMA SC 4.6 MVA to seven (7) Power Electronics FS3350M 3.5 MVA inverters. | 2021-02-03 | N/A
730 | Darby Solar | Darby Solar, LLC | Change inverter from eight (8) SUNGROW SG 3.15 MVA inverters to seven (7) Power Electronics FS3350M 3.46 MVA inverters. | 2021-01-25 | N/A
731 | Branscomb Solar | Branscomb Solar, LLC | Change inverter from eight (8) SUNGROW SG 3.15 MVA inverters to seven (7) Power Electronics FS3350M 3.46 MVA inverters. | 2021-01-25 | N/A
748 | Regan Solar | Regan Solar, LLC | Change inverter from five (5) SMA SC 4.6 MVA to seven (7) Power Electronics FS3350M 3.46 MVA inverters. | 2021-01-25 | N/A
735 | ELP Stillwater Solar | ELP Stillwater Solar LLC | Change the inverter configuration, from two (2) inverters rated at 840kVA each, four (4) inverters rated at 1680kVA each, one (1) inverter rated at 5040kVA, two (2) inverters rated at 3360kVA each and one (1) inverter rated at 4200kVA to one (1) inverters rated at 1680kVA, four (4) inverters rated at 3360kVA each, two (2) inverters rated at 2520kVA each and one (1) inverter rated at 4200kVA. | 2021-01-12 | N/A
597 | Greene County 3 | Hecate Energy Greene County 3 LLC | Inverter change from TMEIC to CHINT. | 2021-01-11 | N/A
513 | Orangeville | Orangeville Energy Storage LLC | Change inverter to 10x SMA SCS 2475 from 18x GE Brilliance 1.25MVA inverters. | 2020-12-14 | N/A
598 | Albany County 2 | Hecate Energy Albany 2 LLC | Inverter change from TMEIC to CHINT. | 2020-12-14 | N/A
572 | Greene County 1 | Hecate Energy Greene 1 LLC | Inverter change from TMEIC to CHINT. | 2020-11-28 | N/A
573 | Greene County 2 | Hecate Energy Greene 2 LLC | Inverter change from TMEIC to CHINT. | 2020-11-28 | N/A
570 | Albany County 1 | Hecate Energy Albany 1 LLC | Inverter change from TMEIC to CHINT. | 2020-11-25 | N/A
638 | Pattersonville | Pattersonville Solar Facility, LLC | Change inverter model from eight (8) TMEIC (PVH-L2700GR) 2700kVA to twenty-nine (29) TMEIC (PVU-L0840GR) 840kW. | 2020-09-18 | N/A
735 | ELP Stillwater Solar | ELP Stillwater Solar LLC | Change inverter from five (5) SMA SC 4.6 MVA to 1, 2, 4, 5 or 6 UPCS TMEIC units placed in parallel consisting of two (2) inverters rated at 840kVA each, four (4) inverters rated at 1680kVA each, one (1) inverter rated at 5040kVA, two (2) inverters rated at 3360kVA each and one (1) inverter rated at 4200kVA. | 2020-09-16 | N/A
780 | Johnstown Solar | Hecate Energy Johnstown LLC | Move POI from 0.5 to a 1 mile closer to the Rotterdam station. | 2020-07-27 | N/A
730 | Darby Solar | Darby Solar, LLC | Change inverter from five (5) SMA SC 4.6 MVA to a eight (8) SUNGROW SG 3.15 MVA inverters. | 2020-04-20 | N/A
731 | Branscomb Solar | Branscomb Solar, LLC | Change inverter from five (5) SMA SC 4.6 MVA to a eight (8) SUNGROW SG 3.15 MVA inverters. | 2020-04-20 | N/A
744 | Magruder Solar | Mitchell Energy Facility, LLC | Change the substation location. | 2020-04-17 | N/A
775 | Puckett Solar | Puckett Solar, LLC | Change PV inverter manufacturer and model to SG3150U Sungrow | 2020-04-14 | N/A
768 | Janis Solar | Janis Solar, LLC | Change inverter type from five (5) SMA SC 4600KVA to seven (7) SUNGROW SG3150U 3150KVA inverters. | 2020-03-30 | N/A
591 | Highview Solar | SunEast Highview Solar LLC | Change inverter from eight (8) Power Electronics FS2800CU15 to a three (3) 5 x 810 KVA string TMEIC inverters and three (3) 4 x 810 KVA string TMEIC inverters. | 2020-02-25 | N/A
669 | Clay Solar | SED NY Holdings LLC | Change inverter from nine (9) SMA SC 2750-EV to a five (5) 5 x 840 KVA string TMEIC inverters and one (1) 4 x 840 KVA string TMEIC inverters. | 2019-12-09 | N/A
670 | SunEast Skyline Solar LLC | SunEast Skyline Solar LLC | Change the inverter from nine (9) SMA SC 2750-EV to a four (4) 5 x 840 KVA string TMEIC inverters and three (3) 3 x 840 KVA string TMEIC inverters. | 2019-12-04 | N/A
584 | Dog Corners Solar | SunEast Dog Corners Solar LLC | Interconnection Customer name change from SED NY Holdings LLC (“SED NY”) to SunEast Dog Corners Solar LLC (“SE Dog Corners”). | 2019-11-21 | N/A
667 | Bakerstand Solar | Bakerstand Solar LLC | Add a series reactor bank to the feeder side of the projects circuit breaker. | 2019-10-04 | N/A
584 | Dog Corners Solar | SunEast Dog Corners Solar LLC | Change inverter from nine (9) SMA SC 2750-EV to a three (3) 5 x 840 KVA string TMEIC inverters and three (3) 4 x 840 KVA string TMEIC inverters. | 2019-10-01 | N/A
742 | Astoria Storage on Demand | Consolidated Edison Co. of NY, Inc. | Change the current POI location to another location fed by the same area substation but different feeders. | 2019-08-07 | N/A
584 | Dog Corners Solar | SunEast Dog Corners Solar LLC | Change inverter from 8 x SC 2500-EV inverters with a rated power of 2.5 MW to 9 x SC 2700-EV inverters with a rated power of 2.22 MW. | 2018-11-15 | N/A
701 | KCE NY 1 | KCE NY 1, LLC | Change number and type of inverters from 16 x S&C with a total MVA rating of 20MVA to 9 x SMA with a total MVA rating of 22.275MVA. | 2018-08-29 | N/A
512 | Lyons Falls Mill Hydro | Northbrook Lyons Falls | The MW value decreased from 11.671MW to 11.204MW. | 2018-07-20 | N/A
477 | Riverhead Solar | Riverhead Solar Farm LLC | Change inverter model from Power Electronics FS2800CU15 to the FS3150MU. | 2018-05-18 | N/A
251 | CPV Valley Energy Center | CPV Valley, LLC | Confirmation of above change of in-service date. | 2011-12-06 | N/A
263 | Stony Creek Wind Farm | Stony Creek Wind Farm | Notice of size reduction from 142.5 MW to 88.5 MW. | 2010-04-29 | N/A
260 | Stephentown Flywheel | Beacon Power | Potential change in transformer size. | 2010-04-12 | N/A
201 | Berrians GT | NRG Energy | Notice of change of machine. | 2009-12-31 | N/A
224 | Berrians GT II | NRG Energy | Notice of size reduction to 50/90 MW summer/winter. | 2009-12-31 | N/A
166 | St. Lawrence Wind Farm | Acciona Windpower | Notice of size reduction to 79.5 MW. | 2009-08-06 | N/A
178 | Allegany Windpark | Noble Envir. Power | Notice of change in size. | 2008-09-19 | N/A
144 | High Sheldon Windfarm | Sheldon Energy | Notice of decision to implement changes. | 2008-06-16 | N/A
843 | NY37 Solar | Sandy Creek Solar LLC | Change Interconnection Customer name from “Sandy Creek Solar LLC” to “Green Corners Solar LLC”. | 2025-11-25 | 2026-02-03
C24-162 | Ramadi Utility Storage | Ramadi LLC | Change Interconnection Customer name from “Ramadi LLC” to “Calpine Mid-Atlantic Development, LLC”. | 2025-11-17 | 2026-02-03
631/887 | NS Power Express/CH Uprate | CHPE, LLC | 1. Change reactive capability of converter model at Astoria from +/- 500 MVAr to +/- 411 MVAr. 2. Update to steady-state project representation and dynamic model. | 2025-11-12 | 2026-02-03
704 | Bear Ridge Solar | Bear Ridge Solar, LLC | Change in milestone dates: • Synchronization Date: from 04-2027 to 04-2028 • Initial Backfeed Date: from 01-2027 to 12-2027 • Commercial Operation Date: from 04-2027 to 04-2028 | 2025-11-07 | 2026-02-03
571 | Heritage Wind | Heritage Wind, LLC | Change in milestone dates: • Synchronization Date: from 06-2026 to 08-2027 • Initial Backfeed Date: from 05-2026 to 05-2027 • Commercial Operation Date: from 09-2026 to 10-2027 | 2025-10-20 | 2026-02-03
865 | Flat Hill Solar | Suneast Flat Hill Solar LLC | 1. Change in milestone dates: • Synchronization Date: from 11-2025 to 05-2027 • Initial Backfeed Date: from 11-2025 to 06-2027 • Commercial Operation Date: from 12-2025 to 08-2027 2. Change inverter model from Sungrow SG3600UD to Sungrow SG4400UD-MV-US with no change to ERIS. | 2025-10-20 | 2026-02-03
C24-108 | NY125C - Little Salmon Solar | Boralex US Development, LLC | Change Interconnection Customer name from “Boralex US Development, LLC” to “Little Salmon Solar LLC”. | 2025-10-20 | 2026-02-03
522/1007 | NYC Energy/NYC Energy LLC - Phase 2 | NYC Energy LLC | 1. Change MVA rating of three PSUs from 96/120 MVA to 112/140 MVA. 2. Change ULTC range of three PSUs. | 2025-10-14 | 2026-02-03
C24-352 | Swiss Valley Energy Storage | Cedar Holdco LLC | Change Interconnection Customer name from “Cedar Holdco LLC” to “Sawhall Energy Storage LLC”. | 2025-10-06 | 2026-02-03
C24-358 | Sugar Loaf Energy Storage I | Cedar Holdco LLC | Change Interconnection Customer name from “Cedar Holdco LLC” to “Hambletonian Energy Storage LLC”. | 2025-10-06 | 2026-02-03
C24-359 | Sugar Loaf Energy Storage II | Cedar Holdco LLC | Change Interconnection Customer name from “Cedar Holdco LLC” to “Hambletonian Energy Storage II LLC”. | 2025-10-06 | 2026-02-03
1184 | NY125B - Two Rivers Solar | Boralex US Development, LLC | Change Interconnection Customer name from “Boralex US Development” to “Two Rivers Solar Farm, LLC”. | 2025-09-25 | 2026-02-03
276 | Homer Solar Energy Center | Homer Solar Energy Center LLC | 1. Change model and number of inverters from (32) x Freesun 3500kVA to (24) x SMA 4400kVA. 2. Shift POI 0.2 miles along the 115kV Cortland – Fenner Line #3. 3. Change PSU size from 60/80/100 MVA to 72/96/120 MVA. | 2025-07-22 | 2026-02-03
584 | Dog Corners Solar | Dog Corners Solar LLC | 1. Change in milestone dates: • Synchronization Date: from 03-2026 to 09-2026 • Initial Backfeed Date: from 03-2026 to 08-2026 • Commercial Operation Date: from 04-2026 to 01-2027 2. Change Interconnection Customer name from “SunEast Dog Corners Solar LLC” to “Dog Corners Solar NY LLC”. | 2025-07-22 | 2026-02-03
885 | Grassy Knoll Solar | SunEast Grassy Knoll Solar LLC | Change Interconnection Customer name from “SunEast Grassy Knoll Solar LLC” to “Grassy Knoll Solar NY LLC”. | 2025-07-17 | 2026-02-03
848 | Fairway Solar | SunEast Fairway Solar LLC | Change Interconnection Customer name from “SunEast Fairway Solar LLC” to “Fairway Solar NY LLC”. | 2025-07-15 | 2026-02-03
1000 | SunEast Flat Stone Solar LLC | SED NY Holdings LLC | 1. Change Interconnection Customer name from “SED NY Holdings LLC” to “Flat Stone Solar NY LLC”. 2. Change Project name from “SunEast Flat Stone Solar LLC” to “Flat Stone Solar”. | 2025-02-03 | 2026-02-03
737 | Empire Wind 1 | Empire Offshore Wind LLC | Change in milestone dates including: Synchronization Date: from 08-2026 to 09-2026 Commercial Operation Date: from 12-2026 to 07-2027 | 2025-09-12 | 2025-10-07
586 | Watkins Rd Solar | SunEast Watkins Road Solar LLC | Change in Interconnection Customer Name from “SunEast Watkins Road Solar LLC” to “Watkins Road Solar NY LLC” | 2025-07-28 | 2025-10-07
C24-058 | Slide Energy Center | Mission Clean Energy Devco LLC | Change in Interconnection Customer Name from "Mission Clean Energy Devco, LLC" to "Slide Energy Center, LLC" | 2025-06-30 | 2025-10-07
C24-266 | Summersweet Energy Center | Mission Clean Energy Devco LLC | Change in Interconnection Customer Name from "Mission Clean Energy Devco, LLC" to "Summersweet Energy Center, LLC" | 2025-06-30 | 2025-10-07
586 | Watkins Rd Solar | SunEast Watkins Road Solar LLC | Change in Milestone dates including: In service from 03-2026 to 12-2026 Initial Synchronization from 02-2026 to 11-2026 Commercial Operation from 07-2026 to 02-2027 | 2025-07-28 | 2025-09-04
828 | Valley Solar | SunEast Valley Solar LLC | Change in Interconnection Customer name from "SunEast Valley Solar LLC" to "Valley Solar NY LLC" | 2025-07-23 | 2025-09-04
885 | Grassy Knoll Solar | SunEast Grassy Knoll Solar LLC | Change in Milestone dates including: In service from 11-2025 to 01-2028 Initial Synchronization to 11-2025 to 02-2028 Commercial Operation from 12-2025 to 05-2028 | 2025-07-17 | 2025-09-04
848 | Fairway Solar | SunEast Fairway Solar LLC | Change in Milestone dates including: In service from 02-2025 to 01-2028 Initial Synchronization to 02-2025 to 01-2028 Commercial Operation from 03-2025 to 05-2028 | 2025-07-15 | 2025-09-04
815 | Bayonne Energy Center III | Bayonne Energy Center III, LLC | Change in Milestone dates including: In service from 07-2026 to 01-2028 Initial Synchronization from 08-2026 to 02-2028 Commercial Operation from 09-2026 to 03-2028 | 2025-06-20 | 2025-09-04
1115 | Flat Creek Solar II | SED NY Holdings LLC | Change in Interconnection Customer Name from “SED NY Holding LLC” to “Flat Creek Solar NY LLC”, and change in Project Name from “Flat Creek Solar II” to “Flat Creek Solar” allowing for a consolidated IA with Q1089. | 2025-02-13 | 2025-09-04
1188 | North Seneca Solar Project, LLC | North Seneca Solar Project | Decrease output of facility from 105MW to 90MW. | 2024-12-23 | 2025-09-04
263 | Stony Creek Wind Farm | Stony Creek Energy LLC | Addition of 87 MW battery storage to Stony Creek Wind Farm without increasing the ERIS of the Project. | 2024-10-10 | 2025-09-04
519 | Canisteo Wind | Canisteo Wind Energy LLC | Addition of 100.5 MW battery storage to Canisteo Wind without increasing the ERIS of the Project. | 2024-10-09 | 2025-09-04
C24-152 | Antelope Energy Storage Center | Hydrostor USA Holdings, Inc , a subsidiary of Hydrostor Inc | Change in Interconnection Customer name from "Hydrostor USA Holdings, Inc , a subsidiary of Hydrostor Inc" to "Antelope Energy Storage LLC" | 2025-06-17 | 2025-08-04
591 | Highview Solar | SunEast Highview Solar LLC | Change in Milestone dates including: In service from 09/2024 to 11/2026 Initial Synchronization to 11/2024 to 11/2026 Commercial Operation from 12/2024 to 12/2026 | 2025-06-03 | 2025-08-04
1039 | Morris Solar | Morris Solar NY LLC | Change in Interconnection Customer name from "SED NY Holdings LLC" to "Morris Solar NY LLC" | 2025-03-05 | 2025-08-04
1123 | KCE NY 29 | KCE NY 29, LLC | Reduction in the project output from 150MW to 79MW at the POI. Change to inverter and BESS type from SunGrow to Tesla with related updates to the PSU, GSUs and collection system impedances | 2024-12-23 | 2025-08-04
C24-130 | Lighthouse Bethlehem | Lighthouse Bethlehem, LLC | Change Interconnection Customer name from "Elevate Bethlehem, LLC" to "Lighthouse Bethlehem, LLC" due to entity legal name change. Change Project name from "Elevate Bethlehem" to"Lighthouse Bethlehem" | 2025-06-17 | 2025-07-01
1289 | Propel NY Energy - Alternate Solution 5 | New York Power Authority / New York Transco LLC. | 1. Change from Air Insulated Switchgear (AIS) to Gas Insulated Switchgear (GIS), at the Uniondale (Former East Garden City) 345 kV Substation 2. Change in the size of the shunt reactor from 120 MVAR to 150 MVAR 3. Holbrook 138kV: Change from PASS to GCB breaker and associated PT/Control Enclosure changes. 4. Newbridge 138kV: Replacement of proposed 63kA PASS breakers with 80kA dead tank breakers. Associated control house and PT relocation. 5. Northport 138kV: Increased capability of the proposed second Northport PAR to +/- 25 degrees, rather than +/-15 degrees. Replacement of proposed 63kA breakers with 80kA breakers. Re-arrangement of station to accommodate these changes. 6. Ruland Road 138kV: Re-sizing of the Newbridge-Ruland road series reactors to 3.2 Ohms each. 7. Stewart Ave 138kV: Re-sizing of the Stewart Ave – Newbridge series reactors to 0.2 ohms each. Re-location of the Stewart Ave – Valley Stream series reactor to the valley stream station, and re-sizing to 3.2 Ohms. 8. Syosset-Greenlawn and Syosset – Oakwood: Change in proposed conductor for underground portion. 9. Removal of the proposed Barret 138kV PARs 10. Change in location of proposed Y55 shunt reactor at Ruland Road 345kV from the station side of the Y55 PAR to the line side of the PAR. 11. Change in size of the proposed Y58 shunt reactor at Shore Road from 106 to 150 MVAR. 12. Change from AIS to GIS at the proposed Ruland Road 345kV and 138kV substations 13. Change from AIS to GIS at the proposed Barret 345kV substation. 14. Cable length updates 15. Change in physical arrangement of the New Rochelle Transition Station | 2025-06-06 | 2025-07-01
1122 | East Fishkill | East Fishkill Storage 1, LLC | Change in Interconnection Customer name from "Microgrid Networks, LLC" to "East Fishkill Storage 1, LLC" | 2025-06-03 | 2025-07-01
1148 | Agricola Wind | Agricola Wind LLC | Change Interconnection Customer name from "Liberty Renewables, Inc." to "Agricola Wind LLC" | 2025-06-03 | 2025-07-01
C24-131 | Lighthouse Arthur Kill II | Lighthouse Arthur Kill II, LLC | Change Interconnection Customer name from "Elevate Arthur Kill II, LLC" to "Lighthouse Arthur Kill II, LLC" due to entity legal name change. Change Project name from "Elevate Arthur Kill II" to"Lighthouse Arthur Kill II" | 2025-05-15 | 2025-07-01
737 | Empire Wind 1 | Empire Offshore Wind LLC | 1. Resize of onshore harmonic filters (x2): 40MVAR to 20 MVAR 2. Resize of onshore shunt capacitors (x2): 85MVAR to 90MVAR 3. Change 70MVAR onshore fixed shunt reactors (x2) to 135MVAR variable shunt reactors (x2) 4. Change onshore 230kV bus tie breaker to normally closed 5. Minor modelling updates to main transformers, auxiliary transformers, interconnection/export cables, and wind turbine/power plant controller model | 2024-08-26 | 2025-07-01
571 | Heritage Wind | Heritage Wind, LLC | Change to 28 Vestas V150-4.5MW WTG | 2024-06-20 | 2025-07-01
828 | Valley Solar | SunEast Valley Solar LLC | COD extension from Nov 2024 to Jan 7 2027 | 2024-06-03 | 2025-07-01
827 | Arthur Kill Energy Storage 1 | Lighthouse Arthur Kill, LLC | Change Interconnection Customer name from "GB Arthur Kill Storage LLC" to "Lighthouse Arthur Kill, LLC" | 2025-05-21 | 2025-06-05
572 | Greene County 1 | Hecate Energy Greene 1 LLC | Updated In-Service Date: May 2027; Initial Synch Date: April 2027; COD: June 2027. | 2025-05-20 | 2025-06-05
573 | Greene County 2 | Hecate Energy Greene 2 LLC | Updated In-Service Date: May 2027; Initial Synch Date: April 2027; COD: June 2027. | 2025-05-20 | 2025-06-05
971 | East Setauket Energy Storage | Savion, LLC | Change in LLC name from "Savion, LLC" to "East Setauket Energy Storage, LLC" | 2025-05-19 | 2025-06-05
1130 | Hoffman Falls Wind | Liberty Renewables Inc. | Change in Interconnection Customer name from “Liberty Renewables, Inc.” to “Hoffman Falls Wind LLC”. | 2025-05-16 | 2025-06-05
N/A | Mortimer – Golah | National Grid | Rebuild the entirety of the Mortimer – Golah #110 115kV circuit, rebuild the Mortimer – Golah #109 69kV circuit and convert the #109 circuit to 115kV operation | 2025-05-07 | 2025-06-05
N/A | Manheim - Rotterdam | National Grid | Rebuild the Manheim – Rotterdam 115kV circuits | 2025-05-07 | 2025-06-05
591 | Bull Run II Wind | Bull Run Energy LLC | COD extension to 05/2028 | 2025-03-06 | 2025-06-05
710 | Horseshoe Solar | Horseshoe Solar Energy LLC | COD extension from 12/2025 to 05/2028. | 2025-02-26 | 2025-06-05
800 | Rich Road Solar Energy Center | EDF Renewables Development, Inc. | Interconnection Customer name change from "EDF Renewables Development, Inc." to "Rich Road Solar Energy Center, LLC" | 2025-02-25 | 2025-06-05
586 | Watkins Rd Solar | SunEast Watkins Road Solar LLC | Change in Initial Synchronization Date from 12/23 to 2/26 Change in In-Service Date from 2/24 to 3/26 Change in COD from 2/24 to 7/26 | 2025-02-23 | 2025-06-05
571 | Heritage Wind | Heritage Wind, LLC | Change POI parcel location by 0.1 miles (528 ft). | 2025-02-21 | 2025-06-05
744 | Magruder BESS | Mitchell Energy Facility, LLC | COD extension from 1/2025 to 4/2028 | 2025-02-19 | 2025-06-05
1089 | Flat Creek Solar | Flat Creek Solar NY LLC | Changing Interconnection Customer name from "SED NY Holdings LLC" to "Flat Creek Solar NY LLC" | 2025-02-03 | 2025-06-05
766 | Sunrise Wind | Sunrise Wind LLC | Modify Initial Synchronization Date to July 2026 and Commercial Operations Date to July 2027. | 2025-01-30 | 2025-06-05
801 | Prattsburgh Wind Farm | Prattsburgh Wind, LLC | COD extension from 12/31/2026 to 09/15/2027 | 2025-01-30 | 2025-06-05
987 | Sunrise Wind II | Sunrise Wind LLC | Modify Initial Synchronization Date to July 2026 and Commercial Operations Date to July 2027 | 2025-01-30 | 2025-06-05
930 | Luyster Creek Energy Storage 3 | Eastern Generation, LLC | Change Interconnection Customer name from "Astoria Generating Company, L.P". to "Eastern Generation, LLC", and Change Project Name from "Astoria BES to 27kV North Queens" to "Luyster Creek Energy Storage 3" | 2025-01-28 | 2025-06-05
575 | Little Pond Solar | Little Pond Solar, LLC | COD Extension to 9/2027 | 2025-01-24 | 2025-06-05
883 | Garnet Energy Center, LLC | Garnet Energy Center, LLC | Change In Service date from October 2025 to November 2027, Synchronization from October 2025 to November 2027 Commercial Operation from November 2025 to April 2028. | 2025-01-21 | 2025-06-05
706 | High Bridge Wind | High Bridge Wind, LLC | Change In-Service/Initial Backfeed Date & Sync Date from 12/2024 to 9/2026 & COD from 2/2025 to 11/2026. | 2024-11-26 | 2025-06-05
907 | Harlem River Yard | Harlem River ESS, LLC | COD extension from Jan 2027 to Jan 2028 | 2024-11-25 | 2025-06-05
617 | Watkins Glen Solar Energy Center | Watkins Glen Solar Energy Center, LLC | Change In Service date from December 2024 to March 2028, Synchronization date from December 2024 to April 2028, and Commercial Operation from January 2025 to April 2028. | 2024-11-19 | 2025-06-05
721 | Excelsior Energy Center | Excelsior Energy Center, LLC | COD extension until November 2026 | 2024-11-05 | 2025-06-05
620 | Gateway Solar Energy Center | Gateway Solar Energy Center, LLC | Change Project name from "North Side Solar" to "Gateway Solar Energy Center". Change Interconnection Customer from "North Side Energy Center, LLC" to "Gateway Solar Energy Center, LLC.", and Change In Service date from October 2024 to February 2028. Synchronization date from November 2024 to February 2028 and Commercial Operation from December 2024 to April 2028. | 2024-10-31 | 2025-06-05
590 | Scipio Solar | Scipio Solar NY LLC | COD extension from 12/2024 to 12/2026 | 2024-10-08 | 2025-06-05
704 | Bear Ridge Solar | Bear Ridge Solar, LLC | Extension of: Initial Backfeed Date - to 06/2026 Synchronization Date - to 09/2026 Commercial Operation Date - to 09/2026 | 2024-09-27 | 2025-06-05
670 | Skyline Solar | SunEast Skyline Solar LLC | COD extension from July 2023 to April 2028 | 2024-09-20 | 2025-06-05
832 | CS Hawthorn Solar | Hawthorn Solar, LLC | Change in COD to 12/2026 | 2024-09-04 | 2025-06-05
833 | Dolan Solar | Dolan Solar, LLC | Change in COD to 12/2026 | 2024-09-04 | 2025-06-05
535 | Riverhead Solar | Riverhead Solar 2, LLC | Change in Milestone dates including: In service to 10/2024 Initial Synchronization from 1/2025 Commercial Operation from 2/2025 | 2024-08-09 | 2025-06-05
787 | Levy Grid | Levy Grid, LLC | Change in the Point of Change of Ownership from what was evaluated in the Facility Study. In this new gen-tie routing, National Grid’s Facilities will be all overhead from the POCO, crossing one existing distribution line, and going into the same POI. | 2024-08-06 | 2025-06-05
834 | Luyster Creek Energy Storage 2 | Eastern Generation, LLC | Changing Interconnection Customer name from "Astoria Generating Company, L.P." to "Eastern Generation, LLC" | 2025-03-10 | 2025-05-06
835 | Luyster Creek Energy Storage 1 | Eastern Generation, LLC | Changing Interconnection Customer name from "Astoria Generating Company, L.P." to "Eastern Generation, LLC" | 2025-01-28 | 2025-05-06
1555 | Liberty Green Line | North Bergen Liberty Generating LLC | Revise interconnection request capacity from 600MW to 1200MW | 2025-01-13 | 2025-05-06
174 | Altona Wind | Emeren US, LLC | Repowering of turbines using Vestas V150-4.5 | 2024-03-08 | 2025-05-06
175 | Ellenburg Wind | Noble Environmental Power, LLC | Repowering of turbines using Vestas V150-4.5 | 2024-03-08 | 2025-05-06
177 | Wethersfield Wind | Noble Environmental Power, LLC | Repowering of turbines using Vestas V150-4.5 | 2024-03-08 | 2025-05-06
214 | Chateaugay Wind | Noble Environmental Power, LLC | Repowering of turbines using Vestas V150-4.5 | 2024-03-08 | 2025-05-06
172/211 | Clinton Wind | Noble Environmental Power, LLC | Repowering of turbines using Vestas V150-4.5 | 2024-03-08 | 2025-05-06
173/212 | Bliss Wind | Noble Environmental Power, LLC | Repowering of turbines using Vestas V150-4.5 | 2024-03-08 | 2025-05-06
931 | Astoria Energy Storage | East River ESS, LLC | Increasing Tesla Inverters from 1100KVA to 1300KVA and limiting ERIS to 100MW via plant controller | 2025-06-24 | 2025-03-27
N/A | Southeast Batavia-Golah Rebuild | National Grid | National Grid has a project to rebuild the existing ~15 mile long 115kV circuit between Golah and Lapp Insulator (bus 135859), which is a portion of the series 115kV path between Batavia, Southeast Batavia, and Golah. | 2025-02-22 | 2025-03-27
N/A | South Oswego- Lighthouse Hill Rebuild | National Grid | National Grid has a project to rebuild the South Oswego – Tar Hill 115kV circuits (note that Tar Hill is the name of the station replacing the existing Lighthouse Hill Station). This project includes rebuilding the majority of what today we call the South Oswego – Indeck Oswego #6, Indeck Oswego – Tar Hill (formally Lighthouse Hill) #2, South Oswego – Nine Mile Point #1 and Fitzpatrick – Tar Hill (formally Lighthouse Hill) #3. | 2025-02-21 | 2025-03-27
865 | Flat Hill Solar | Flat Hill Solar NY LLC | Interconnection Customer name change from "SunEast Flat Hill Solar LLC" to "Flat Hill Solar NY LLC" | 2025-02-11 | 2025-03-27
734 | Ticonderoga Solar | ELP Ticonderoga Solar LLC | Changing Milestone dates including: In service: from 01/2025 to 11/2026 Commercial Operation: from 03/2025 to 12/2026 | 2025-02-10 | 2025-03-27
716 | Moraine Solar Energy Center | Moraine Solar Energy Center, LLC | Changing Interconnection Customer to from "EDF Renewables Development, Inc" to "Moraine Solar Energy Center, LLC" | 2025-01-08 | 2025-03-27
774 | Tracy Solar Energy Center | Tracy Solar Energy Center, LLC | Changing Interconnection Customer name from "EDF Renewables Development, Inc." to "Tracy Solar Energy Center, LLC" and Changing project name from "Tracy Solar Energy Centre" to "Tracy Solar Energy Center" | 2025-01-08 | 2025-03-27
720 | Trelina Solar Energy Center | Trelina Solar Energy Center, LLC | Changing Milestone dates including: In service: from 12/2024 to 04/2028 Initial Synchronization: from 12/2024 to 03/2028 Commercial Operation: from 01/2025 to 04/2028 | 2024-01-27 | 2025-03-27
C24-031 | Crossbuck Energy Storage, LLC | BayWa r.e Projects LLC. | Changing Interconnection Customer name from "BayWa r.e. Solar Projects LLC" to "BayWa r.e Projects LLC" | 2025-03-07 | 2025-03-07
C24-032 | Oakdale Battery Storage LLC | BayWa r.e Projects LLC. | Changing Interconnection Customer name from "BayWa r.e. Solar Projects LLC" to "BayWa r.e Projects LLC" | 2025-03-07 | 2025-03-07
C24-044 | Honey Bee Battery Storage, LLC | BayWa r.e Projects LLC. | Changing Interconnection Customer name from "BayWa r.e. Solar Projects LLC" to "BayWa r.e Projects LLC" | 2025-03-07 | 2025-03-07
C24-047 | Lincoln Park DG, LLC | BayWa r.e Projects LLC. | Changing Interconnection Customer name from "BayWa r.e. Solar Projects LLC" to "BayWa r.e Projects LLC" | 2025-03-07 | 2025-03-07
C24-049 | North Catskill DG LLC | BayWa r.e Projects LLC. | Changing Interconnection Customer name from "BayWa r.e. Solar Projects LLC" to "BayWa r.e Projects LLC" | 2025-03-07 | 2025-03-07
C24-292 | Loganberry Energy Storage, LLC | BayWa r.e Projects LLC. | Changing Interconnection Customer name from "BayWa r.e. Solar Projects LLC" to "BayWa r.e Projects LLC" | 2025-03-07 | 2025-03-07
C24-297 | Deer River Wind | Deer River Wind, LLC | Correction of the Project name to match original documentation to "Deer River Wind" | 2025-03-07 | 2025-03-07
C24-338 | Aria Storage 2 | Terra-Gen Development Company, LLC | Changing Interconnection Customer name from "Terra-Gen Development, LLC" to "Terra-Gen Development Company, LLC" | 2025-02-19 | 2025-03-07
C24-337 | Aria Storage 1 | Terra-Gen Development Company, LLC | Changing Interconnection Customer name from "Terra-Gen Development, LLC" to "Terra-Gen Development Company, LLC" | 2025-02-18 | 2025-03-07
C24-094 | Alcazar 2 | Terra-Gen Development Company, LLC | Changing Interconnection Customer name from "Terra-Gen Development, LLC" to "Terra-Gen Development Company, LLC" | 2025-02-17 | 2025-03-07
C24-093 | Alcazar 1 | Terra-Gen Development Company, LLC | Changing Interconnection Customer name from "Terra-Gen Development, LLC" to "Terra-Gen Development Company, LLC" | 2025-02-16 | 2025-03-07
C24-085 | Arch 4 | Terra-Gen Development Company, LLC | Changing Interconnection Customer name from "Terra-Gen Development, LLC" to "Terra-Gen Development Company, LLC" | 2025-02-15 | 2025-03-07
C24-088 | Arch 3 | Terra-Gen Development Company, LLC | Changing Interconnection Customer name from "Terra-Gen Development, LLC" to "Terra-Gen Development Company, LLC" | 2025-02-14 | 2025-03-07
C24-087 | Arch 2 | Terra-Gen Development Company, LLC | Changing Interconnection Customer name from "Terra-Gen Development, LLC" to "Terra-Gen Development Company, LLC" | 2025-02-13 | 2025-03-07
C24-086 | Arch 1 | Terra-Gen Development Company, LLC | Changing Interconnection Customer name from "Terra-Gen Development, LLC" to "Terra-Gen Development Company, LLC" | 2025-02-12 | 2025-03-07
596 | Alle Catt II Wind | Alle-Catt Wind Energy LLC | Changing the inverter from eighty-one (81) Vestas 4.2 MW turbines to seventy-six (76) Vestas 4.5 MW turbines resulting in an increased MW output of the facility from 340.2 MW to 342.0 MW. | 2024-10-08 | 2025-02-03
644 | Columbia County 1 | Hecate Energy Columbia County 1, LLC | Separating the project into 2 phases consisting of 42MWac and 18MWac as well as changing the Initial Sync Date to 12/1/2026 and COD to 2/28/2027 | 2024-05-01 | 2025-02-03
835 | Luyster Creek Energy Storage 1 | Astoria Generating Company, LP | Changing to a Tesla Megapack 2XL model due to the unavailability of Tesla Megapack 1 | 2024-02-02 | 2025-02-03
N/A | NYSEG rating changes | NYSEG | Rating changes for Bennett-Moraine Rd 115kV, Moraine Rd-Meyer 115kV, Bath-Meads creek 115kV, Meads Creek-Montour Falls 115kV | 2024-10-18 | 2024-11-01
N/A | Colton - Nicholville Rebuild | National Grid | Rebuild the existing ~18 mile long 115kV circuit between Colton and Nicholville, which is a portion of the series 115kV path between Colton, Malone and Willis | 2024-08-09 | 2024-11-01
N/A | Montour Falls | NYSEG | Rearranging the 115 kV line terminations of Montour Falls substation to make construction more feasible | 2024-07-11 | 2024-11-01
1532 | Syracuse | Syracuse, LLC | Repowering facility with BESS | 2024-03-28 | 2024-11-01
1533 | Beaver Falls | Beaver Falls, LLC | Repowering facility with BESS | 2024-03-28 | 2024-11-01
1164 | Glenwood BESS | Juno Power Management LLC | Addition of 1 inverter to generate requested ERIS at POI | 2024-03-14 | 2024-11-01
N/A | Idlewild Project | Con Edison | Con Edison will construct a new 138 kV load serving substation in eastern Queens – Eastern Queens 138 kV – to provide supply to a new Idlewild 27 kV Distribution Area Substation to meet growing demand in Queens. The new Idlewild 27kV Distribution Area Substation will not serve new load; the load to be supplied by Idlewild will be transferred out of an existing Jamaica 27 kV Distribution Area Substation (which is supplied by Jamaica 138 kV substation – an existing substation that will connect to Eastern Queens 138 kV) | 2024-03-28 | 2024-05-03
1443 | Vineyard Mid-Atlantic 2 | Vineyard Mid-Atlantic | Updated parmaters for the projects feeders from the offshore substation to the onshore substation and from the onshore substaiton to the POI | 2024-01-25 | 2024-05-03
683 | KCE NY 2 | KCE NY 2, LLC | Changing Milestone dates including: In service: from 11/10/23 to 5/1/27 Initial Synchronization: from 11/15/23 to 5/15/27 Commercial Operation: from 12/31/23 to 6/1/27 | 2024-01-19 | 2024-05-03
899 | Scriba-Volney Series Reactor | Sithe/Independence Power Partners, LP | Changing COD from 3/24 to 3/26 | 2024-01-09 | 2024-05-03
396 | Baron Wind | Baron Winds, LLC | Changing COD from 12/24 to 12/26 | 2024-01-08 | 2024-05-03
843 | NY37 Solar | Sandy Creek Solar LLC | Shift the project along the line behind the tap connection of Q864 (Greens Corners Solar). Both projects are to be combined behind a single HV breaker. | 2023-12-22 | 2024-04-01
864 | Greens Corners Solar | Boralex | Move the project POI 0.2 miles to the north to accommodate Q843 (NY37 Solar - formerly Sandy Creek Solar). | 2023-12-22 | 2024-04-01
815 | Bayonne Energy Center III | Bayonne Energy Center III, LLC | Updating GSU and PSU parameters, changing the size and number of shunt capacitors, the inverter manufactuer, and the station service load. | 2023-07-17 | 2024-04-01
519 | Canisteo Wind | Canisteo Wind Energy LLC | Updating wind turbines to 67 Vestas V150-4.5 from 69 Vestas V150-4.2. | 2023-05-19 | 2024-04-01
834 | Luyster Creek Energy Storage 2 | Astoria Generating Company, LP | Move project to a new breaker position inside the Astoria West substation, interconnecting via the existing feeder 24122 between breakers 10N, 1N & BT. | 2023-05-05 | 2024-04-01
1340 | Atlantic Shores Offshore Wind Bight 4 | Atlantic Shores Offshore Wind Bight, LLC | Change POI to Brooklyn Clean Energy Hub because POI Farragut 345kV was determined physically infeasible | 2023-11-15 | 2024-03-01
956 | Holtsville 138kV Energy Storage | Holtsville Energy Storage, LLC | Changing gen tie cable route and site location for a more convenient ROW. The POI remains the same. The tie line has also been corrected from 0.1 to 0.5 miles. | 2023-11-06 | 2024-03-01
717 | Morris Ridge Solar Energy Center | Morris Ridge Solar Energy Center, LLC | Reducing number of feeders from 8 to 7 | 2023-08-30 | 2024-03-01
865 | Flat Hill Solar | Flat Hill Solar NY LLC | Changing inverters to SunGrow SG3600UD. | 2023-08-08 | 2024-03-01
885 | Grassy Knoll Solar | SunEast Grassy Knoll Solar LLC | Changing inverters to SunGrow SG3600UD. | 2023-08-08 | 2024-03-01
N/A | CLCPA Phase Line 910 | Avangrid | Line rebuild of NYSEG 115kV line 910 | 2023-10-30 | 2023-12-01
1081 | KCE NY 28 |  | Changing Inverter, PSU impedance change, Collection impedance change, aux power load | 2023-10-13 | 2023-12-01
N/A | 115 kV Line 982 Full Rebuild | Avangrid | (1) Rebuild the existing 21-mile 115 kV line with 1192 Bunting ACSR conductor on the existing centerline with light duty steel monopole structures | 2023-10-10 | 2023-12-01
N/A | Clarks Corners 345/115 Substation Upgrades | Avangrid | (1) 2 Bay 115 kV Expansion to the north. (2) Two (2) new power transformer positions. | 2023-10-10 | 2023-12-01
N/A | Jennison 115/46 kV Substation Upgrades | Avangrid | (1) Rebuild Jennison Substation “off-site” as a 4 bay BAAH 0.75 miles away. (2) Bring line 919 in and out. | 2023-10-10 | 2023-12-01
N/A | 115 kV Line 946 Full Rebuild | Avangrid | (1) Rebuild the existing 20-mile 115 kV line with 1192 Bunting ACSR on an offset and with light duty steel monopoles. | 2023-10-10 | 2023-12-01
N/A | 115 kV Line 949 Full Rebuild | Avangrid | (1) Rebuild the existing 25-mile 115 kV line with 1192 Bunting ACSR conductor on an offset and with light duty steel monopoles | 2023-10-10 | 2023-12-01
N/A | 115 kV Line 962 Full Rebuild | Avangrid | (1) Rebuild the existing 35-mile 115 kV line with 1192 Bunting ACSR conductor on an offset with light duty steel monopole structures. (2) Modify terminal bay at South Owego. (3) Modify terminal bay at Hillside | 2023-10-10 | 2023-12-01
N/A | Lounsberry 115/12.5 kV Substation Full Rebuild | Avangrid | (1) New 115 kV four position Ring bus. (2) Install new 22.4 MVA 115/12.5 kV transformer with LTC. (3) Install new 12.5 kV MV GIS and Control Building. | 2023-10-10 | 2023-12-01
N/A | 115 kV Line 961 Full Rebuild | Avangrid | (1) Rebuild the existing 18-mile 115 kV line with 1192 Bunting ACSR conductor on an offset with light duty steel monopole structures. (2) Modify terminal bay at South Owego. | 2023-10-10 | 2023-12-01
N/A | NYSEG 230 kV Line 68 Full Rebuild | Avangrid | Rebuild the existing 24-mile 230 kV line with bundled 1192 Bunting ACSR conductor on an offset with steel H-Frame structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 230 kV Line 69 Full Rebuild | Avangrid | Rebuild the existing 1-mile 230 kV line with 2156 Bluebird ACSR conductor on an offset with steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 230 kV Line 72 Full Rebuild | Avangrid | Rebuild the existing 27-mile 230 kV line with 2156 Bluebird ACSR conductor on an offset with steel H-Frame structures. | 2023-10-10 | 2023-12-01
N/A | Bath 115/34.5 kV Substation Rebuild | Avangrid | Full rebuild of substation as 115 kV three-bay breaker-and-a-half (BAAH) air insulated substation (AIS) with two (2) new 115/34.5 kV 50 MVA transformers, a +150/-150 MVAR dynamic VAR compensation unit (STATCOM or SVC) | 2023-10-10 | 2023-12-01
N/A | Bennett 115/34.5 kV Substation Expansion and Upgrades | Avangrid | Partial rebuild of the substation with a 115kV bus expansion (extra position for interconnecting a new generator), a 0.05pu Power Flow Control Device, and terminal work on L725. | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 932 Power Flow Control Device & Structure Replacements | Avangrid | Install a Power Flow Control Device at Bennett Substation and perform in-kind structure replacements where required to address all asset condition issues. | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 723 Full Rebuild | Avangrid | Rebuild the existing 15-mile 115 kV line with bundled 795 Drake ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 953 Full Rebuild | Avangrid | Rebuild the existing 5-mile 115 kV line with 2156 Bluebird ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 965 Full Rebuild | Avangrid | Rebuild the existing 22-mile 115 kV line with bundled 795 Drake ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 711 Full Rebuild | Avangrid | Rebuild the existing 3-mile 115 kV line with 2156 Bluebird ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 712 Full Rebuild | Avangrid | Rebuild the existing 6-mile 115 kV line with 2156 Bluebird ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 935 Full Rebuild | Avangrid | Rebuild the existing 9-mile 115 kV line with 2156 Bluebird ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | Stoney Ridge Transformer Replacement | Avangrid | Replace transformer Bank 1 with one (1) new 448 MVA transformer. | 2023-10-10 | 2023-12-01
N/A | Hickling 115/34.5 kV Substation Rebuild | Avangrid | Full rebuild of the substation as a 115 kV four-bay breaker-and-a-half (BAAH) air insulated substation (AIS) design, two (2) new 115/34.5 kV 50 MVA transformers, a new 34.5 kV GIS straight bus with a tie breaker as well as a 12.5 kV GIS straight bus. | 2023-10-10 | 2023-12-01
N/A | Eelpot 115 kV Substation Expansion | Avangrid | Addition of a new 115 kV circuit breaker, a +100/-100 MVAR new dynamic VAR compensation unit (STATCOM or SVC), and 115 kV line terminal work. | 2023-10-10 | 2023-12-01
N/A | Greenidge 115 kV Substation Upgrades | Avangrid | One (1) new 115 kV circuit breaker for Line 968, Line 968 terminal work, and a new 30 MVAR capacitor bank (with 115 kV circuit breaker). | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 722 Full Rebuild | Avangrid | Rebuild the existing 23-mile 115 kV line with 1590 Falcon ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 724 Full Rebuild | Avangrid | Rebuild the existing 15-mile 115 kV line with 1590 Falcon ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 968 Full Rebuild | Avangrid | Rebuild the existing 5-mile 115 kV line with 1590 Falcon ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | Watercure 345/230/115 kV Substation Expansion | Avangrid | Expand the 345 kV two-bay breaker-and-a-half (BAAH) with an extra bay that has one (1) empty bay position, adding a three-bay BAAH for a 115 kV addition, rerouting the Hillside 115 kV lines to Watercure Road’s new 115 kV BAAH, and adding one (1) new 345/115 kV three winding 448 MVA transformer. The transformer will connect with the new 115 kV BAAH and the 345 kV BAAH expansion. | 2023-10-10 | 2023-12-01
N/A | Hillside 230/115/34.5 kV Substation Upgrades | Avangrid | Decommissioning the substation’s 115 kV bus work, decommissioning the two (2) 115/34.5 kV transformers (Banks 1 and 2), re-routing the 115 kV lines to a new 115 kV at Watercure Road substation (at least 1.3 miles), replacing two 230 kV breakers, separating the 34.5 kV breaker position of Bank 3 and 4 (new 34.5 kV breaker and position for Bank 3), grounding the 115 kV side at the 230 kV transformers. | 2023-10-10 | 2023-12-01
N/A | Montour Falls 115/34.5 kV Substation Rebuild | Avangrid | Full rebuild of the substation as a four-bay breaker-and-a-half (BAAH) air insulated substation (AIS) design, two (2) new 115/34.5 kV 50 MVA transformers, two (2) new 115 kV 30 MVAR capacitor banks, a new 34.5 kV GIS straight bus, well as a 12.5 kV GIS straight bus (converted from 8.3 kV). | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 978 Full Rebuild | Avangrid | 115 kV Line 978 is double circuit with 115 kV Line 963 from Montour Falls to Ridge Road to Hillside. Rebuild the existing 16-mile double circuit line with 1192 Bunting ACSR from Montour Falls to Ridge Road and 1192 Bunting ACSR from Ridge Road to Hillside. The new double circuit line would be rebuilt on an offset with custom steel structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 963 Partial Rebuild | Avangrid | 115 kV Line 963 is double circuit with 115 kV Line 978 from Montour Falls to Ridge Road to Hillside. Rebuild the existing 16-mile double circuit line with 1590 Falcon ACSR from Montour Falls to Ridge Road and 1590 Falcon ACSR from Ridge Road to Hillside. The new double circuit line would be rebuilt on an offset with custom steel structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 230 kV Line 67 Full Rebuild | Avangrid | Rebuild the existing 11-mile 230 kV line with bundled 1192 Bunting ACSR conductor on an offset with steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | RGE 115 kV Line 906 Full Rebuild | Avangrid | Rebuild the existing 30-mile 115 kV line with 1590 Falcon ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 115 kV Line 934 Full Rebuild | Avangrid | Rebuild the existing 19-mile 115 kV line with 795 Drake ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 34.5 kV Line 539 Partial Rebuild | Avangrid | Rebuild 2 miles from Marshall to Marsh Hill of the existing 13-mile 34.5 kV line with 477 Pelican ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 34.5 kV Line 542 Full Rebuild | Avangrid | Rebuild the existing 6-mile 34.5 kV line with 477 Pelican ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 34.5 kV Line 546 Partial Rebuild | Avangrid | Rebuild 8 miles of 34.5 kV line from Troupsburg to Marsh Hill with 477 Pelican ACSR conductor on an offset with light duty steel monopole structures. Rebuild 3 miles of the existing 8-mile 34.5 kV line from Troupsburg to Woodhull with 477 Pelican conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | NYSEG 34.5 kV Line 565 Full Rebuild | Avangrid | Rebuild the existing 8-mile 34.5 kV line with 477 Pelican ACSR conductor on an offset with light duty steel monopole structures. | 2023-10-10 | 2023-12-01
N/A | Minor Substation Upgrades | Avangrid | Terminal Equipment at the following stations will be replaced. Moraine Rd Flat St Spencer Hill Yawger Rd Caton Ave West Erie Ave Sta 128 Sullivan Park | 2023-10-10 | 2023-12-01
907 | Harlem River Yard |  | Proposing to reduce the project's capacity from 100 MW to 79.9 MW for both ERIS and CRIS due to site considerations. The decrease will be made through the plant controller to limit the project output to 79.9 MW. | 2023-06-07 | 2023-12-01
1352 | Buchanan Energy Storage - North | Peekskill BESS LLC | Increase maximum withdrawal from the system from 500MW to 505MW | 2023-11-07 | 2023-11-16
1353 | Eastview Energy Storage Project | Central Westchester Power LLC | Increase maximum withdrawal from the system from 400MW to 404MW | 2023-11-07 | 2023-11-16
1360 | Buchanan Energy Storage-South | Peekskill BESS LLC | Increase maximum withdrawal from the system from 500MW to 505MW | 2023-11-07 | 2023-11-16
1502 | Oswego Solar | Oswego Clean Energy LLC | Change from (9) 3.15MVA Sungrow SG3150UD-MV inverters to (8) 3.425MVA Sungrow SG3425UD-MV inverters | 2023-11-02 | 2023-11-16
1493 | Queensboro Renewable Express Circuit A | Queensboro Development, LLC | Designate the 2 feeders to Vernon 138kV, a 345kV PAR, and 138kV transformer as an elective SUF | 2023-10-13 | 2023-11-02
505 | Ball Hill Wind | Ball Hill Wind Energy, LLC | Changing Project model from 4 generators to a 1 generator equivalent model | 2023-09-29 | 2023-11-02
1177 | Souther Tier Energy Center | Southern Tier Energy Center, LLC | Changing from Solar to 4hr Standalone battery storage | 2023-09-29 | 2023-11-02
1307 | Riverhead Energy, LLC | Riverhead Energy | Change inverter from Power Electronics FP3350k to FP4200M inverter | 2023-09-26 | 2023-11-02
1190 | OW Ocean Winds East 4 | Bluepoint Wind, LLC. | Change in POI from Farragut 345kV substation to the Brooklyn Clean Energy Hub 345kV substation | 2023-09-18 | 2023-11-02
N/A | Con Edison’s Jamaica to KIAC-JFK Feeder Replacement | Calpine | Replace the existing 138kV cable between Con Edison’s Jamaica substation and KIAC-JFK’s high voltage switchyard with like in kind. | 2023-09-09 | 2023-11-02
1265 | Monticello Hills Wind | Liberty Renewables Inc. | Addition of 1 turbine to increase the nameplate rating, and increase the PSU size from 20/27/30MVA to 22/29/36MVA | 2023-08-03 | 2023-11-02
637 | Flint Mine Solar | Flint Mine Solar LLC | Changing projects’ In-Service Date, Initial Synchronization Date, and Commercial Operation Date from September 2023, September 2023 and September 2023 to December 2025, December 2025 and May 2026, respectively | 2023-07-11 | 2023-11-02
505 | Ball Hill Wind | Ball Hill Wind Energy, LLC | Increase CRIS and ERIS from 100MW to 103MW | 2023-03-10 | 2023-11-02
1292 | Hemlock Hollow Wind | Liberty Renewables Inc. | Decrease ERIS and CRIS from 90MW to 87.9MW to account for losses | 2023-09-13 | 2023-10-02
612 & 695 | South Fork Wind Farm & South Fork Wind Farm II | South Fork Wind, LLC | Adding a +/-75 MVAr STATCOM unit and a 30.5 MVAr harmonic filter to the 69 kV bus | 2023-08-09 | 2023-10-02
1137 | Salt Rush Wind | Invenergy Wind Development North America LLC | Increase the nameplate to 81MW to achieve the requested 75MW ERIS | 2023-08-08 | 2023-10-02
1138 | Wintergreen Solar | Invenergy Solar Project Development LLC | Increase the nameplate to 79.8MW to achieve the requested 75MW ERIS and the addition of a 13MVAR shunt capacitor to meet powerfactor requirement | 2023-08-08 | 2023-10-02
1230 | Erie-Wyoming County Solar II | ConnectGen Erie-Wyoming LLC | Change from Solar to CSR Solar plus storage ERIS/CRIS Solar 50MW BESS 0MW | 2023-08-02 | 2023-10-02
N/A | Southhampton to Deerfield Transmission | LIPA | Construction of a new 138kV circuit from Southhampton to Deerfield Substation the project will be initially operated at 69kV with the flexibility of converting to 138kV as needed | 2023-08-04 | 2023-09-06
581 | Hills Solar | SunEast Hills Solar LLC | Changing inverter from TEMIC 4200/3360 to SunGrow SG3600UD | 2023-06-07 | 2023-09-06
1374 | Community OSW East Garden City 1 | Community Offshore Wind, LLC | Change in turbine from Vestas V236-15M to GE Haliade- X 17MW | 2023-03-22 | 2023-09-06
586 | Watkins Rd Solar | SunEast Watkins Road Solar LLC | Change the inverter from nine (9) SMA SC 2750-EV to a five (5) 5 x 840 KVA string TMEIC inverters and one (1) 4 x 840 KVA string TMEIC inverter. | 2023-03-20 | 2023-09-06
586 | Watkins Rd Solar | SunEast Watkins Road Solar LLC | Changing inverter from TEMIC 4200/3360 to SunGrow SG3600UD | 2023-03-20 | 2023-09-06
581 | Hills Solar | SunEast Hills Solar LLC | Change the inverter from nine (9) SMA SC 2750-EV to a five (5) 5 x 840 KVA string TMEIC inverters and one (1) 4 x 840 KVA string TMEIC inverter. | 2023-03-16 | 2023-09-06
1223 | Moffitt ESC | Fresh Air Energy II | Increasing nameplate rating from 100MW to 103.9MW and from 100MVA to 140.4MVA to account for losses and meet powerfactor criteria | 2023-07-14 | 2023-08-01
1231 | Mill Point Solar II | ConnectGen Montgomery County LLC | 100MW Solar facility changing fuel source from Solar to CSR (ES+Solar) 100MW solar with 0MW storage. This is an uprate project to 1031 which is CSR. | 2023-05-30 | 2023-07-17
N/A | Clinton Wind Power | AES | Repower the project by replacing turbine blades and drivetrains on each of the individual WTGs at the site. To limit the maximum output at the POI to the current nameplate capacity, developer will use a GE WindCONTROL software platform at the project substation | 2023-08-18 | 2023-06-29
N/A | Bliss Wind Power | AES | Repower the project by replacing turbine blades and drivetrains on each of the individual WTGs at the site. To limit the maximum output at the POI to the current nameplate capacity, developer will use a GE WindCONTROL software platform at the project substation | 2023-08-18 | 2023-06-29
N/A | Altona Wind Power | AES | Repower the project by replacing turbine blades and drivetrains on each of the individual WTGs at the site. To limit the maximum output at the POI to the current nameplate capacity, developer will use a GE WindCONTROL software platform at the project substation | 2023-08-18 | 2023-06-29
N/A | Ellenburg Wind Power | AES | Repower the project by replacing turbine blades and drivetrains on each of the individual WTGs at the site. To limit the maximum output at the POI to the current nameplate capacity, developer will use a GE WindCONTROL software platform at the project substation | 2023-08-18 | 2023-06-29
N/A | Wethersfield Wind Power | AES | Repower the project by replacing turbine blades and drivetrains on each of the individual WTGs at the site. To limit the maximum output at the POI to the current nameplate capacity, developer will use a GE WindCONTROL software platform at the project substation | 2023-08-18 | 2023-06-29
N/A | Chateaugay Wind Power | AES | Repower the project by replacing turbine blades and drivetrains on each of the individual WTGs at the site. To limit the maximum output at the POI to the current nameplate capacity, developer will use a GE WindCONTROL software platform at the project substation | 2023-08-18 | 2023-06-29
N/A | ConEd Brooklyn Clean Energy Hub | Con Edison | Build a new 345kV substation between Rainey-Farragut transmission circuits | 2023-05-22 | 2023-06-05
631 & 887 | NS Power Express & CH Uprate | CHPE LLC | Reconfigure the Astoria 345kV ring bus from an 8-breaker ring bus to a 6-breaker ring bus | 2023-03-29 | 2023-06-05
1041 | Silverline Energy Center | Silverline Energy Center, LLC | Reduce the project size from 200 MW to 150 MW and modify the project to a Co-located Storage Resource project consisting of 150 MW solar Generator and 20 MW energy storage Generator | 2023-02-15 | 2023-06-05
1180 | Union Energy Center | Union Energy Center, LLC | Reduce the project size from 150 MW to 116 MW. | 2023-03-21 | 2023-05-05
1016 | El Steinway 1 | Beacon Wind LLC | Move the Point of Interconnection of the project from Astoria West 138kV substation to a new 345kV substation that is interconnected via a loop-in/loop-out of the two existing Mott Haven-Rainey 345kV circuits | 2023-03-17 | 2023-05-05
1199 | El Steinway 1.1 | Beacon Wind LLC | Reduce the project size from 300 MW to 200 MWand move the Point of Interconnection of the project from Astoria West 138kV substation to a new 345kV substation that is interconnected via a loop-in/loop-out of the two existing Mott Haven-Rainey 345kV circuits | 2023-03-17 | 2023-05-05
1197 | Cold Creek Solar | Northland Power U.S. Projects | Move the Point of Interconnection of the project to a different point along the same transmission line, Station 162- Station 180 115kV line (Line#907) | 2023-03-12 | 2023-05-05
1017 | El Steinway 2 | Beacon Wind LLC | Move the Point of Interconnection of the project from Astoria East 138kV substation to a new 345kV substation that is interconnected via a loop-in/loop-out of the two existing Mott Haven-Rainey 345kV circuits | 2023-03-02 | 2023-05-05
959 | El Oceanside 2 | Empire Offshore Wind LLC | Change wind turbines from GE turbines to Vesta turbines, including the Developer Attachment Facilities. | 2023-02-25 | 2023-05-05
746 | North Street Energy Storage | Peconic River Energy Storage LLC d/b/a North Street Energy Storage | Change proposed Commercial Operation Date from March 31, 2024 to February 7, 2025. | 2023-01-12 | 2023-05-05
612/695 | South Fork I & II Wind Farm | Deepwater Wind South Fork, LLC | Modify In-Service Date, Initial Synchronization Date, and Commercial Operation Date from January 2023, July 2023 and August 2023 to May 2023, August 2023 and November 2023, respectively. | 2023-03-14 | 2023-04-03
686 | Bull Run Solar | Invenergy Solar Development North America LLC | Move the Point of Interconnection along the Patnode-Duley 230kV line to directly interconnect to the new 230kV substation created by Q521 Bull Run II Wind and reduce the Project’s size from 170 MW to 125 MW | 2023-03-09 | 2023-04-03
857 | Columbia Solar | EDF Renewables Development, Inc. | Move the Point of Interconnection along the Edic-Fraser 345kV line | 2023-03-07 | 2023-04-03
971 | East Setauket Energy Storage | Savion LLC | Move the Point of Interconnection along the Holbrook-Miller Place 138kV line | 2023-03-02 | 2023-04-03
957 | Holtsville Energy Storage | Holtsville Energy Storage | Move the Point of Interconnection of Q#957 along the Holtsville-Patchogue 69kV | 2023-02-24 | 2023-04-03
N/A | Nine Mile Point 1 | Nine Mile Point Nuclear Station LLC | Replace 40 and 55 relays with a new digital SEL-700G relay | 2023-02-24 | 2023-04-03
974 | KCE NY 19 | KCE NY 19 LLC | Reduce the project size from 80 MW to 79 MW and modify facility equipment | 2023-02-16 | 2023-04-03
883 | Garnet Energy Center | Garnet Energy Center LLC | Clarify the Point of Interconnection as interconnecting on the Pannell-Clay 345kV circuit#2 (PC2) rather than the Pannell-Clay 345kV circuit#1 (PC1) | 2023-02-14 | 2023-04-03
959 | EI Oceanside 2 | Empire Offshore Wind LLC | Modify the project configuration at the Liotta 138kV Point of Interconnection from a four-bay 138kV bus to a three-bay 138kV bus, and redesign the generating facility equipment (e.g., modify transformers at Liotta substation from 138/230kV transformers to 138/345kV transformers) | 2023-01-17 | 2023-04-03
717 | Morris Ridge Solar Energy Center | EDF Renewables Development, Inc. | Change inverters from Power Electronics (PE) FS3430M to SMA SUNNY CENTRAL 4200 UP-US including its plant step-up transformer impedance and rating | 2023-01-16 | 2023-04-03
1036 | Mainesburg ESS | Juno Power Management LLC | Reduce the project size from 300 MW to 130 MW | 2023-02-10 | 2023-03-02
1068 | Buchanan Point BESS | Juno Power Management LLC | Reduce the project size from 500 MW to 300 MW | 2023-02-10 | 2023-03-02
1136 | Honey Ridge Solar | Honey Ridge Solar 1, LLC | Change Capacitive Resource Interconnection Service (CRIS) request of the Co-located Storage Resource project from 30 MW energy storage Generator and 95 MW solar Generator to 60 MW energy storage Generator and 65 MW solar Generator without changing the Project’s total CRIS request. | 2023-02-02 | 2023-03-02
881 | New Bremen Solar | New Bremen Solar LLC | Modify the project configuration at the Point of Interconnection (POI) from five (5) breaker ring bus to three (3) breaker ring bus including moving the POI along the Bremen-Lowville 115kV (Line#6). | 2023-02-01 | 2023-03-02
1255 | Holtsville Brookhaven Battery Storage | Holtsville Brookhaven Battery Storage LLC | Reduce the project from 80 MW to 79.9 MW | 2023-01-27 | 2023-03-02
1079 | Somerset Solar | Somerset Solar LLC | Reduce the project size from 200 MW to 125 MW | 2023-01-25 | 2023-03-02
783 | South Ripley Solar | ConnectGen Chautauqua County LLC | Modify the Point of Interconnection to interconnect the Project directly to the South Ripley 230kV substation | 2023-01-11 | 2023-03-02
1089/1115 | Flat Creek Solar 1 & 2 | SED NY Holdings LLC | Modify the project configuration to utilize a single/common gen-tie facility for both projects | 2022-12-13 | 2023-03-02
1125 | NYPA Northern NY Priority Transmission Project | NYPA | Modify (1) the new bay at Edic 345kV of the project to include a hybrid breaker, e.g., two breakers in series in a single breaker position, and (2) the design from retiring the entire Porter 230 kV substation to partial retiring the Porter 230kV substation, e.g., keeping Edic 345/230K transformer, Edic-Porter 230kV circuit (Line#17), and two Porter 230/115kV transformers | 2022-11-28 | 2023-03-02
396 | Baron | Innogy | Change wind turbines of the Phase 2 of the project from 27 Vestas V150 4.2 MW to 26 Vestas V150 4.5 MW including their associated electrical equipment resulted in increasing the Phase 2 MW output from 113.2 MW to 117.0 MW and change the Phase 2 COD from December 31, 2023 to December 2024. | 2022-07-01 | 2023-03-02
1203 | Suffragette Solar | EDF Renewables Development, Inc. | Change the transformer model | 2022-12-15 | 2023-02-02
1223 | Moffitt ESC | Fresh Air Energy II | Change the generator step-up transformer from a 2-winding transformer to a 3-winding transformer with wye grounded high side | 2022-12-15 | 2023-02-02
N/A | Ball Hill Wind Farm | Ball Hill Wind Energy LLC | Increase existing generating capability from 100 MW to 103 MW without any change to equipment | 2023-01-03 | 2023-01-19
785 | Erie Wyoming County Solar | ConnectGen Erie-Wyoming LLC | Addition of 175 MW energy storage to proposed 175 MW solar Generator behind the same Point of Interconnection with no change in proposed ERIS. | 2022-12-07 | 2023-01-19
858 | Genesee Road Solar | EDF Renewables Development, Inc. | Reduce project size from 350 MW to 250 MW | 2022-11-11 | 2023-01-19
860 | Rosalen Solar | EDF Renewables Development, Inc. | Reduce project size from 350 MW to 200 MW | 2022-11-11 | 2023-01-19
1188 | North Seneca Solar Project | North Seneca Solar Project, LLC | Change the generator step-up transformer from a 2-winding transformer to a 3-winding transformer | 2022-11-10 | 2023-01-19
N/A | KIAC JFK | Calpine Energy Service LP | Increase in the KIAC generating facility’s auxiliary load by 10 MVA; operation of the KIAC generating facility as a Behind-the-Meter Net Generation Resource to feed the KIA Central Substation#2 in the event of an outage of the distribution 27kV/13.kV switchgear of the KIA Central Substation#2. | 2022-10-27 | 2023-01-19
1096 | Allegany 2 Solar | Northland Power U.S. Projects | Add 40 MW energy storage to proposed 100 MW solar Generator behind the same Point of Interconnection with no change in proposed ERIS | 2022-10-26 | 2023-01-19
1031 | Mill Point Solar | ConnectGen Montgomery County LLC | Add 174 MW energy storage to proposed 250 MW solar Generator behind the same Point of Interconnection with no change in proposed ERIS | 2022-10-13 | 2023-01-19
737 | El Sunset Park | Empire Offshore Wind LLC | Change of turbine composition from sixty-eight 12 MW turbines to fifty-four 15 MW turbines with no change in MW output. | 2022-02-04 | 2023-01-19
422 | Eight Point Wind | NextEra | Change the composition of wind turbines from eighteen (18) GE 5.5MW/6.44MW and six (6) GE 2.03MW/2.78 MVA wind turbines to (8) GE 5.449 MW/6.44 MVA, (10) GE 5.5 MW/6.44 MVA and (7) GE 2.086 MW/2.78 MVA including the electrical characteristics of their corresponding padmount transformers without changing its ERIS values of 111.2 MW | 2022-10-21 | 2022-12-02
N/A | Jericho Rise Wind Farm | Jericho Rise Wind Farm LLC | Increase existing generating capability from 77.7 MW to 80.3 MW via software improvement | 2022-10-21 | 2022-12-02
1180 | BPUS Generation Development LLC | BPUS Generation Development LLC | Operate the power factor (PF) of the facility within +/- 0.95 while its PF capability is a leading 0.95 PF to a lagging 0.83 PF | 2022-08-29 | 2022-12-02
800 | Rich Road Solar | EDF Renewables Development, Inc. | Change its 240 MW Large Facility project comprised of 240 MW solar Generator to a 240 MW Large Facility project comprised of 240 MW solar Generator and 20 MW battery Generator behind a single Point of Injection. | 2022-08-15 | 2022-12-02
857 | Columbia Solar | EDF Renewables Development, Inc. | Change its 350 MW Large Facility project comprised of 350 MW solar Generator to a 350 MW Large Facility project comprised of 350 MW solar Generator and 20 MW battery Generator behind a single Point of Injection. | 2022-08-15 | 2022-12-02
858 | Genesee Road Solar | EDF Renewables Development, Inc. | Change its 350 MW Large Facility project comprised of 350 MW solar Generator to a 350 MW Large Facility project comprised of 350 MW solar Generator and 20 MW battery Generator behind a single Point of Injection. | 2022-08-15 | 2022-12-02
1040 | Riverline Energy Center | Riverline Energy Center LLC | Change the project fuel type from a 200MW solar project to a 200 MW battery project. | 2022-06-30 | 2022-12-02
1088 | Harvest Hills Solar | ConnectGen Cayuga County LLC | Change its 200 MW Large Facility project comprised of 200 MW solar Generator to a 200 MW Large Facility project comprised of 200 MW solar Generator and 150 MW battery Generator behind a single Point of Injection. | 2022-06-23 | 2022-12-02
N/A | Nine Mile Point 2 | Nine Mile Point Nuclear Station LLC | Install a 2MW electrolyzer, resulting in a 2MW increase to the facility’s auxiliary load | 2022-08-29 | 2022-11-01
637 | Flint Mine Solar | Flint Mine Solar LLC | Change proposed Commercial Operation Date from September 2023 to October 2024 | 2022-08-26 | 2022-11-01
276 | Homer Solar Energy Center | EDF Renewable | Move POI approximately 728 feet south/southwest along the Cortland-Fenner 115kV line | 2022-08-22 | 2022-11-01
N/A | NGrid LTP Project | NGrid | Rebuild Mortimer-Pannell 24/25 115kV circuits to increase the line ratings from 150 MVA to 250 MVA. | 2022-07-05 | 2022-11-01
1206 | NY Interconnection 2 | NY Interconnection LLC | Change the project type from a Class Year Transmission project to a Large Generating Facility project. | 2022-09-13 | 2022-10-03
1207 | NY Interconnection 1 | NY Interconnection LLC | Change the project type from a Class Year Transmission project to a Large Generating Facility project. | 2022-09-13 | 2022-10-03
618 | High River Solar | High River Energy Center LLC | Change the inverters from (49) 2.0 MVA GE LV5-1511-30-UL-SLR to (30) 3.43 MVA/3.09 MW @35°C Power Electronics FS3430M inverters including the electrical characteristics of their corresponding padmount transformers and feeders. | 2022-06-09 | 2022-10-03
619 | East Point Solar | East Point Energy Center LLC | Change the inverters from (27) 2.0 MVA inverters GE LV5-1511-30-UL-SLR to (15) 4.2 MVA Sunny Central 4200 UP-US Solar Inverters feeders. | 2022-06-09 | 2022-10-03
N/A | Far Rockaway GT1 | PSEG-LIPA | Install the evaporative cooling and wet compression system resulted in increasing the Summer ERIS baseline from 53.5 MW to 61.5 MW. | 2022-07-31 | 2022-09-01
1007 | NYC Energy LLC Phase 2 | NYC Energy LLC | Relocate the POI within the same Hudson Avenue substation. | 2022-07-19 | 2022-09-01
596 | Alle Catt II Wind | Invenergy | Change the generation composition from twelve (12) GE 2.3-116 series and eighty-six (86) 3.6-137 series wind turbines for a total maximum output of 339.7 MW to eighty-one (81) Vestas V150-4.2 series wind turbines for a total maximum output of 340.2 MW. | 2021-10-08 | 2022-08-01
393 | Berrians East Repower | NRG | Change proposed In-Service, Initial Synchronization, and Commercial Operation Dates from 5/2022, 8/2023, and 12/2023 to 5/2023, 8/2024 and 12/2024, respectively. | 2022-06-15 | 2022-07-01
678 | Calverton Solar Energy Center | LI Solar Generation, LLC | Change (1) the composition of inverters from 22 x 1.155 MVA GE inverters to 8 x 3.43 MVA Power Electronics FS3430M inverters, (2) the composition of padmount transformers from 11 x 2.31 MVA transformers with 8 x 3.51 MVS transformers, (3) the main transformer from a two-winding 138/34.5kV 25.4 MVA transformer to a three-winding 138/34.5/13.8kV 30 MVA transformer, and (4) the generating collection system design, but maintain the project’s total maximum output at 22.9 MW. | 2022-05-27 | 2022-07-01
912 | Intrepid Storage 69 | Hecate Grid Intrepid LLC | Move the Point of Interconnection of the project from Barrett 69kV substation to a new 34.5kV substation that is interconnected via a loop-in/loop-out of the two existing Barrett – Oil City and Barrett – Ocean 4T2 34.5 kV lines. | 2022-05-27 | 2022-07-01
918 | Intrepid Storage 138 | Hecate Grid Intrepid LLC | Move the Point of Interconnection of the project from Barrett 138kV substation to a new 138kV substation that is interconnected via a loop-in/loop-out of the two existing Barrett – Valley Stream 138 kV lines. | 2022-05-27 | 2022-07-01
422 | Eight Point Wind | NextEra | Change the composition of wind turbines from twenty-seven (27) GE 3.43-130 series and four (4) GE 2.3-130 series wind turbines to eight-teen (18) GE 5.5MW/6.44MW and six (6) GE 2.03MW/2.78 MVA wind turbines and also increase its ERIS to 111.2 MW from its ERIS baseline of 101.2 MW. | 2022-05-17 | 2022-07-01
N/A | NYSEG Wave Trap | NYSEG | Change the design of the wave trap of the East Towanda-Hillside 230 kV line (Line#70) from 3000A to 2000A. | 2022-05-18 | 2022-06-02
543 | NY Transco Segment B | Transco | Classify the Dover phase angle regulators (PARs) as a transmission facility and part of the project and install a by-pass breaker in lieu of a by-pass disconnect for the Dover PARs. | 2022-04-22 | 2022-06-02
1125 | NYPA Northern NY Priority Transmission Project | NYPA | Change the breaker arrangement of the new Haverstock 345 kV substation from a breaker-and-a-half scheme to a double-breaker double-bus double-bus-tie-breaker scheme, move the termination of the Adirondack-Marcy line to a separate bay within Marcy 345 kV substation and relocate the new Wills 230 kV site from north of the existing Willis 230kV site to east of the existing Willis 230kV site. | 2022-02-17 | 2022-05-05
958/959 | EI Oceanside 1 & 2 | Empire Offshore Wind LLC | Move the Point of Interconnection (POI) of Q959/958 from the Barrett 138 kV substation to a new Barrett 138kV expansion substation, which is also known as the Liotta 138kV substation that is interconnected via a loop-in/loop-out of the two existing Barrett-Valley Stream 138kV lines. | 2022-03-04 | 2022-04-01
720 | Trelina Solar | Trelina Solar Energy Center LLC | Reduce the generation output from 80MW to 79.8MW | 2022-02-08 | 2022-04-01
519 | Canisteo Wind | Canisteo Wind Energy LLC | Change the generation composition from ninety (90) GE 3.23-130 series wind turbines for a total maximum output of 290.7 MW to sixty-nine (69) Vestas V150-4.2 series wind turbines for a total maximum output of 289.8 MW. | 2021-08-06 | 2022-04-01
495 | Mohawk Solar | Mohawk Solar LLC | Change proposed Commercial Operation Date from December 2022 to November 2024 | 2022-01-26 | 2022-03-01
546 | Roaring Brook Wind | Atlantic Wind LLC | Change proposed Commercial Operation Date from December 2021 to April 2022. | 2022-01-12 | 2022-03-01
N/A | Nine Mile Point 2 | Nine Mile Point Nuclear Station LLC | Replace the generator step-up transformers | 2021-08-11 | 2022-03-01
N/A | Flats Rd Substation | CHG&E | Change the design kV level of the Flats Rd 69kV substation from a 69kV substation to a 115kV substation, but continue to operate it as a 69kV substation. | 2021-11-03 | 2022-01-04
396 | Baron | Innogy | Change Phase 2 COD of the project from 7/9/23 to 12/31/23. | 2021-10-22 | 2022-01-04
1142 | Minerva BESS I | Minerva Power Connection LLC | Change the MW size of the project from 600 MW to 300 MW | 2021-10-07 | 2022-01-04
580 | WNY STAMP | Genesee County Economic Development | Reconfigure the new Q580 STAMP load 345 kV substation design from a breaker-and-half substation to a normally non-bus tie, two-ring bus substation and reduce the proposed load project from 500 MW to 300 MW. | 2021-09-30 | 2021-12-01
N/A | RG&E LTP Project | RG&E | Rebuild RG&E transmission lines: Lines 917 (Station 7 - Station 69), 945 (Station 69 - Station 71), 946 (Station 70 - Station 71) and 947 (Station 418 – Station 113 – Spencerport – Station 70). | 2021-07-27 | 2021-10-01
393 | Berrians East Repower | NRG | Change proposed In-Service Date, Initial Synchronized Date, and Commercial Operation Date from 01/2022, 01/2023, and 06/2023 to 05/2022, 08/2023, and 12/2023, respectively. | 2021-07-21 | 2021-08-02
546 | Roaring Brook Wind | Atlantic Wind LLC | Change proposed In-Service Date, Initial Synchronized Date, and Commercial Operation Date from 03/2021, 04/2021, and 04/2021 to 09/2021, 10/2021, and 12/2021, respectively. | 2021-07-15 | 2021-08-02
396 | Baron | Innogy | Change the COD of Phase 1 of the project to 12/15/22 and clarify the MW sizes of Phases 1 and 2 of the project as 121.8 MW and 113.2 MW, respective. | 2021-06-15 | 2021-07-01
783/1014 | South Ripley Solar | ConnectGen Chautauqua County LLC | Merge the queue positions of two co-located projects – Q783 South Ripley 270 MW solar project and Q1014 South Ripley 20 MW energy storage project | 2021-04-28 | 2021-06-01
505 | Ball Hill Wind | Ball Hill Wind Energy, LLC | Change the turbine composition from twenty-nine (29) 3.45 MW Vestas V126 turbines to twenty-two (22) 4.3MW Vestas V150 and three (3) 4.2 MW Vestas V136 turbines without changing the project’s size of 100 MW. | 2021-04-02 | 2021-06-01
783 | South Ripley Solar | ConnectGen Chautauqua County LLC | Change the project’s inverter nameplate rating from 273.8 MW to 278.1 MW without changing the 270 MW total output of the project. | 2021-04-05 | 2021-05-03
958/959 | EI Oceanside 1 & 2 | Empire Offshore Wind LLC | Reduce Q959 from 1500 MW to 1260 MW and Q958 from 1000 MW to 96 MW and clarifying Q958 as a 96 MW uprate or a 1356 MW alternative project of Q959. | 2021-03-26 | 2021-05-03
N/A | NYPA St. Lawrence AVR Upgrade | NYPA | Replace the automatic voltage regulator (AVR) of St. Lawrence units | 2021-03-12 | 2021-05-03
579 | Blue Stone Wind | Northland Power | Change wind turbines from thirty-six (36) 3.45MW Vestas turbines to twenty-six (26) 4.3MW Vestas turbines resulted in decreasing the project’s total MW output from 124.2 MW to 111.8 MW | 2021-03-11 | 2021-05-03
706 | High Bridge Wind | Northland Power | Change the turbine rating from Vestas V150 4.2 MW to Vestas V150 4.3 MW without changing the project’s size of 100.8 MW total MW output. | 2021-03-11 | 2021-05-03
N/A | PSEG-LIPA SDU Project | NYPA | Modify the PSEG-LIPA CY17 SDU to build a new underground Terryville-Flowerfield 69 kV line rather than reconductoring the Port Jefferson-Stony Brook 69 kV line. | 2021-03-11 | 2021-05-03
620 | North Side Solar | North Park Energy, LLC | Move the POI of the project approximately 0.72 mile to the east of its original location. | 2021-02-25 | 2021-05-03
612/695 | South Fork I & II Wind Farm | Deepwater Wind South Fork, LLC | Change wind turbines from seventeen (17) 8 MW Siemens turbines for a 136 MW total output to twelve (12) 11.5 MW Gamesa turbines for a 138 MW total output. | 2020-10-09 | 2021-05-03
777 | White Creek Solar | Community Energy Solar, LLC | Change the composition of the project inverters from fifty-four (54) 2.7 MVA TMEIC units to thirty-one (31) 6 x 0.795 MVA TMEIC inverter units. | 2021-03-03 | 2021-04-07
387 | Cassadaga | Innogy | Change proposed In-Service Date from 1/2021 to 12/2020, change the proposed Initial Synchronized Date from 12/2020 to 3/2021 and change Commercial Operation Date from 4/2021 to 6/2021. | 2021-02-19 | 2021-04-07
396 | Baron | Innogy | Change proposed In-Service Date from 5/2020 to 5/2022, change proposed Initial Synchronized Date from 5/2020 to 6/2022 and change proposed Commercial Operation Date from 7/2020 to 9/2022. | 2021-02-19 | 2021-04-07
710 | Horseshoe Solar | Invenergy Solar Development North America LLC | Change the inverters from 63x 3.2MVA inverters to 48x 4.2MVA, replace the transformer from one 121 MVA 3- winding transformer (115/34.5/13.8kV) to two 66 MVA 3-winding transformers (115/34.5/13.8kV) and shorten the generator lead from 0.75 miles to 0.1 miles. | 2021-02-15 | 2021-04-07
987/1045 | NY Wind Holbrook 2 | Bay State Wind | Change the classification of Q987 and Q1045 as uprated projects of Q766, e.g., (1) Q987 is a 44 MW uprate of Q766 and (2) Q1045 is (i) a 126 MW uprate of Q987 or (ii) a 170 MW uprate of Q766. | 2021-02-09 | 2021-04-07
950 | Orlean Solar | Orleans Solar LLC | Change the number of circuits looping into the new proposed substation from three Lockport-Mortimer lines (Lines#111, 113 and 114) to two Lockport-Mortimer lines (Lines#111 and 113). | 2021-02-05 | 2021-04-07
N/A | NYPA Niagara Exciter and Governor Upgrade | NYPA | Replace the exciters and governors of Niagara units. | 2021-02-03 | 2021-04-07
531 | Number 3 Wind | Invenergy | Change the composition of the project from a configuration of five (5) GE 2.3-116 series wind turbines and twenty-six (26) GE 3.6-137 series wind turbines for a total maximum output of 105.8MW and a 10.5MVAR cap bank to a configuration of five (5) GE 2.3-116 series wind turbines and twenty-two (22) Vestas V150-4.2 series wind turbines for a total maximum output of 103.9MW and a 7.2MVAR cap bank. | 2021-01-20 | 2021-04-07
825 | Setauket Energy Storage | Setauket Energy Storage, LLC | Reduce the size of the project from 76.8 MW to 65.3 MW. | 2020-12-15 | 2021-04-07
971 | East Setauket Energy Storage | Savion, LLC | Reduce the size of the project from 293.5 MW to 125 MW. | 2020-12-15 | 2021-04-07
631 | NS Power Express | Champlain Hudson Power Express, Inc. | Change the project from a three-terminal HVdc project to a two-terminal HVdc project, eliminating the New Scotland converter station and the proposed 320 kV DC transmission line from New Scotland to the Astoria converter station connecting to the Astoria Annex 345 kV station. | 2021-02-10 | 2021-03-01
N/A | PSEG-LIPA LTP Project | PSEG-LIPA | Convert the Wildwood-Riverhead 69 kV line to the Wildwood-Riverhead 138 kV line. | 2021-02-09 | 2021-03-01
907 | Harlem River Yard | 174 Power Global | Change the inverter manufacturer from SMA to Tesla. | 2021-02-02 | 2021-03-01
931 | Astoria Energy Storage | Hanwha Energy USA Holdings d/d/a/ 174 Power Global | Change the inverter manufacturer from SMA to Tesla. | 2021-02-02 | 2021-03-01
543 | NY Transco Segment B | Transco | Change the single 50% series compensation system to a two-step series compensation system (16.67% and 33.33%). Also change the proposed line ratings of transmission lines 34, 42, 44 and 305. | 2020-12-28 | 2021-03-01
956 | Holbrook Energy Storage | Holbrook Energy Storage | Reduce the project size from 296.4 MW to 110 MW. | 2020-12-23 | 2021-03-01
811 | Cider Solar | Hecate Energy Cider Solar LLC | Move the proposed Point of Interconnection (POI) approximately 3 miles from the original proposed POI along the same transmission line. | 2020-10-14 | 2021-03-01
N/A | NGrid LTP Project | NGrid | Rebuild a major portion of Lockport – Batavia 115kV circuit (aka circuit #112). | 2020-11-12 | 2021-02-02
766 | NY Wind Holbrook | Bay State Wind | Replace (a) two AC generator leads of the generating facility directly connected to the Holbrook 138kV substation to (b) a combination of a monopole HVdc and two AC leads connected to the Holbrook 138kV substation. | 2020-10-19 | 2021-02-02
N/A | ConEd LTP Projects | ConEd | Add (1) 2nd 345/138 kV PAR controlled Rainey – Corona feeder, (2) 3rd 345/138 kV PAR controlled Gowanus – Greenwood feeder, and (3)345/138 kV PAR controlled Goethals – Fox Hills feeder with Fox Hills rebuild as a ring bus. | 2020-11-12 | 2020-12-08
430 | Cedar Rapids Transmission | H.Q. Energy Services U.S. Inc. | Change the composition of the circuit from NYPA MAL4 through the NGrid line from 100% of 1590 MCM AAC conductor to a combination of 636 MCM ACSS conductor and 1590 MCM AAC conductor. | 2019-11-26 | 2020-12-08
740 | Oakdale Battery Storage | Bay State Wind | Change inverters of the project from forty-eight (48) SMA 2750-EV-US inverters to forty-seven (47) SMA SC-3600 US-UP inverters with no change to the total MW charging or discharging of the project. | 2020-09-30 | 2020-12-01
545A | Empire State Line | NextEra | Reconfigure the two double circuit entrances to the new Dysinger 345 kV substation to two single circuit entrance and one double circuit entrance. | 2020-09-28 | 2020-12-01
393 | Berrians East Repower | NRG | Modification to the proposed generator to retire the existing 38.5 MVAR cap bank and replace the existing 547 MVA H65 generator with a new H84 generator with a rating of 600 MVA in order to meet Con Edison’s power factor requirements. | 2020-07-12 | 2020-11-02
N/A | Greenidge | Emera Energy U.S. Sub. No. 1, Inc. | Increase the behind-the-meter (BTM) load at Greenidge generation bus from the current 32 MW to 64 MW and continue to maintain the reverse relay tripping to prevent the BTM load facility from drawing power from the grid. | 2020-08-06 | 2020-10-05
543 | NY Transco Segment B | Transco | Expand the configuration of the Van Wagner substation to a two-bay breaker-and-a-half substation to loop Athens-Pleasant Valley and Leeds Pleasant Valley 345 kV lines (Line 91 and 92, respectively) into the Van Wagner substation resulting in the creation of four new line segments: an Athens-Van Wagner line, a Leeds-Van Wagner line, and two Van Wagner-Pleasant Valley lines with reconductoring of the two new Van Wagner- Pleasant Valley lines. This modification retracts the initial proposal of the radial connection of the Van Wagner cap banks to Pleasant Valley substation. | 2020-06-18 | 2020-10-05
396 | Baron | Innogy | Change (i) the turbine composition from eleven (11) Gamesa G114 2.625 MW and fifty-six (56) Nordex N117 3.675 MW to eight (8) Gamesa G114 2.625MW and fifty-one (51) Vestas V150 4.2MW (no change in the MW size of the project), (ii) the main transformer from one (1) 34.5/230 kV, 150/200/250 MVA transformer to two (2) 34.5/230 kV, 84/112/135 MVA transformers, and (iii) the Commercial Operation Date from December 2020 to two operational phases with a proposed Commercial Operation Date for phase 1 (126MW) of September 1, 2022, and a proposed Commercial Operation Date for phase 2 (109MW) of July 9, 2023. | 2020-05-26 | 2020-08-31
543 | NY Transco Segment B | Transco | Change a portion of the project from (1) removing the existing 138 kV line from Shoemaker (O&R) to Sugarloaf (O&R) 138 kV substations and installing two new 138 kV lines on a double circuit structure between the two stations to (2) keeping the existing 138 kV line from Shoemaker-Sugarloaf 138 kV line as is, repurposing the parallel path Rock Tavern-Sugarloaf 115 kV and adding a Sugarloaf 115/138 kV transformer. | 2020-05-15 | 2020-08-07
N/A | Astoria 3 | Astoria Generating Company L.P. | Replace the equipment, e.g., generator step up transformers, generator leads, and other equipment at site, associated with Astoria 3 with the equipment associated with the retired Astoria 4 that also results in changing Astoria 3’s breaker positions. | 2020-01-24 | 2020-03-05
430 | Cedar Rapids Transmission | H.Q. Energy Services U.S. Inc. | Change the route of the #12 Line (National Grid 115 kV Alcoa – Dennison #12 line) that is required to be reconductored as part of the project resulted in shortening the existing line from ~3 miles to ~1.7 miles. | 2019-11-26 | 2020-03-05
393 | Berrians East Repower | NRG | Change the turbine composition from three simple cycle 7F turbines to a single simple cycle 7H turbine, which could reduce the net total output of the project from 508 MW in summer and 584 MW in winter to 431 MW in summer and 438 MW in winter. | 2019-08-15 | 2020-02-04
505 | Ball Hill Wind | Ball Hill Wind Energy, LLC | Change COD to 12/2021. | 2016-10-06 | 2020-02-04
N/A | Ramapo Bank 1300 Replacement | O&R | Replace the existing three single-phase Ramapo 345/138 kV transformer (Bank 1300) with a new single three-phase transformer. | 2019-10-25 | 2019-12-04
N/A | Greenidge | Emera Energy U.S. Sub. No. 1, Inc. | Add a 30 MW load at Greenidge generation bus including a reverse relay tripping to prevent the load facility from drawing power from the grid. | 2019-09-23 | 2019-12-04
N/A | Erie/Steel Wind Facilities | Erie Wind, LLC/ Niagara Wind Power, LLC | Replace the wind turbines of the existing Erie/Steel Wind facility (PTIDs 323596 and 323693) from Clipper 2.5 MW wind turbines for a total of 35 MW to GE 2.5 MW wind turbines for the same total of 35 MW. | 2019-03-20 | 2019-12-04
546 | Roaring Brook Wind | Atlantic Wind LLC | Change (1) the composition of the project from 39 Gamesa 2.0 MW wind turbine generators to a combination of 12 Siemens Gamesa 4.5 MW, 3 Siemens Gamesa 4.2 MW and 5 Gamesa 2.625 MW wind turbine generators, resulting in a change of Project output from 78 MW to 79.725 MW; (2) the individual wind turbine step-up transformers from thirty-nine 2.35 MVA pad mounted transformers to twelve 5.5 MVA, three 5.0 MVA, and five 2.85 MVA units to match the wind turbine generators; (3) the 34.5 kV collector system to account for connection of 20 wind turbines instead of the original 39 wind turbines; and (4) the 115/34.5 kV main step up transformer from 60/80/100 MVA, 9% impedance to a main step-up transformer with 51/68/85 MVA, 9.5% impedance. | 2019-09-10 | 2019-11-01
678 | Calverton Solar Energy Center | LI Solar Generation, LLC | Change the POI within the PSEG-LIPA Edwards 138 kV substation from between breaker#1320 and bank#2 to between bank#2 and breaker#1360 resulted in also moving the new breaker from between breaker#1320 and bank#2 to between bank#2 and breaker#1360. | 2019-08-14 | 2019-09-05
698 | Energy Storage II | Helix Ravenswood, LLC | Change the POI from Vernon-Rainey 138kV to Rainey- Farragut 345kV. | 2019-07-17 | 2019-09-05
276 | Homer Solar Energy Center | EDF Renewable | Change the proposed facility from a 90 MW wind farm facility to a 90 MW solar farm facility. | 2019-05-21 | 2019-09-05
522 | NYC Energy | NYC Energy LLC | Change the proposed facility from a 79.9 MW gas turbine facility to a 79.9 MW energy storage facility. | 2019-02-28 | 2019-09-05
543 | NY Transco Segment B | Transco | Change in the physical location of the two shunt capacitor banks connecting at the Pleasant Valley 345 kV substation of Q543 from the Pleasant Valley 345 site to the Van Wagner site, which is 0.81 miles away. | 2019-07-08 | 2019-08-01
458 | CH Interconnection | TDI USA Holding | Change the operating voltage of the HVdc cable of Q458 CH Interconnection from 320 kV to 400 kV. | 2019-06-11 | 2019-08-01
387 | Cassadaga | Innogy | Change (1) the composition of the wind turbines from 42 Vestas 3.0 MW V112s with a total output of 126.0 MW to 10 Gamesa 2.625 MW G114s and 27 Nordex 3.675 MW N117s with a total output of 126.5 MW and (2) the main transformer from a three-winding 115/34.5/13.8kV 84/112/140 MVA transformer with 8% impedance to a two-winding 115/34.5kV 112/140 MVA transformers with 11% impedance. | 2019-01-18 | 2019-08-01
396 | Baron | Innogy | Change (1) the composition of the wind turbines from 100 Vestas 3.0 MW V112s with a total output of 300.0 MW to 11 Gamesa 2.625 MW G114s and 56 Nordex 3.675 MW N117s with a total output of 238.4 MW and (2) the entrance into the Canandaigua substation from the Northwest corner to the Southeast corner resulted in an additional 600 ft of 230kV underground cable. | 2019-01-18 | 2019-08-01
596 | Alle Catt II Wind | Invenergy | Change (1) the composition of wind turbines of Q596 project from one hundred five GE 3.23-130 turbines for a total of 339.1 MW to eighty-six GE 3.6-137 and twelve GE 2.3-116 turbines for a total of 339.78 MW resulted in an increase of 0.68 MW of the project’s Energy Resource Interconnection Service (ERIS) value and (2) the length of the generator lead line from 8 to 10.68 miles. | 2019-05-07 | 2019-07-08
N/A | NYSEG and RG&E Multiple LTP Projects | NYSEG/RG&E | · Frog Valley Capacitor · Big Tree Expansion · Erie St Expansion · Stolle Rd Rebuild · Robinson Rd Rebuild/Expansion · Line 947 Uprate · Station 418 to Station 48 New 115kV Line · Station 56 Reconfiguration · Hook Rd Capacitor · Coddington Series Bus-Tie Breaker · Etna Series Bus-Tie Breaker · Line 981 Uprate (Etna-East Ithaca) · Fuller Hollow Expansion · Langdon Rd Expansion · Oakdale Expansion and Westover 115kV Removal · Coopers Corners Rebuild · Colliers Rebuild · East Norwich Rebuild · Jennison Rebuild · Fraser Expansion and Delhi 115kV Removal · New Morris Station · Klinekill Reverse Power Relay · Churchtown Capacitor · Ten Mile River Expansion | 2019-05-03 | 2019-07-08
579 | Blue Stone Wind | Calpine | Change (1) the turbine composition of the project from 36 Vestas 3.45 MW turbines with a total generating capacity of 124.2 MW to 27 Siemens Gamesa SG4.X- 145 turbines with an operating configuration of 4.6 MW per turbine to maintain the total generating capacity of 124.2 MW and (2) the plant GSU transformer from an 86 MVA transformer to a 133 MVA transformer. | 2019-04-04 | 2019-07-08
N/A | Ramapo Bank 2300 Replacement | O&R | Replace the existing three single-phase Ramapo 345/138 kV transformer (Bank 2300) with a new single three- phase transformer | 2019-05-17 | 2019-06-10
N/A | Oak Street 138kV Substation | O&R | Build a new Oak Street 138kV substation between the O&R Burns to Corporate Drive 138 kV line (Line 702) | 2019-05-01 | 2019-06-10
495 | Mohawk Solar | Mohawk Solar LLC | Change (1) the inverter type from 45 SMA SC2200-US central station inverters to 710 SMA Sunny Highpower PEAK3 150 kVA string inverters, (2) inverter step-up transformers from 45, 2.2 MVA pad mounted transformers to eight (8) 1 MVA, fifteen (15) 2 MVA, and nineteen (19) 3 MVA units, (3) three 34.5 kV collector circuits from the solar array areas to the collector substation to four 34.5 kV collector circuits, and (4) the 115/34.5 kV main step-up transformer from 60/80/100 MVA, 8% impedance to 66/88/110 MVA, 9.5% impedance. | 2019-04-05 | 2019-05-03
N/A | Burns-West Nyack 138kV | O&R | Build a new 138kV line from Burns to West Nyack (Line 705) | 2019-03-14 | 2019-05-03
531 | Number 3 Wind | Invenergy | Add a 10.5 MVAr capacitor bank at 34.5 kV side and change the rating of the main transformer at the collector station to 78/104/130 MVA. | 2019-03-06 | 2019-04-01
363 | Poseidon Offshore | Anbaric Development Partners, LLC | Change the project type from a Class Year Transmission project to a Large Generating Facility project. | 2018-06-28 | 2019-04-01
596 | Alle Catt II Wind | Invenergy | Move the Point of Interconnection (POI) of the project approximately 300’ south of the original POI along the same line. | 2019-01-28 | 2019-03-06
766 | NY Wind Holbrook | Bay State Wind | Change the generator lead technology from HVdc to AC | 2019-01-23 | 2019-03-06
531 | Number 3 Wind | Invenergy | Change the composition of the project’s wind turbines from forty-six (46) GE2.3‐116 turbines to twenty-six (26) GE3.6‐137 turbines and five (5) GE 2.3‐116 turbines for the same total output of 105.8MW. | 2019-01-22 | 2019-03-06
764 | NY Wind Shoreham (aka Canal) | Bay State Wind | Change an alternative POI, e.g., Canal 138 kV, to a primary POI and reduce the size of the project from 880 MW to 440 MW | 2019-01-22 | 2019-03-06
422 | Eight Point Wind | NextEra | Change wind turbines from thirty-two (32) GE 3.23‐130 series for a total of 101.2 MW to twenty-seven (27) GE 3.43‐130 and four (4) GE 2.3‐130 series wind turbines for a total of 101.8 MW resulted in increasing the project’s Energy Resource Interconnection Service (ERIS) value from 101.2 MW to 101.8 MW, which is a 0.6 MW increase in proposed ERIS value. | 2019-01-15 | 2019-03-06
N/A | 2nd Riverhead-Canal 138kV | LIPA | Build a 2nd 138kV line from Riverhead to Canal | 2019-01-15 | 2019-03-06
579 | Blue Stone Wind | Calpine | Change wind turbines from 36 Vestas 126 3.45 MW turbines to 31 Vestas 136 4.0 MW turbines. | 2018-12-13 | 2019-01-09
596 | Alle Catt II Wind | Invenergy | Reduce the project’s size comprised of 118 GE 3.23 MW turbines for a total of 381.1 MW to 105 GE 3.23 MW turbines for a total of 339.1 MW (10.78% reduction in size). | 2018-11-27 | 2019-01-09
N/A | Hempstead Railroad | Covanta | Replace the normally out-of-service generator step-up (GSU) transformer Bank 1 from a 15/20/25 MVA, 13.2kV-69kV, with an impedance of 6.66% on 15 MVA to a 57.8/76.9/96 MVA, 13.2kV-69kV, with an impedance of 8.8% with ± 7.5% tolerance on 57.8 MVA base. | 2018-11-12 | 2019-01-09
387 | Cassadaga | Everpower | Relocate the Cassadaga POI station location to a nearby parcel. | 2018-04-02 | 2018-09-06
N/A | Leeds-Hurley Series Compensation | Central Hudson | Replace the conventional series compensation with SmartWire SmartValve technology. | 2017-12-15 | 2018-05-01
349 | Taylor Biomass | Taylor Biomass Energy- Montgomery, LLC | Change of COD to 04/2021. | 2017-12-08 | 2018-01-05
N/A | Fenner | Canastota LLC | Replace 19 out of 20 GE turbines from a 1.5 MW GE wind turbine with a 70.5 m rotor with a 1.5 MW SLE GE win turbine with an 82.5 m rotor. | 2017-10-16 | 2018-01-05
N/A | Nine Mile Point 2 | Nine Mile Point Nuclear Station LLC | Replace the GE Mark I Analog Turbine Control System with a Westinghouse Digital Turbine Control and Protection System | 2017-09-19 | 2018-01-05
N/A | Avangrid NYSEG/RG&E BES Projects | NYSEG/RG&E | Addition of Geneva, Ithaca, Oneonta North and Rochester transmission projects does not require an SIS. | 2017-07-24 | 2018-01-05
N/A | Canandaigua | Canandaigua LLC | Replace Clipper C-96 machines with either GE or Vestas machines. | 2017-05-23 | 2017-11-03
N/A | PV-20 Submarine Cable Replacement | NYPA | Replacing a portion of PV-20 that runs underground and underneath Lake Champlain for approximately 1.7 miles between Cumberland Head, NY and Grand Isle, VT does not require an SIS. | 2017-04-10 | 2017-10-02
N/A | 2nd East Garden-Valley | LIPA | Addition of the 2nd EGC-Valley Stream 138kV line does not require an SIS. | 2017-05-04 | 2017-08-01
525 | Western NY Energy Link | NYPA | Remove the new bus-tie breaker at Niagara 115 kV from the proposed project. | 2017-04-04 | 2017-05-09
401 | Caithness II | Caithness | Change a 2x1 F-Class dual fuel combined cycle plant that has a maximum generating capacity of 764 MW in summer (at 85°F, 20 MW station load) and 808 MW in winter (at 10°F, 22 MW station load) to a 1x1 H-class dual-fuel combined-cycle plant that has a maximum potential generating capacity of 599 MW in summer (at 85°F, 16.5 MW station load) and 632 MW in winter (at 10°F, 14.5 MW station load); change the project request for both ERIS and CRIS from 744 MW to 533 MW; and reconfigure both the modified Sills Rd ring bus and the proposed new Sills Rd ring bus as detailed in the attached one-line diagram. | 2017-02-13 | 2017-05-09
393 | Berrians East Repower | NRG | Change of two 1-on-1 combined cycle plant to 3 simple cycle plant (aka replacing two HRSG steam units that are part of the two 1-on-1 combine cycle plant with a GT unit, and there is no change to the original two GT units that are part of the two 1-on-1 combine cycle plant.) | 2017-02-27 | 2017-04-03
422 | Eight Point Wind | NextEra | Change project name, reduce size from 103.4 MW to 101.2 MW, change wind turbines from thirty-two 3.32 MW GE to twenty-seven 3.43 MW GE and five 1.715 MW GE, and other electrical characteristic changes. | 2017-02-24 | 2017-04-03
458 | CH Interconnection | TDI USA Holding | Change the project from a three-terminal project (two points of withdrawal at Hertel and New Scotland and one point of injection at Astoria) to a two-terminal project (one at Hertel and one at Astoria). | 2016-12-06 | 2017-04-03
386 | Grand Isle Inter-Tie Project | NGrid | Redesigned the new proposed 230 kV to add an additional breaker to a bay and reconfigure the connections in the station to add the 3rd 230/115 kV transformer to the new 230 kV substation. | 2016-11-07 | 2017-03-02
N/A | New Buchanan 345kV | Con Edison | Installing a new breaker#12 at Buchanan North 345 kV substation does not require an SIS. | 2017-01-04 | 2017-02-17
N/A | Lines 141 and 142 Reconductoring | NGrid | Reconductoring of the northern 20.5 miles of the Gardenville-Dunkirk 141 and 142 115 kV lines does not require an SIS. | 2016-12-13 | 2017-01-03
467 | Tallgrass Solar | Invenergy | Rescinded the 6/15/16 change request. Keep the inverter as a single GE module of 4MVA. | 2016-11-07 | 2016-12-01
510 | Bayonne Energy Center II | Bayonne Energy Center | Redesign of using one breaker to provide the fault protection for both shunt reactor and capacitor devices, but also retain a circuit switcher for the shunt reactor device. | 2016-10-06 | 2016-11-01
N/A | East River Units 6 & 7 | Con Edison | Increase ERIS for Units 6 and 7 for 10 and 2 MW, respectively, due to better operational optimization of the units. | 2016-09-16 | 2016-11-01
251 | CPV Valley Energy Center | CPV Valley, LLC | Change of COD to 2/15/18. | 2016-07-28 | 2016-09-02
467 | Tallgrass Solar | Invenergy | Change of inverter from a single GE module of 4MVA to a new GE 4x1MVA due to product discontinued. | 2016-06-15 | 2016-08-01
232 & 510 | Bayonne Energy Center I & II | Bayonne Energy Center | Amend the BEC I’s IA to include 110 MVAr shunt reactor, a second 1.75 MW diesel engine, and associated equipment, instead of including such equipment in BEC II. | 2016-06-06 | 2016-07-01
N/A | Lasher Rd 115kV | NGrid | Addition of the Lasher Rd 115kV switch yard does not require an SIS. | 2015-11-25 | 2016-01-04
N/A | Stony Creek Wind Farm | Stony Creek Energy LLC | Application of GE WindBoost on 58 turbines to increase capacity by 0.09 MW per turbine, cancel plans to install a 59th turbine, for a net total increase in ERIS of 3.62 MW. | 2014-06-24 | 2015-07-06
N/A | Sithe Independence Station | Dynegy Marketing and Trade, LLC | Upgrade of combustion turbine components to improve efficiency. May increase maximum summer capability by up to 43 MW, but not above the base ERIS level. | 2015-04-08 | 2015-06-01
N/A | East River Units 10 & 20 | Con Edison | Installation of GE controls to improve efficiency and increase maximum output. Upgrades determined to be non-material subject to increase in capacity not to exceed 10 MW above base ERIS level for each unit. | 2014-10-10 | 2014-12-03
N/A | High Sheldon Wind Farm | Sheldon Energy LLC | Application of GE WindBoost on 47 of 75 turbines to increase capacity from 1.5 MW to 1.62 MW per turbine, a total increase in ERIS of 5.64 MW. | 2014-03-07 | 2014-10-02
201 | Berrians GT | NRG Energy | Change in specifications for the generator lead cable for the Berrians GT & GT II project (Q#201/224) . | 2014-06-16 | 2014-08-01
224 | Berrians GT II | NRG Energy | Change in specifications for the generator lead cable for the Berrians GT & GT II project (Q#201/224) | 2014-06-16 | 2014-08-01
N/A | Black River Gen Facility | ReEnergy Black River LLC | Additional changes to the planned interconnection of the Black River Gen Facility to the Fort Drum Load. | 2014-05-15 | 2014-06-02
N/A | Durkirk Units 2, 3 and 4 | NRG Energy, Inc. | Addition of natural gas as fuel for Units 2, 3 and 4 with an expected completion date of 9/1/2015. | 2014-01-15 | 2014-04-01
N/A | Lewiston Pump Generating Plant | NYPA | Life extension and modernization project to refurbish or replace several plant components. | 2013-04-10 | 2014-01-07
N/A | Black River Gen Facility | ReEnergy Black River LLC | Change of interconnection configuration of the Black River Gen Facility to directly serve the Fort Drum Load. | 2013-10-10 | 2013-12-03
263 | Stony Creek Wind Farm | Stony Creek Wind Farm | Reduction of number of turbines from 59 to 58 and reduction in overall size from 94.4 MW to 92.8 MW. | 2013-08-28 | 2013-09-05
197 | Roaring Brook Wind | PPM Roaring Brook, LLC | Change of I/S Date to 10/2015 and COD to 12/2015. | 2012-10-11 | 2013-02-19
237 | Allegany Wind | Allegany Wind, LLC | Change of COD to 12/2/2013. | 2012-09-19 | 2012-10-09
166 | St. Lawrence Wind Farm | Cape Vincent Wind Power | Change of ownership and combined with Q#207 Cape Vincent Project. (See related entry for Q#207 below.) | 2012-03-22 | 2012-08-07
207 | Cape Vincent | Cape Vincent Wind Power | 1. Q#166 St. Lawrence Wind Farm Project combine with Q#207 Cape Vincent Project. Modifications: Configuration: Both projects connecting into the Rockledge Substation through a single 115 kV line. 2. Change of COD to 12/31/2014. 3. Change of turbines: Change to Siemens 2.3 turbines for both projects. Resultant reduction in size: • Q#166: Change from 79.5 MW to 75.9 MW • Q#207: Change from 210 MW to 209.3 MW Overall: Change from 289.5 MW to 285.2 MW | 2012-03-22 | 2012-08-07
263 | Stony Creek Wind Farm | Stony Creek Wind Farm | Change of COD to September 2013. | 2012-06-07 | 2012-07-12
N/A | Fort Drum Gen Facility | ReEnergy Black River LLC | Change of fuel type. | 2012-06-07 | 2012-07-12
266 | Berrians GT III | NRG Energy | Change of in-service date to June 2016. | 2012-02-24 | 2012-03-07
263 | Stony Creek Wind Farm | Stony Creek Wind Farm | Increase in maximum output for ERIS from 88.5 MW to 94.4 MW. | 2012-01-30 | 2012-02-16
310 | Cricket Valley Energy Center | Cricket Valley Energy Center | Increase in maximum output for ERIS from 1,002 MW Summer/1,115 MW Winter to 1,019.9 MW Summer/ 1,136 MW Winter. | 2012-01-27 | 2012-02-16
251 | CPV Valley Energy Center | CPV Valley, LLC | Increase in maximum output for ERIS from 656 MW Summer/753 MW Winter to 678 MW Summer/784 MW Winter. | 2012-01-13 | 2012-02-16
267 | Winergy NYV Wind Farm | Winergy Power | Change of turbines to Siemens SWT-6.0-154 and extension of COD to Jan 2019 for Stage 1 and Jan 2020 for Stage 2. | 2012-01-12 | 2012-02-16
291 | LI Cable – Phase 1 | Long island Cable | Change of turbines to Siemens SWT-6.0-154 and extension of COD to Jan 2019 for Stage 1 and Jan 2020 for Stage 2. | 2012-01-12 | 2012-02-16
292 | LI Cable – Phase 2a | Long island Cable | Change of turbines to Siemens SWT-6.0-154 and extension of COD to Jan 2019 for Stage 1 and Jan 2020 for Stage 2. | 2012-01-12 | 2012-02-16
169 | Alabama Ledge Wind Farm | Alabama Ledge Wind Farm | Extension of the COD to October 2013. | 2011-06-16 | 2012-02-16
270 | Hounsfield Wind | Wind Development Contract Company | Change of COD to 12/2015. | 2011-12-22 | 2012-01-23
198 | Arkwright Summit Wind | New Grange | Extension of the COD to 9/30/2013. | 2011-12-20 | 2012-01-23
231 | Seneca | Seneca Energy II, LLC | Change of in-service date to 10/1/2012. | 2011-11-30 | 2012-01-23
161&171 | Marble River | Marble River, LLC | Change of turbines to Vestas V112, resultant reduction in size from 216.3 MW to 215.3 MW, and elimination of capacitor banks. | 2011-08-17 | 2012-01-23
182 | Howard Wind | Howard Wind, LLC | Change of COD to December 2011. | 2011-03-03 | 2011-12-05
261 | South Pier Improvement | Astoria Generating Co. | Change of in-service date to January 2015. | 2011-10-17 | 2011-11-16
266 | Berrians GT III | NRG Energy | Reduction in size from 744 MW Summer/789 MW Winter to 250 MW Summer/290 MW Winter, and change of in-service date to June 2014. | 2011-09-12 | 2011-11-16
251 | CPV Valley Energy Center | CPV Valley, LLC | Potential change of in-service date to May 2016. | 2011-08-08 | 2011-11-16
182 | Howard Wind | Howard Wind, LLC | Change machines and reduce size to 57.4 MW. | 2011-03-03 | 2011-08-02
207 | Cape Vincent | Cape Vincent Wind Power | Change of in-service date to 09/2013 and change of COD to 12/2013. | 2011-05-23 | 2011-07-05
166 | St. Lawrence Wind Farm | St. Lawrence Windpower | Change of in-service date to 09/2013 and change of COD to 12/2013. | 2011-05-04 | 2011-07-05
201 | Berrians GT | NRG Energy | Change of in-service date to June 2014. | 2011-04-27 | 2011-07-05
224 | Berrians GT II | NRG Energy | Change of in-service date to June 2014. | 2011-04-27 | 2011-07-05
216 | Nine Mile Point 2 Uprate | Nine Mile Point Nuclear | Change of COD for full capacity uprate to June 2014. Partial capacity uprate (115 MW) expected by June 2012. | 2011-03-28 | 2011-05-04
206 | Hudson Transmission | Hudson Trans. Partners | Change of COD to 5/31/2013. | 2011-03-17 | 2011-04-04
161&171 | Marble River | Marble River, LLC | Change of COD to 10/31/2012. | 2011-01-27 | 2011-02-17
125 | Linden VFT | Linden VFT LLC | Alternative configuration for Goethals ring bus. | 2011-01-21 | 2011-02-17
147 | West Hill Windfarm | West Hill Windpower, LLC | Change of proposed I/S date to 09/2012. | 2010-08-31 | 2010-09-30
119 | Prattsburgh Wind Farm | ECOGEN, LLC | Change of proposed I/S date to 05/2012. | 2010-08-23 | 2010-09-30
157 | NY I Project | BP Wind Energy NA, Inc. | Change of proposed I/S date to 12/15/2013. | 2010-07-17 | 2010-07-29
213 | Ellenburg II Windpark | Noble | Change of COD to 10/10/2011. | 2010-05-12 | 2010-05-26
330 | Upton Solar Farms | BP Solar | Change of inverter vendor to SMA Sunny Central with small reduction in size from 32.0 MW to 31.5 MW. | 2010-04-13 | 2010-05-26
254 | Ripley-Westfield Wind | Ripley-Westfield Wind, LLC | Change to Siemens 2.3 MW turbines. Reduced size from 124.8 MW to 124.2 MW. | 2010-03-29 | 2010-05-26
263 | Stony Creek Wind Farm | Stony Creek Wind Farm | Potential reduction in size from 142.5 MW to 88.5 MW. | 2010-04-21 | 2010-04-29
156 | Fairfield Wind Project | PPM Energy/Atlantic Wind | 1) Change proposed COD to 01/2011; 2) Reduce size from 120 MW to 74 MW; 3) Change of turbines to Gamesa 2.0 MW units; 4) Reduce 34.5 kV collection system and 34.5/115 kV step-up transformer to match reduced project size; 5) Move POI 1.6 miles west, but on same line. | 2009-09-23 | 2010-04-29
198 | Arkwright Summit Wind | New Grange | Developer proposal to change from 6-breaker ring to 3- breaker ring interconnection. | 2009-01-20 | 2010-04-29
234 | Steel Winds II | Steel Winds, LLC | Reduce size from 45 MW to 15 MW. | 2010-01-27 | 2010-02-19
166 | St. Lawrence Wind Farm | Acciona Wind Energy | Potential change of COD to 9/2012. | 2010-01-19 | 2010-02-19
210 | Fortran | Canadian Niagara Power | Change of proposed I/S date to Q4 2012. | 2010-01-13 | 2010-02-19
201 | Berrians GT | NRG Energy | Potential change of machine to GE 7FA CC. | 2009-11-11 | 2009-12-22
224 | Berrians GT II | NRG Energy | Potential changes: reduce size from 256/280 MW to 50/90 MW summer/winter, use excess capacity of Q201 rather than new units. | 2009-11-11 | 2009-12-22
266 | Berrians GT III | NRG Energy | Change of machines to GE 7FA CC. | 2009-11-11 | 2009-12-22
147 | West Hill Windfarm | NY Windpower | Reduce size from 37.5 MW to 31.5 MW, change transformer. (Potential impact of changes on design of SUFs to be evaluated in engineering design studies conducted under the Interconnection Agreement.) | 2009-03-03 | 2009-12-22
119 | Prattsburgh Wind Farm | Ecogen LLC | Change of proposed I/S date to 09/2010. | 2009-02-24 | 2009-12-22
169 | Alabama Ledge Wind Farm | Alabama Ledge Wind Farm | Change of turbines to Suzlon S88, increase size from 79.2 MW to 79.8 MW. | 2009-02-02 | 2009-12-22
198 | Arkwright Summit Wind (formerly New Grange) | New Grange | Change of turbines to Suzlon S88, increase size from 79.2 to 79.8 MW, change proposed I/S date to 2010. (Developer proposal to change from 6-breaker ring to 3- breaker ring yet to be evaluated by NYISO and TO.) | 2009-01-20 | 2009-12-22
216 | Nine Mile Point 2 Uprate | Nine Mile Point Nuclear | Change of proposed I/S date to Q2/2012. | 2009-01-15 | 2009-12-22
186 | Jordanville Wind Project | Iberdrola | Potential change of proposed in-service date to 12/2011. | 2008-12-23 | 2009-12-22
161&171 | Marble River | Marble River, LLC | Change of COD to 10/31/2011. | 2008-12-11 | 2009-12-22
178 | Allegany Windpark | Noble Envir. Power | Change of POI. | 2008-09-30 | 2009-12-22
166 | St. Lawrence Wind Farm | Acciona Windpower | Potential extension of COD to 12/2011. | 2008-08-11 | 2009-12-22
142 | Steuben Wind (formerly Hartsville) | EC&R Northeast, LLC | Change COD to 11/2010. | 2008-05-27 | 2009-12-22
127A | Munnsville | Airtricity | Change I/S date for the last 6 MW of the project to 12/31/2012. | 2008-04-22 | 2009-12-22
152 | Moresville Energy Ctr | Moresville Energy | Potential changes: change turbines to Vestas V90, reduce size from 129 MW to 99 MW. | 2008-03-26 | 2009-12-22
125 | Linden VFT | East Coast Power | Remove NY-side capacitor banks. | 2009-03-30 | 2009-05-29
222 | Ball Hill Windpark | Noble Envir. Power | Reduce size to 90 MW. | 2008-09-29 | 2008-10-14
169 | Alabama Ledge Wind Farm | Alabama Ledge Wind Farm | Change of POI, change turbines, change in size. | 2008-07-11 | 2008-10-14
161&171 | Marble River | Marble River, LLC | Change turbines, change size to 216.3 MW. | 2008-05-01 | 2008-10-14
207 | Cape Vincent | BP Alternative Energy | Change turbines and transformers. | 2008-07-23 | 2008-09-08
222 | Ball Hill Windpark | Noble Envir. Power | Potential reduction in size from 99 MW to 93 MW. | 2008-06-24 | 2008-09-08
178 | Allegany Windpark | Noble Envir. Power | Potential increase in size from 99 MW to 100.5 MW. | 2008-06-23 | 2008-09-08
198 | New Grange Wind Farm | New Grange | Change turbines, reduce size from 79.8 MW to 79.2 MW. | 2008-04-10 | 2008-09-08
166 | St. Lawrence Wind Farm | Acciona Windpower | Potential size reduction from 130 to 79.5 MW. | 2008-06-09 | 2008-06-12
186 | Jordanville Wind Project | Iberdrola | Reduce size from 136 MW to 80 MW, replace 230 kV line with 34.5 kV feeders. | 2008-04-11 | 2008-06-12
166 | St. Lawrence Wind Farm | Acciona Windpower | Change machines. | 2008-03-05 | 2008-06-12
144 | High Sheldon Windfarm | Sheldon Energy | Potential changes: Reduce size from 129 MW to 112.5 MW, elimination of 20 MVAr fixed capacitor due to increased machine VAr cap. | 2008-02-15 | 2008-06-12
234 | Steel Winds II | Steel Winds | Reduce size from 60 MW to 45 MW, change in-service date to 9/30/09 | 2008-03-13 | 2008-04-08
N/A | Niagara Gen Facility | Niagara Generation | Change in fuel and related equipment (no change to generator) | 2008-02-26 | 2008-04-08
177 | Wethersfield Windfield | Noble Envir. Power | Potential size reduction from 127.5 to 126.0 MW. | 2007-12-11 | 2007-12-20
172 | Clinton Windfield | Noble Envir. Power | Potential size reduction from 80.0 to 79.5 MW. | 2007-12-05 | 2007-12-20
175 | Ellenburg Windfield | Noble Envir. Power | Potential size increase from 79.5 to 81.0 MW. | 2007-12-05 | 2007-12-20
212 | Bliss II Windfield | Noble Envir. Power | Potential size reduction from 30.0 to 28.5 MW. | 2007-12-05 | 2007-12-20
201 | Berrians GT | NRG Energy | Change machines (no change in size), change in-service date to 2010/06 | 2007-10-25 | 2007-12-20
224 | Berrians GT II | NRG Energy | Change machines, reduce size from 322.5 MW to 256/280 MW summer/winter. | 2007-10-25 | 2007-12-20
160 | Jericho Rise Wind Farm | Jericho Rise Wind Farm | Change machines, reduce size from 101.2 MW to 79.2 MW, and change POI to Willis 115 kV Substation. | 2007-10-22 | 2007-12-20
232 | Bayonne Energy Center | Bayonne Energy Center | Change machines (no change in size). | 2007-11-21 | 2007-11-28
186 | Jordanville Wind | Community Energy | Reduce size from 150 MW to 136 MW. | 2007-09-18 | 2007-10-03
119 | Prattsburgh Wind Farm | Ecogen LLC | Potential change of turbines. | 2007-09-10 | 2007-10-03
219 | Huntley | NRG Energy | Change machines and increase size from 630 to 661 MW | 2007-08-27 | 2007-10-03
N/A | Jamaica Upgrades | Con Edison | Two new breakers, 30 MVAR Cap, relocate connection of KIAC generator. | 2007-08-21 | 2007-10-03
168 | Dairy Hills Wind Farm | Dairy Hills Wind Farm | Reduce size from 132 MW to 120 MW. | 2007-06-11 | 2007-06-26
182 | Howard Wind | Everpower Global | Change machines and reduce size to 62.5 MW. | 2007-06-11 | 2007-06-26
214 | Chateaugay Windpark | Noble Envir. Power | Increase size from 100 MW to 106.5 MW. | 2007-05-30 | 2007-06-26
147 | West Hill Windfarm | NY Windpower | Change machines and reduce size to 37.5 MW. | 2007-01-19 | 2007-05-03
113 | Prattsburgh Wind Park | Windfarm Prattsburgh | Reduce size from 75 MW to 55.5 MW. | 2006-11-10 | 2007-05-03
135&199 | Canandaigua I & II | UPC Wind Management | Increase size of projects by 0.5 MW each. | 2006-08-30 | 2007-05-03
135&199 | Canandaigua I & II | UPC Wind Management | Change machines. | 2006-07-13 | 2007-05-03
135&199 | Canandaigua I & II | UPC Wind Management | Change in Developer Attachment Facilities. | 2006-03-07 | 2007-05-03
161&171 | Marble River & Clinton County Wind Farms | Marble River, LLC | Increase in combined size of projects from 208 MW to 218 MW. | 2006-08-10 | 2006-08-21
115 | E. Fishkill Transformer | Central Hudson | Request to install for standby operation. | 2006-06-14 | 2006-06-19
141 | Flat Rock Wind Power | Flat Rock Wind Power | Increase size from 300 MW to 321 MW. | 2006-03-30 | 2006-04-10
N/A | Seymour Gas Turbines | NYPA | Change interconnection of existing GTs from Gowanus- Greenwood line to Greenwood bus. | 2006-03-13 | 2006-04-10
N/A | Black River Plant | Black River Generation | Increase plant size by about 7 MW. | 2006-02-06 | 2006-02-22
107 | Caithness Bellport | Caithness Long Island | Increase size from 290 MW to 309.6 MW. | 2004-10-13 | 2004-11-09
N/A | Fitzpatrick Nuclear Unit | Entergy | Increase plant size from 883 MW to 896 MW. | 2004-08-10 | 2004-09-14
141 | Flat Rock Wind Power | Flat Rock Wind Power | Change machines. | 2004-03-03 | 2004-03-09
69 | Empire State Newsprint | Besicorp-Empire Power | Small changes to interconnection plans. | 2003-12-22 | 2004-01-08
N/A | Indian Pt. 2 Nuclear Unit | Entergy | Increase size to 1,042 MW. | 2003-04-02 | 2003-04-30
N/A | East 74th St. GTs | Con Edison | Change interconnection of existing units. | 2003-02-14 | 2003-03-04
N/A | Indian Pt. 3 Nuclear Unit | Entergy | Increase size to 1,042 MW. | 2002-09-12 | 2002-10-17
93 | In-City I (Cross Hudson) | PSEG Power | Reduce size from 1200 MW to 550 MW. | 2002-08-19 | 2002-09-13