## gen_params_CTs_reserves
ns10min_aero | ns10min_f | ns10min_j25 | ns10min_j15
Yes | No | Yes | Yes

## CTs_runtimes_scr
rt_limit_aero_scr | rt_limit_j25_scr | rt_limit_j15_scr | rt_limit_f_scr | rt_limit_ccj_scr
3066 | 3066 | 3066 | 3066 | 8760

## nox_limits
Area | NOx.Limit
C | 200000
F | 200000
G1 | 200000
G2 | 50000
J | 50000
K | 50000

## tech_params_aero
AREA | TECH_PARAMS | HR_SUM_AERO | HR_WIN_AERO | VOC_NG_AERO | VOC_OIL_AERO | CAP_SUM_AERO | CAP_WIN_AERO | MM_COST_AERO | STARTUP_FUEL_AERO | STARTUP_MM_AERO | NOX_NG_SUM_AERO | SO2_NG_SUM_AERO | CO2_NG_SUM_AERO | NOX_NG_WIN_AERO | SO2_NG_WIN_AERO | CO2_NG_WIN_AERO | NOX_OIL_SUM_AERO | SO2_OIL_SUM_AERO | CO2_OIL_SUM_AERO | NOX_OIL_WIN_AERO | SO2_OIL_WIN_AERO | CO2_OIL_WIN_AERO | EFORd_AERO
K | K - Long Island | 9670 | 9450 | 9.74 | 9.81 | 166.6 | 188.2 | 570 | 100 | 0 | 13.653 | 3.5929 | 214341.4013 | 13.3424 | 3.5111 | 209464.9682 | 42.8067 | 2.669 | 285788.535 | 41.8328 | 2.6083 | 279286.6242 | 0.8997
J | J - NYC | 9670 | 9460 | 10.19 | 10.23 | 166.5 | 188.2 | 570 | 100 | 0 | 13.653 | 3.5929 | 214341.4013 | 13.3565 | 3.5149 | 209686.6242 | 42.8067 | 2.669 | 285788.535 | 41.8771 | 2.611 | 279582.1656 | 0.8997
G1 | G - LHV (Dutchess) | 9670 | 9440 | 9.87 | 9.92 | 166.5 | 188.2 | 570 | 100 | 0 | 13.6385 | 3.5891 | 214114.1039 | 13.3141 | 3.5037 | 209021.421 | 42.7613 | 2.6662 | 285485.4719 | 41.7442 | 2.6028 | 278695.228 | 0.8997
G2 | G - LHV (Rockland) | 9670 | 9440 | 9.87 | 9.92 | 166.5 | 188.2 | 570 | 100 | 0 | 13.6385 | 3.5891 | 214114.1039 | 13.3141 | 3.5037 | 209021.421 | 42.7613 | 2.6662 | 285485.4719 | 41.7442 | 2.6028 | 278695.228 | 0.8997
F | F - Capital | 9660 | 9440 | 9.97 | 10.02 | 166.7 | 188.2 | 570 | 100 | 0 | 13.6244 | 3.5854 | 213892.6829 | 13.3141 | 3.5037 | 209021.421 | 42.7171 | 2.6634 | 285190.2439 | 41.7442 | 2.6028 | 278695.228 | 0.8997
C | C - Central | 9670 | 9440 | 10.09 | 10.12 | 166.7 | 188.2 | 570 | 100 | 0 | 13.6385 | 3.5891 | 214114.1039 | 13.3141 | 3.5037 | 209021.421 | 42.7613 | 2.6662 | 285485.4719 | 41.7442 | 2.6028 | 278695.228 | 0.8997

## tech_params_aero_noscr
AREA | TECH_PARAMS | HR_SUM_AERO | HR_WIN_AERO | VOC_NG_AERO | VOC_OIL_AERO | CAP_SUM_AERO | CAP_WIN_AERO | MM_COST_AERO | STARTUP_FUEL_AERO | STARTUP_MM_AERO | NOX_NG_SUM_AERO | SO2_NG_SUM_AERO | CO2_NG_SUM_AERO | NOX_NG_WIN_AERO | SO2_NG_WIN_AERO | CO2_NG_WIN_AERO | NOX_OIL_SUM_AERO | SO2_OIL_SUM_AERO | CO2_OIL_SUM_AERO | NOX_OIL_WIN_AERO | SO2_OIL_WIN_AERO | CO2_OIL_WIN_AERO | EFORd_AERO
K | K - Long Island | 9670 | 9450 | 8.91 | 8.78 | 166.6 | 188.2 | 570 | 100 | 0 | 171.2268 | 3.5929 | 214341.4013 | 167.3312 | 3.5111 | 209464.9682 | 285.3779 | 2.669 | 285788.535 | 278.8854 | 2.6083 | 279286.6242 | 0.8997
J | J - NYC | 9670 | 9460 | 9.36 | 9.2 | 166.5 | 188.2 | 570 | 100 | 0 | 171.2268 | 3.5929 | 214341.4013 | 167.5083 | 3.5149 | 209686.6242 | 285.3779 | 2.669 | 285788.535 | 279.1805 | 2.611 | 279582.1656 | 0.8997
G1 | G - LHV (Dutchess) | 9670 | 9440 | 9.04 | 8.92 | 166.5 | 188.2 | 570 | 100 | 0 | 171.0452 | 3.5891 | 214114.1039 | 166.9769 | 3.5037 | 209021.421 | 285.0753 | 2.6662 | 285485.4719 | 278.2948 | 2.6028 | 278695.228 | 0.8997
G2 | G - LHV (Rockland) | 9670 | 9440 | 9.04 | 8.92 | 166.5 | 188.2 | 570 | 100 | 0 | 171.0452 | 3.5891 | 214114.1039 | 166.9769 | 3.5037 | 209021.421 | 285.0753 | 2.6662 | 285485.4719 | 278.2948 | 2.6028 | 278695.228 | 0.8997
F | F - Capital | 9660 | 9440 | 9.14 | 9.02 | 166.7 | 188.2 | 570 | 100 | 0 | 170.8683 | 3.5854 | 213892.6829 | 166.9769 | 3.5037 | 209021.421 | 284.7805 | 2.6634 | 285190.2439 | 278.2948 | 2.6028 | 278695.228 | 0.8997
C | C - Central | 9670 | 9440 | 9.27 | 9.12 | 166.7 | 188.2 | 570 | 100 | 0 | 171.0452 | 3.5891 | 214114.1039 | 166.9769 | 3.5037 | 209021.421 | 285.0753 | 2.6662 | 285485.4719 | 278.2948 | 2.6028 | 278695.228 | 0.8997

## tech_params_f
AREA | TECH_PARAMS | HR_SUM_F | HR_WIN_F | VOC_NG_F | VOC_OIL_F | CAP_SUM_F | CAP_WIN_F | STARTUP_FUEL_F | STARTUP_MM_F | NOX_NG_SUM_F | SO2_NG_SUM_F | CO2_NG_SUM_F | NOX_NG_WIN_F | SO2_NG_WIN_F | CO2_NG_WIN_F | NOX_OIL_SUM_F | SO2_OIL_SUM_F | CO2_OIL_SUM_F | NOX_OIL_WIN_F | SO2_OIL_WIN_F | CO2_OIL_WIN_F | EFORd_F
K | K - Long Island | 10200 | 9890 | 1.52 | 8.83 | 218 | 227.2 | 325 | 9500 | 17.8701 | 4.6181 | 277086.6142 | 17.327 | 4.4778 | 268665.3543 | 64.7539 | 3.5138 | 369448.8189 | 62.7859 | 3.407 | 358220.4724 | 0.9566
J | J - NYC | 10210 | 9900 | 1.54 | 9.21 | 217.8 | 226.9 | 325 | 9500 | 17.8876 | 4.6226 | 277358.2677 | 17.3445 | 4.4823 | 268937.0079 | 64.8174 | 3.5172 | 369811.0236 | 62.8494 | 3.4104 | 358582.6772 | 0.9566
G1 | G - LHV (Dutchess) | 10200 | 9890 | 1.52 | 8.84 | 217 | 226.5 | 325 | 9500 | 17.8701 | 4.6181 | 274677.1654 | 17.327 | 4.4778 | 266329.1339 | 64.7539 | 3.5138 | 366236.2205 | 62.7859 | 3.407 | 355105.5118 | 0.9566
G2 | G - LHV (Rockland) | 10200 | 9890 | 1.52 | 8.84 | 217 | 226.5 | 325 | 9500 | 17.8701 | 4.6181 | 274677.1654 | 17.327 | 4.4778 | 266329.1339 | 64.7539 | 3.5138 | 366236.2205 | 62.7859 | 3.407 | 355105.5118 | 0.9566
F | F - Capital | 10180 | 9880 | 1.52 | 8.84 | 217 | 225.9 | 325 | 9500 | 17.835 | 4.5089 | 272936.2205 | 17.3094 | 4.376 | 264892.9134 | 64.627 | 3.5069 | 363914.9606 | 62.7224 | 3.4035 | 353190.5512 | 0.9566
C | C - Central | 10180 | 9880 | 1.52 | 8.84 | 215.8 | 224.9 | 325 | 9500 | 17.835 | 4.5089 | 271733.8583 | 17.3094 | 4.376 | 263725.9843 | 64.627 | 3.4067 | 362311.811 | 62.7224 | 3.3063 | 351634.6457 | 0.9566

## tech_params_f_noscr
AREA | TECH_PARAMS | HR_SUM_F | HR_WIN_F | VOC_NG_F | VOC_OIL_F | CAP_SUM_F | CAP_WIN_F | STARTUP_FUEL_F | STARTUP_MM_F | NOX_NG_SUM_F | SO2_NG_SUM_F | CO2_NG_SUM_F | NOX_NG_WIN_F | SO2_NG_WIN_F | CO2_NG_WIN_F | NOX_OIL_SUM_F | SO2_OIL_SUM_F | CO2_OIL_SUM_F | NOX_OIL_WIN_F | SO2_OIL_WIN_F | CO2_OIL_WIN_F | EFORd_F
K | K - Long Island | 10200 | 9890 | 0.95 | 8.04 | 218 | 227.2 | 325 | 9500 | 80.2146 | 4.6181 | 277086.6142 | 77.7767 | 4.4778 | 268665.3543 | 431.6929 | 3.5138 | 369448.8189 | 418.5728 | 3.407 | 358220.4724 | 0.9566
J | J - NYC | 10210 | 9900 | 0.97 | 8.42 | 217.8 | 226.9 | 325 | 9500 | 80.2932 | 4.6226 | 277358.2677 | 77.8553 | 4.4823 | 268937.0079 | 432.1161 | 3.5172 | 369811.0236 | 418.9961 | 3.4104 | 358582.6772 | 0.9566
G1 | G - LHV (Dutchess) | 10200 | 9890 | 0.94 | 8.04 | 217 | 226.5 | 325 | 9500 | 80.2146 | 4.6181 | 274677.1654 | 77.7767 | 4.4778 | 266329.1339 | 431.6929 | 3.5138 | 366236.2205 | 418.5728 | 3.407 | 355105.5118 | 0.9566
G2 | G - LHV (Rockland) | 10200 | 9890 | 0.94 | 8.04 | 217 | 226.5 | 325 | 9500 | 80.2146 | 4.6181 | 274677.1654 | 77.7767 | 4.4778 | 266329.1339 | 431.6929 | 3.5138 | 366236.2205 | 418.5728 | 3.407 | 355105.5118 | 0.9566
F | F - Capital | 10180 | 9880 | 0.94 | 8.04 | 217 | 225.9 | 325 | 9500 | 80.0573 | 4.5089 | 272936.2205 | 77.698 | 4.376 | 264892.9134 | 430.8465 | 3.5069 | 363914.9606 | 418.1496 | 3.4035 | 353190.5512 | 0.9566
C | C - Central | 10180 | 9880 | 0.94 | 8.04 | 215.8 | 224.9 | 325 | 9500 | 80.0573 | 4.5089 | 271733.8583 | 77.698 | 4.376 | 263725.9843 | 430.8465 | 3.4067 | 362311.811 | 418.1496 | 3.3063 | 351634.6457 | 0.9566

## tech_params_j25
AREA | TECH_PARAMS | HR_SUM_J25 | HR_WIN_J25 | VOC_NG_J25 | VOC_OIL_J25 | CAP_SUM_J25 | CAP_WIN_J25 | STARTUP_FUEL_J25 | STARTUP_MM_J25 | NOX_NG_SUM_J25 | SO2_NG_SUM_J25 | CO2_NG_SUM_J25 | NOX_NG_WIN_J25 | SO2_NG_WIN_J25 | CO2_NG_WIN_J25 | NOX_OIL_SUM_J25 | SO2_OIL_SUM_J25 | CO2_OIL_SUM_J25 | NOX_OIL_WIN_J25 | SO2_OIL_WIN_J25 | CO2_OIL_WIN_J25 | EFORd_J25
K | K - Long Island | 9370 | 9300 | 1.39 | 10.93 | 359 | 371.1 | 490 | 26600 | 26.4848 | 6.9222 | 415329.7645 | 26.2869 | 6.8704 | 412226.9807 | 96.3084 | 5.317 | 553773.0193 | 95.5889 | 5.2773 | 549635.9743 | 0.9566
J | J - NYC | 9370 | 9300 | 1.43 | 11.46 | 358.7 | 370.2 | 490 | 26600 | 26.4848 | 6.9222 | 415329.7645 | 26.2869 | 6.8704 | 412226.9807 | 96.3084 | 5.317 | 553773.0193 | 95.5889 | 5.2773 | 549635.9743 | 0.9566
G1 | G - LHV (Dutchess) | 9360 | 9300 | 1.39 | 10.93 | 357.4 | 370.2 | 490 | 26600 | 26.4565 | 6.9148 | 412481.3704 | 26.2869 | 6.8704 | 409837.2591 | 96.2056 | 5.2111 | 549975.1606 | 95.5889 | 5.1777 | 546449.6788 | 0.9566
G2 | G - LHV (Rockland) | 9360 | 9300 | 1.39 | 10.93 | 357.4 | 370.2 | 490 | 26600 | 26.4565 | 6.9148 | 412481.3704 | 26.2869 | 6.8704 | 409837.2591 | 96.2056 | 5.2111 | 549975.1606 | 95.5889 | 5.1777 | 546449.6788 | 0.9566
F | F - Capital | 9350 | 9290 | 1.39 | 10.91 | 357.7 | 369.2 | 490 | 26600 | 26.4283 | 6.8073 | 410839.4004 | 26.2587 | 6.7636 | 408202.9979 | 96.1028 | 5.2056 | 547785.8672 | 95.4861 | 5.1722 | 544270.6638 | 0.9566
C | C - Central | 9350 | 9280 | 1.4 | 10.91 | 355.6 | 367.4 | 490 | 26600 | 26.4283 | 6.8073 | 408436.8308 | 26.2304 | 6.7563 | 405379.015 | 96.1028 | 5.2056 | 544582.4411 | 95.3833 | 5.1666 | 540505.3533 | 0.9566

## tech_params_j25_noscr
AREA | TECH_PARAMS | HR_SUM_J25 | HR_WIN_J25 | VOC_NG_J25 | VOC_OIL_J25 | CAP_SUM_J25 | CAP_WIN_J25 | STARTUP_FUEL_J25 | STARTUP_MM_J25 | NOX_NG_SUM_J25 | SO2_NG_SUM_J25 | CO2_NG_SUM_J25 | NOX_NG_WIN_J25 | SO2_NG_WIN_J25 | CO2_NG_WIN_J25 | NOX_OIL_SUM_J25 | SO2_OIL_SUM_J25 | CO2_OIL_SUM_J25 | NOX_OIL_WIN_J25 | SO2_OIL_WIN_J25 | CO2_OIL_WIN_J25 | EFORd_J25
K | K - Long Island | 9370 | 9300 | 0.93 | 10.23 | 359 | 371.1 | 490 | 26600 | 331.5616 | 6.9222 | 415329.7645 | 329.0846 | 6.8704 | 412226.9807 | 642.0557 | 5.317 | 553773.0193 | 637.2591 | 5.2773 | 549635.9743 | 0.9566
J | J - NYC | 9370 | 9300 | 0.95 | 10.76 | 358.7 | 370.2 | 490 | 26600 | 331.5616 | 6.9222 | 415329.7645 | 329.0846 | 6.8704 | 412226.9807 | 642.0557 | 5.317 | 553773.0193 | 637.2591 | 5.2773 | 549635.9743 | 0.9566
G1 | G - LHV (Dutchess) | 9360 | 9300 | 0.93 | 10.23 | 357.4 | 370.2 | 490 | 26600 | 331.2077 | 6.9148 | 412481.3704 | 329.0846 | 6.8704 | 409837.2591 | 641.3704 | 5.2111 | 549975.1606 | 637.2591 | 5.1777 | 546449.6788 | 0.9566
G2 | G - LHV (Rockland) | 9360 | 9300 | 0.93 | 10.23 | 357.4 | 370.2 | 490 | 26600 | 331.2077 | 6.9148 | 412481.3704 | 329.0846 | 6.8704 | 409837.2591 | 641.3704 | 5.2111 | 549975.1606 | 637.2591 | 5.1777 | 546449.6788 | 0.9566
F | F - Capital | 9350 | 9290 | 0.93 | 10.21 | 357.7 | 369.2 | 490 | 26600 | 330.8539 | 6.8073 | 410839.4004 | 328.7307 | 6.7636 | 408202.9979 | 640.6852 | 5.2056 | 547785.8672 | 636.5739 | 5.1722 | 544270.6638 | 0.9566
C | C - Central | 9350 | 9280 | 0.93 | 10.21 | 355.6 | 367.4 | 490 | 26600 | 330.8539 | 6.8073 | 408436.8308 | 328.3769 | 6.7563 | 405379.015 | 640.6852 | 5.2056 | 544582.4411 | 635.8887 | 5.1666 | 540505.3533 | 0.9566

## tech_params_j15_noscr
AREA | TECH_PARAMS | HR_SUM_J15 | HR_WIN_J15 | VOC_NG_J15 | VOC_OIL_J15 | CAP_SUM_J15 | CAP_WIN_J15 | STARTUP_FUEL_J15 | STARTUP_MM_J15 | NOX_NG_SUM_J15 | SO2_NG_SUM_J15 | CO2_NG_SUM_J15 | NOX_NG_WIN_J15 | SO2_NG_WIN_J15 | CO2_NG_WIN_J15 | NOX_OIL_SUM_J15 | SO2_OIL_SUM_J15 | CO2_OIL_SUM_J15 | NOX_OIL_WIN_J15 | SO2_OIL_WIN_J15 | CO2_OIL_WIN_J15 | EFORd_J15
G1 | G - LHV (Dutchess) | 9390 | 9340 | 0.93 | 10.21 | 340.9 | 350.5 | 490 | 26600 | 189.6096 | 6.4343 | 387262.0985 | 188.6 | 6.4 | 385200 | 643.4261 | 4.9262 | 516349.4647 | 640 | 4.9 | 513600 | 0.9566
F | F - Capital | 9390 | 9320 | 0.93 | 10.21 | 341.2 | 351 | 490 | 26600 | 189.4068 | 6.4274 | 385642.7807 | 187.9949 | 6.3795 | 382767.9144 | 642.738 | 4.921 | 514190.3743 | 637.9465 | 4.8843 | 510357.2193 | 0.9566
C | C - Central | 9370 | 9320 | 0.93 | 10.21 | 338 | 346.1 | 490 | 26600 | 189.2058 | 6.4206 | 382825.6959 | 188.1961 | 6.3863 | 380782.8694 | 642.0557 | 4.8154 | 510434.2612 | 638.6296 | 4.7897 | 507710.4925 | 0.9566

## tech_params_ccj
AREA | TECH_PARAMS | HR_SUM_CCJ | HR_WIN_CCJ | VOC_NG_CCJ | VOC_OIL_CCJ | CAP_SUM_CCJ | CAP_WIN_CCJ | MM_COST_CCJ | STARTUP_FUEL_CCJ | STARTUP_MM_CCJ | NOX_NG_SUM_CCJ | SO2_NG_SUM_CCJ | CO2_NG_SUM_CCJ | NOX_NG_WIN_CCJ | SO2_NG_WIN_CCJ | CO2_NG_WIN_CCJ | NOX_OIL_SUM_CCJ | SO2_OIL_SUM_CCJ | CO2_OIL_SUM_CCJ | NOX_OIL_WIN_CCJ | SO2_OIL_WIN_CCJ | CO2_OIL_WIN_CCJ | EFORd_CCJ | HR_SUM_MIN_CCJ | HR_WIN_MIN_CCJ | NOX_NG_SUM_MIN_CCJ | SO2_NG_SUM_MIN_CCJ | CO2_NG_SUM_MIN_CCJ | NOX_NG_WIN_MIN_CCJ | SO2_NG_WIN_MIN_CCJ | CO2_NG_WIN_MIN_CCJ | NOX_OIL_SUM_MIN_CCJ | SO2_OIL_SUM_MIN_CCJ | CO2_OIL_SUM_MIN_CCJ | NOX_OIL_WIN_MIN_CCJ | SO2_OIL_WIN_MIN_CCJ | CO2_OIL_WIN_MIN_CCJ | CAP_SUM_MIN_CCJ | CAP_WIN_MIN_CCJ
K | K - Long Island | 6370 | 6340 | 1.58 | 2.48 | 517.9 | 547.8 | 600 | 3490 | 26600 | 26.6933 | 6.8756 | 411320 | 26.5676 | 6.8432 | 409382.8571 | 97.0667 | 5.3589 | 558133.3333 | 96.6095 | 5.3337 | 555504.7619 | 0.9708 | 7130 | 7540 | 29.8781 | 7.6959 | 460394.2857 | 31.5962 | 8.1384 | 486868.5714 | 108.6476 | 5.9983 | 624723.8095 | 114.8952 | 6.3432 | 660647.619 | 235.7 | 199.5
J | J - NYC | 6370 | 6350 | 1.61 | 2.84 | 512.3 | 546.7 | 600 | 3490 | 26600 | 26.651 | 6.8647 | 410668.1458 | 26.5674 | 6.8431 | 409378.7639 | 96.9128 | 5.3504 | 557248.8114 | 96.6086 | 5.3336 | 555499.2076 | 0.9708 | 7180 | 7530 | 30.0399 | 7.7376 | 462888.1141 | 31.5043 | 8.1147 | 485452.2979 | 109.2361 | 6.0307 | 628107.7655 | 114.561 | 6.3247 | 658725.832 | 232.3 | 199.3
G1 | G - LHV (Dutchess) | 6360 | 6350 | 1.59 | 2.45 | 514.7 | 544.8 | 600 | 3490 | 26600 | 26.6514 | 6.7638 | 408251.4286 | 26.6095 | 6.7532 | 407609.5238 | 96.9143 | 5.2495 | 554026.6667 | 96.7619 | 5.2413 | 553155.5556 | 0.9708 | 7130 | 7550 | 29.8781 | 7.5827 | 457678.0952 | 31.6381 | 8.0294 | 484638.0952 | 108.6476 | 5.8851 | 621102.2222 | 115.0476 | 6.2317 | 657688.8889 | 234 | 198.7
G2 | G - LHV (Rockland) | 6360 | 6350 | 1.59 | 2.45 | 514.7 | 544.8 | 600 | 3490 | 26600 | 26.6514 | 6.7638 | 408251.4286 | 26.6095 | 6.7532 | 407609.5238 | 96.9143 | 5.2495 | 554026.6667 | 96.7619 | 5.2413 | 553155.5556 | 0.9708 | 7130 | 7550 | 29.8781 | 7.5827 | 457678.0952 | 31.6381 | 8.0294 | 484638.0952 | 108.6476 | 5.8851 | 621102.2222 | 115.0476 | 6.2317 | 657688.8889 | 234 | 198.7
F | F - Capital | 6360 | 6360 | 1.59 | 2.45 | 513.3 | 542.1 | 600 | 3490 | 26600 | 26.6514 | 6.7638 | 407040 | 26.6514 | 6.7638 | 407040 | 96.9143 | 5.2495 | 552411.4286 | 96.9143 | 5.2495 | 552411.4286 | 0.9708 | 7130 | 7560 | 29.8781 | 7.5827 | 456320 | 31.68 | 8.04 | 483840 | 108.6476 | 5.8851 | 619291.4286 | 115.2 | 6.24 | 656640 | 233.4 | 198
C | C - Central | 6370 | 6360 | 1.59 | 2.45 | 509.9 | 539.2 | 600 | 3490 | 26600 | 26.6933 | 6.6733 | 397973.3333 | 26.6514 | 6.6629 | 397348.5714 | 97.0667 | 5.2578 | 550044.4444 | 96.9143 | 5.2495 | 549180.9524 | 0.9708 | 7130 | 7570 | 29.8781 | 7.4695 | 445455.2381 | 31.7219 | 7.9305 | 472944.7619 | 108.6476 | 5.8851 | 615669.8413 | 115.3524 | 6.2483 | 653663.4921 | 232.1 | 197

## Aero_NoSCR_Filtered
[6 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[6 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_Aeroderivative |  |  |  |  | Simple Cycle Aeroderivative Siemens 3x SGT-A65 (No SCR)
|  |  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable |  | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW |  | Summer | MW | 166.6 | 166.5 | 166.5 | 166.5 | 166.7 | 166.7
44 | 52 | Net Plant Output, kW |  | Winter | MW | 188.2 | 188.2 | 188.2 | 188.2 | 188.2 | 188.2
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Summer | Btu/kWh | 9670 | 9670 | 9670 | 9670 | 9660 | 9670
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Winter | Btu/kWh | 9450 | 9460 | 9440 | 9440 | 9440 | 9440
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Heat Rate - ISO Conditions | Btu/kWh | 9420 | 9420 | 9430 | 9430 | 9430 | 9430 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 171.2268 | 171.2268 | 171.0452 | 171.0452 | 170.8683 | 171.0452
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 3.5929 | 3.5929 | 3.5891 | 3.5891 | 3.5854 | 3.5891
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 214341.4013 | 214341.4013 | 214114.1039 | 214114.1039 | 213892.6829 | 214114.1039
Natural Gas Emission Rates - Winter
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 167.3312 | 167.5083 | 166.9769 | 166.9769 | 166.9769 | 166.9769
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 3.5111 | 3.5149 | 3.5037 | 3.5037 | 3.5037 | 3.5037
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 209464.9682 | 209686.6242 | 209021.421 | 209021.421 | 209021.421 | 209021.421
ULSD Emission Rates - Summer
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 285.3779 | 285.3779 | 285.0753 | 285.0753 | 284.7805 | 285.0753
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 2.669 | 2.669 | 2.6662 | 2.6662 | 2.6634 | 2.6662
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 285788.535 | 285788.535 | 285485.4719 | 285485.4719 | 285190.2439 | 285485.4719
ULSD Emission Rates - Winter
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 278.8854 | 279.1805 | 278.2948 | 278.2948 | 278.2948 | 278.2948
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 2.6083 | 2.611 | 2.6028 | 2.6028 | 2.6028 | 2.6028
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 279286.6242 | 279582.1656 | 278695.228 | 278695.228 | 278695.228 | 278695.228
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  |  | Fuel Required per Start (regular start - 21 min. to full load) | MMBtu/Start | 100 | 100 | 100 | 100 | 100 | 100
16 | 16 | Equivalent Forced Outage Rate Demand, % |  | EFORd outage rate | % | 10.03% | 10.03% | 10.03% | 10.03% | 10.03% | 10.03%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 8.91 | 9.36 | 9.04 | 9.04 | 9.14 | 9.27
190 | 193 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 8.78 | 9.2 | 8.92 | 8.92 | 9.02 | 9.12
177 | 180 | Major Maintenance Cost, 2020$/GT-hr or $/engine-hr |  | Maj. Maintenance per Hour | $/hr | 570 | 570 | 570 | 570 | 570 | 570
177 | 180 | Major Maintenance Cost, 2020$/GT-start |  | Maj. Maintenance per Start | $/Start | N/A | N/A | N/A | N/A | N/A | N/A
Updated 7/27/2020

## Aero_SCR_Filtered
[5 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[5 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_Aeroderivative |  |  |  | Simple Cycle Aeroderivative Siemens 3x SGT-A65 (with SCR)
|  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW | Summer | MW | 166.6 | 166.5 | 166.5 | 166.5 | 166.7 | 166.7
44 | 52 | Net Plant Output, kW | Winter | MW | 188.2 | 188.2 | 188.2 | 188.2 | 188.2 | 188.2
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Summer | Btu/kWh | 9670 | 9670 | 9670 | 9670 | 9660 | 9670
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Winter | Btu/kWh | 9450 | 9460 | 9440 | 9440 | 9440 | 9440
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Heat Rate - ISO Conditions | Btu/kWh | 9420 | 9420 | 9430 | 9430 | 9430 | 9430 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 13.653 | 13.653 | 13.6385 | 13.6385 | 13.6244 | 13.6385
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 3.5929 | 3.5929 | 3.5891 | 3.5891 | 3.5854 | 3.5891
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 214341.4013 | 214341.4013 | 214114.1039 | 214114.1039 | 213892.6829 | 214114.1039
Natural Gas Emission Rates - Winter
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 13.3424 | 13.3565 | 13.3141 | 13.3141 | 13.3141 | 13.3141
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 3.5111 | 3.5149 | 3.5037 | 3.5037 | 3.5037 | 3.5037
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 209464.9682 | 209686.6242 | 209021.421 | 209021.421 | 209021.421 | 209021.421
ULSD Emission Rates - Summer
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 42.8067 | 42.8067 | 42.7613 | 42.7613 | 42.7171 | 42.7613
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 2.669 | 2.669 | 2.6662 | 2.6662 | 2.6634 | 2.6662
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 285788.535 | 285788.535 | 285485.4719 | 285485.4719 | 285190.2439 | 285485.4719
ULSD Emission Rates - Winter
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 41.8328 | 41.8771 | 41.7442 | 41.7442 | 41.7442 | 41.7442
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 2.6083 | 2.611 | 2.6028 | 2.6028 | 2.6028 | 2.6028
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 279286.6242 | 279582.1656 | 278695.228 | 278695.228 | 278695.228 | 278695.228
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 21 min. to full load) | MMBtu/Start | 100 | 100 | 100 | 100 | 100 | 100
16 | 16 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 10.03% | 10.03% | 10.03% | 10.03% | 10.03% | 10.03%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - NG Firing | $/MWh | 9.74 | 10.19 | 9.87 | 9.87 | 9.97 | 10.09
190 | 193 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 9.81 | 10.23 | 9.92 | 9.92 | 10.02 | 10.12
177 | 180 | Major Maintenance Cost, 2020$/GT-hr or $/engine-hr | Maj. Maintenance per Hour | $/hr | 570 | 570 | 570 | 570 | 570 | 570
177 | 180 | Major Maintenance Cost, 2020$/GT-start | Maj. Maintenance per Start | $/Start | N/A | N/A | N/A | N/A | N/A | N/A
Updated 7/27/2020

## F-Class_NoSCR_Filtered
[6 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[6 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_F-Class |  |  |  |  | Simple Cycle Frame F-Class: GE 1x 7F.05 (No SCR)
|  |  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable 1 | Variable 2 | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW |  | Summer | MW | 218 | 217.8 | 217 | 217 | 217 | 215.8
44 | 52 | Net Plant Output, kW |  | Winter | MW | 227.2 | 226.9 | 226.5 | 226.5 | 225.9 | 224.9
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Summer | Btu/kWh | 10200 | 10210 | 10200 | 10200 | 10180 | 10180
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Winter | Btu/kWh | 9890 | 9900 | 9890 | 9890 | 9880 | 9880
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Heat Rate - ISO Conditions | Btu/kWh | 10160 | 10160 | 10160 | 10160 | 10160 | 10160 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 80.2146 | 80.2932 | 80.2146 | 80.2146 | 80.0573 | 80.0573
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 4.6181 | 4.6226 | 4.6181 | 4.6181 | 4.5089 | 4.5089
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 277086.6142 | 277358.2677 | 274677.1654 | 274677.1654 | 272936.2205 | 271733.8583
Natural Gas Emission Rates - Winter
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 77.7767 | 77.8553 | 77.7767 | 77.7767 | 77.698 | 77.698
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 4.4778 | 4.4823 | 4.4778 | 4.4778 | 4.376 | 4.376
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 268665.3543 | 268937.0079 | 266329.1339 | 266329.1339 | 264892.9134 | 263725.9843
ULSD Emission Rates - Summer
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 431.6929 | 432.1161 | 431.6929 | 431.6929 | 430.8465 | 430.8465
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 3.5138 | 3.5172 | 3.5138 | 3.5138 | 3.5069 | 3.4067
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 369448.8189 | 369811.0236 | 366236.2205 | 366236.2205 | 363914.9606 | 362311.811
ULSD Emission Rates - Winter
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 418.5728 | 418.9961 | 418.5728 | 418.5728 | 418.1496 | 418.1496
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 3.407 | 3.4104 | 3.407 | 3.407 | 3.4035 | 3.3063
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 358220.4724 | 358582.6772 | 355105.5118 | 355105.5118 | 353190.5512 | 351634.6457
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 325 | 325 | 325 | 325 | 325 | 325
16 | 16 | Equivalent Forced Outage Rate Demand, % |  | EFORd outage rate | % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 0.95 | 0.97 | 0.94 | 0.94 | 0.94 | 0.94
190 | 193 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 8.04 | 8.42 | 8.04 | 8.04 | 8.04 | 8.04
177 | 180 | Major Maintenance Cost, 2020$/GT-start |  | Maj. Maintenance per Start | $/Start | 9500 | 9500 | 9500 | 9500 | 9500 | 9500
Updated 7/27/2020

## F-Class_SCR_Filtered
[5 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[5 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_F-Class |  |  |  | Simple Cycle Frame F-Class: GE 1x 7F.05
|  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW | Summer | MW | 218 | 217.8 | 217 | 217 | 217 | 215.8
44 | 52 | Net Plant Output, kW | Winter | MW | 227.2 | 226.9 | 226.5 | 226.5 | 225.9 | 224.9
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Summer | Btu/kWh | 10200 | 10210 | 10200 | 10200 | 10180 | 10180
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Winter | Btu/kWh | 9890 | 9900 | 9890 | 9890 | 9880 | 9880
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Heat Rate - ISO Conditions | Btu/kWh | 10160 | 10160 | 10160 | 10160 | 10160 | 10160 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 17.8701 | 17.8876 | 17.8701 | 17.8701 | 17.835 | 17.835
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 4.6181 | 4.6226 | 4.6181 | 4.6181 | 4.5089 | 4.5089
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 277086.6142 | 277358.2677 | 274677.1654 | 274677.1654 | 272936.2205 | 271733.8583
Natural Gas Emission Rates - Winter
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 17.327 | 17.3445 | 17.327 | 17.327 | 17.3094 | 17.3094
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 4.4778 | 4.4823 | 4.4778 | 4.4778 | 4.376 | 4.376
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 268665.3543 | 268937.0079 | 266329.1339 | 266329.1339 | 264892.9134 | 263725.9843
ULSD Emission Rates - Summer
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 64.7539 | 64.8174 | 64.7539 | 64.7539 | 64.627 | 64.627
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 3.5138 | 3.5172 | 3.5138 | 3.5138 | 3.5069 | 3.4067
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 369448.8189 | 369811.0236 | 366236.2205 | 366236.2205 | 363914.9606 | 362311.811
ULSD Emission Rates - Winter
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 62.7859 | 62.8494 | 62.7859 | 62.7859 | 62.7224 | 62.7224
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 3.407 | 3.4104 | 3.407 | 3.407 | 3.4035 | 3.3063
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 358220.4724 | 358582.6772 | 355105.5118 | 355105.5118 | 353190.5512 | 351634.6457
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 325 | 325 | 325 | 325 | 325 | 325
16 | 16 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - NG Firing | $/MWh | 1.52 | 1.54 | 1.52 | 1.52 | 1.52 | 1.52
190 | 193 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 8.83 | 9.21 | 8.84 | 8.84 | 8.84 | 8.84
177 | 180 | Major Maintenance Cost, 2020$/GT-start | Maj. Maintenance per Start | $/Start | 9500 | 9500 | 9500 | 9500 | 9500 | 9500
Updated 7/27/2020

## J-Class25ppm_NoSCR_Filtered
[6 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[6 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_J-Class25ppm |  |  |  |  | Simple Cycle Frame J-Class GE 1x HA.02 (25ppm) (No SCR)
|  |  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable |  | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW |  | Summer | MW | 359 | 358.7 | 357.4 | 357.4 | 357.7 | 355.6
44 | 52 | Net Plant Output, kW |  | Winter | MW | 371.1 | 370.2 | 370.2 | 370.2 | 369.2 | 367.4
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Summer | Btu/kWh | 9370 | 9370 | 9360 | 9360 | 9350 | 9350
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Winter | Btu/kWh | 9300 | 9300 | 9300 | 9300 | 9290 | 9280
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Heat Rate - ISO Conditions | Btu/kWh | 9340 | 9340 | 9340 | 9340 | 9340 | 9340 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 331.5616 | 331.5616 | 331.2077 | 331.2077 | 330.8539 | 330.8539
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 6.9222 | 6.9222 | 6.9148 | 6.9148 | 6.8073 | 6.8073
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 415329.7645 | 415329.7645 | 412481.3704 | 412481.3704 | 410839.4004 | 408436.8308
Natural Gas Emission Rates - Winter
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 329.0846 | 329.0846 | 329.0846 | 329.0846 | 328.7307 | 328.3769
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 6.8704 | 6.8704 | 6.8704 | 6.8704 | 6.7636 | 6.7563
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 412226.9807 | 412226.9807 | 409837.2591 | 409837.2591 | 408202.9979 | 405379.015
ULSD Emission Rates - Summer
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 642.0557 | 642.0557 | 641.3704 | 641.3704 | 640.6852 | 640.6852
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 5.317 | 5.317 | 5.2111 | 5.2111 | 5.2056 | 5.2056
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 553773.0193 | 553773.0193 | 549975.1606 | 549975.1606 | 547785.8672 | 544582.4411
ULSD Emission Rates - Winter
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 637.2591 | 637.2591 | 637.2591 | 637.2591 | 636.5739 | 635.8887
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 5.2773 | 5.2773 | 5.1777 | 5.1777 | 5.1722 | 5.1666
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 549635.9743 | 549635.9743 | 546449.6788 | 546449.6788 | 544270.6638 | 540505.3533
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 490 | 490 | 490 | 490 | 490 | 490
16 | 16 | Equivalent Forced Outage Rate Demand, % |  | EFORd outage rate | % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 0.93 | 0.95 | 0.93 | 0.93 | 0.93 | 0.93
190 | 193 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 10.23 | 10.76 | 10.23 | 10.23 | 10.21 | 10.21
177 | 180 | Major Maintenance Cost, 2020$/GT-start |  | Maj. Maintenance per Start | $/Start | 26600 | 26600 | 26600 | 26600 | 26600 | 26600
Updated 7/27/2020

## J-Class25ppm_SCR_Filtered
[5 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[5 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_J-Class25ppm |  |  |  | Simple Cycle Frame J-Class GE 1x HA.02 (25 ppm)
|  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW | Summer | MW | 359 | 358.7 | 357.4 | 357.4 | 357.7 | 355.6
44 | 52 | Net Plant Output, kW | Winter | MW | 371.1 | 370.2 | 370.2 | 370.2 | 369.2 | 367.4
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Summer | Btu/kWh | 9370 | 9370 | 9360 | 9360 | 9350 | 9350
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Plant Heat Rate - Winter | Btu/kWh | 9300 | 9300 | 9300 | 9300 | 9290 | 9280
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) | Net Heat Rate - ISO Conditions | Btu/kWh | 9340 | 9340 | 9340 | 9340 | 9340 | 9340 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 26.4848 | 26.4848 | 26.4565 | 26.4565 | 26.4283 | 26.4283
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 6.9222 | 6.9222 | 6.9148 | 6.9148 | 6.8073 | 6.8073
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 415329.7645 | 415329.7645 | 412481.3704 | 412481.3704 | 410839.4004 | 408436.8308
Natural Gas Emission Rates - Winter
211 | 215 | NOX | NOX Emissions Rate | lb/hr | 26.2869 | 26.2869 | 26.2869 | 26.2869 | 26.2587 | 26.2304
211 | 215 | SO2 | SO2 Emissions Rate | lb/hr | 6.8704 | 6.8704 | 6.8704 | 6.8704 | 6.7636 | 6.7563
211 | 215 | CO2 | CO2 Emissions Rate | lb/hr | 412226.9807 | 412226.9807 | 409837.2591 | 409837.2591 | 408202.9979 | 405379.015
ULSD Emission Rates - Summer
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 96.3084 | 96.3084 | 96.2056 | 96.2056 | 96.1028 | 96.1028
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 5.317 | 5.317 | 5.2111 | 5.2111 | 5.2056 | 5.2056
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 553773.0193 | 553773.0193 | 549975.1606 | 549975.1606 | 547785.8672 | 544582.4411
ULSD Emission Rates - Winter
226 | 229 | NOX | NOX Emissions Rate | lb/hr | 95.5889 | 95.5889 | 95.5889 | 95.5889 | 95.4861 | 95.3833
226 | 229 | SO2 | SO2 Emissions Rate | lb/hr | 5.2773 | 5.2773 | 5.1777 | 5.1777 | 5.1722 | 5.1666
226 | 229 | CO2 | CO2 Emissions Rate | lb/hr | 549635.9743 | 549635.9743 | 546449.6788 | 546449.6788 | 544270.6638 | 540505.3533
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 490 | 490 | 490 | 490 | 490 | 490
16 | 16 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 4.34% | 4.34% | 4.34% | 4.34% | 4.34% | 4.34%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - NG Firing | $/MWh | 1.39 | 1.43 | 1.39 | 1.39 | 1.39 | 1.4
190 | 193 | Total Variable O&M Cost, 2020$/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 10.93 | 11.46 | 10.93 | 10.93 | 10.91 | 10.91
177 | 180 | Major Maintenance Cost, 2020$/GT-start | Maj. Maintenance per Start | $/Start | 26600 | 26600 | 26600 | 26600 | 26600 | 26600
Updated 7/27/2020

## J-Class15ppm_NoSCR_Filtered
[6 empty] | ZONE G - Dutchess | ZONE F | ZONE C
[6 empty] | 4 | 3 | 2
Sheet | Raw_J-Class15ppm |  |  |  |  | Simple Cycle Frame J-Class GE 1x HA.02 (15 ppm) (No SCR)
|  |  |  | Item | Units | G - LHV (Dutchess) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable |  | Performance Values (per unit)
Net Plant Output
32 | 40 | Net Plant Output, kW |  | Summer | MW | 340.9 | 341.2 | 338
44 | 52 | Net Plant Output, kW |  | Winter | MW | 350.5 | 351 | 346.1
Net Plant Heat Rate, Btu/kWh (HHV)
32 | 40 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Summer | Btu/kWh | 9390 | 9390 | 9370
44 | 52 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Plant Heat Rate - Winter | Btu/kWh | 9340 | 9320 | 9320
56 | 64 | Net Plant Heat Rate, Btu/kWh (HHV) |  | Net Heat Rate - ISO Conditions | Btu/kWh | 9340 | 9350 | 9340 | <- Used to scale emissions rates for winter/summer values
Natural Gas Emission Rates - Summer
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 189.6096 | 189.4068 | 189.2058
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 6.4343 | 6.4274 | 6.4206
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 387262.0985 | 385642.7807 | 382825.6959
Natural Gas Emission Rates - Winter
205 | 209 | NOX |  | NOX Emissions Rate | lb/hr | 188.6 | 187.9949 | 188.1961
205 | 209 | SO2 |  | SO2 Emissions Rate | lb/hr | 6.4 | 6.3795 | 6.3863
205 | 209 | CO2 |  | CO2 Emissions Rate | lb/hr | 385200 | 382767.9144 | 380782.8694
ULSD Emission Rates - Summer
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 643.4261 | 642.738 | 642.0557
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 4.9262 | 4.921 | 4.8154
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 516349.4647 | 514190.3743 | 510434.2612
ULSD Emission Rates - Winter
219 | 223 | NOX |  | NOX Emissions Rate | lb/hr | 640 | 637.9465 | 638.6296
219 | 223 | SO2 |  | SO2 Emissions Rate | lb/hr | 4.9 | 4.8843 | 4.7897
219 | 223 | CO2 |  | CO2 Emissions Rate | lb/hr | 513600 | 510357.2193 | 507710.4925
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 490 | 490 | 490
16 | 16 | Equivalent Forced Outage Rate Demand, % |  | EFORd outage rate | % | 4.34% | 4.34% | 4.34%
Variable O&M & Maj. Maintenance Costs (per unit)
184 | 187 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 0.93 | 0.93 | 0.93
190 | 193 | Total Variable O&M Cost, 2020$/MWh | SCR Related Costs, $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 10.21 | 10.21 | 10.21
177 | 180 | Major Maintenance Cost, 2020$/GT-start |  | Maj. Maintenance per Start | $/Start | 26600 | 26600 | 26600
Updated 7/27/2020

## J-Class_CC_Filtered
[5 empty] | ZONE K | ZONE J | ZONE G - Dutchess | ZONE G - Rockland | ZONE F | ZONE C
[5 empty] | 7 | 6 | 4 | 5 | 3 | 2
Sheet | Raw_J-Class_CC |  |  |  | Combined Cycle J-Class Frame 1x1 GE HA.02
|  |  | Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Section Row # Start | Section Row # End | Variable | Performance Values (per unit)
Net Plant Output
101 | 104 | Net Plant Output, kW | Summer | MW | 517.9 | 512.3 | 514.7 | 514.7 | 513.3 | 509.9
67 | 70 | Net Plant Output, kW | Winter | MW | 547.8 | 546.7 | 544.8 | 544.8 | 542.1 | 539.2
Net Plant Output (MECL)
111 | 114 | Net Plant Output, kW | Summer | MW | 235.7 | 232.3 | 234 | 234 | 233.4 | 232.1
77 | 80 | Net Plant Output, kW | Winter | MW | 199.5 | 199.3 | 198.7 | 198.7 | 198 | 197
Net Plant Heat Rate (HHV)
101 | 104 | Net Plant Heat Rate, Btu/kWh (HHV) | Summer | Btu/kWh | 6370 | 6370 | 6360 | 6360 | 6360 | 6370
67 | 70 | Net Plant Heat Rate, Btu/kWh (HHV) | Winter | Btu/kWh | 6340 | 6350 | 6350 | 6350 | 6360 | 6360
82 | 85 | Net Plant Heat Rate, Btu/kWh (HHV) | ISO Conditions | Btu/kWh | 6300 | 6310 | 6300 | 6300 | 6300 | 6300
Net Plant Heat Rate (HHV) (MECL)
111 | 114 | Net Plant Heat Rate, Btu/kWh (HHV) | Summer | Btu/kWh | 7130 | 7180 | 7130 | 7130 | 7130 | 7130
77 | 80 | Net Plant Heat Rate, Btu/kWh (HHV) | Winter | Btu/kWh | 7540 | 7530 | 7550 | 7550 | 7560 | 7570
Natural Gas Emission Rates - Summer
239 | 242 | NOX | NOX Emissions Rate | lb/hr | 26.6933 | 26.651 | 26.6514 | 26.6514 | 26.6514 | 26.6933
239 | 242 | SO2 | SO2 Emissions Rate | lb/hr | 6.8756 | 6.8647 | 6.7638 | 6.7638 | 6.7638 | 6.6733
239 | 242 | CO2 | CO2 Emissions Rate | lb/hr | 411320 | 410668.1458 | 408251.4286 | 408251.4286 | 407040 | 397973.3333
Natural Gas Emission Rates - Winter
239 | 242 | NOX | NOX Emissions Rate | lb/hr | 26.5676 | 26.5674 | 26.6095 | 26.6095 | 26.6514 | 26.6514
239 | 242 | SO2 | SO2 Emissions Rate | lb/hr | 6.8432 | 6.8431 | 6.7532 | 6.7532 | 6.7638 | 6.6629
239 | 242 | CO2 | CO2 Emissions Rate | lb/hr | 409382.8571 | 409378.7639 | 407609.5238 | 407609.5238 | 407040 | 397348.5714
ULSD Emission Rates - Summer
246 | 249 | NOX | NOX Emissions Rate | lb/hr | 97.0667 | 96.9128 | 96.9143 | 96.9143 | 96.9143 | 97.0667
246 | 249 | SO2 | SO2 Emissions Rate | lb/hr | 5.3589 | 5.3504 | 5.2495 | 5.2495 | 5.2495 | 5.2578
246 | 249 | CO2 | CO2 Emissions Rate | lb/hr | 558133.3333 | 557248.8114 | 554026.6667 | 554026.6667 | 552411.4286 | 550044.4444
ULSD Emission Rates - Winter
246 | 249 | NOX | NOX Emissions Rate | lb/hr | 96.6095 | 96.6086 | 96.7619 | 96.7619 | 96.9143 | 96.9143
246 | 249 | SO2 | SO2 Emissions Rate | lb/hr | 5.3337 | 5.3336 | 5.2413 | 5.2413 | 5.2495 | 5.2495
246 | 249 | CO2 | CO2 Emissions Rate | lb/hr | 555504.7619 | 555499.2076 | 553155.5556 | 553155.5556 | 552411.4286 | 549180.9524
Natural Gas Emission Rates - Summer (MECL)
239 | 242 | NOX | NOX Emissions Rate | lb/hr | 29.8781 | 30.0399 | 29.8781 | 29.8781 | 29.8781 | 29.8781
239 | 242 | SO2 | SO2 Emissions Rate | lb/hr | 7.6959 | 7.7376 | 7.5827 | 7.5827 | 7.5827 | 7.4695
239 | 242 | CO2 | CO2 Emissions Rate | lb/hr | 460394.2857 | 462888.1141 | 457678.0952 | 457678.0952 | 456320 | 445455.2381
Natural Gas Emission Rates - Winter (MECL)
239 | 242 | NOX | NOX Emissions Rate | lb/hr | 31.5962 | 31.5043 | 31.6381 | 31.6381 | 31.68 | 31.7219
239 | 242 | SO2 | SO2 Emissions Rate | lb/hr | 8.1384 | 8.1147 | 8.0294 | 8.0294 | 8.04 | 7.9305
239 | 242 | CO2 | CO2 Emissions Rate | lb/hr | 486868.5714 | 485452.2979 | 484638.0952 | 484638.0952 | 483840 | 472944.7619
ULSD Emission Rates - Summer (MECL)
246 | 249 | NOX | NOX Emissions Rate | lb/hr | 108.6476 | 109.2361 | 108.6476 | 108.6476 | 108.6476 | 108.6476
246 | 249 | SO2 | SO2 Emissions Rate | lb/hr | 5.9983 | 6.0307 | 5.8851 | 5.8851 | 5.8851 | 5.8851
246 | 249 | CO2 | CO2 Emissions Rate | lb/hr | 624723.8095 | 628107.7655 | 621102.2222 | 621102.2222 | 619291.4286 | 615669.8413
ULSD Emission Rates - Winter (MECL)
246 | 249 | NOX | NOX Emissions Rate | lb/hr | 114.8952 | 114.561 | 115.0476 | 115.0476 | 115.2 | 115.3524
246 | 249 | SO2 | SO2 Emissions Rate | lb/hr | 6.3432 | 6.3247 | 6.2317 | 6.2317 | 6.24 | 6.2483
246 | 249 | CO2 | CO2 Emissions Rate | lb/hr | 660647.619 | 658725.832 | 657688.8889 | 657688.8889 | 656640 | 653663.4921
Other Performance Values (per unit)
MANUAL UPDATE --> |  |  | Fuel Required per Start (regular start - 30 min. to full load) | MMBtu/Start | 3490 | 3490 | 3490 | 3490 | 3490 | 3490
22 | 22 | Equivalent Forced Outage Rate Demand, % | EFORd outage rate | % | 2.92% | 2.92% | 2.92% | 2.92% | 2.92% | 2.92%
Variable O&M & Maj. Maintenance Costs (per unit)
212 | 215 | Total Variable O&M Cost, 2020 $/MWh | Variable Cost per Hour - NG Firing | $/MWh | 1.58 | 1.61 | 1.59 | 1.59 | 1.59 | 1.59
223 | 226 | Total Variable O&M Cost, 2020 $/MWh | Variable Cost per Hour - ULSD Firing | $/MWh | 2.48 | 2.84 | 2.45 | 2.45 | 2.45 | 2.45
205 | 208 | Major Maintenance Cost, 2020 $/GT-hr | Maj. Maintenance per Hour | $/GT-hr | 600 | 600 | 600 | 600 | 600 | 600
205 | 208 | Major Maintenance Cost, 2020$/GT-start | Maj. Maintenance per Start | $/Start | 26600 | 26600 | 26600 | 26600 | 26600 | 26600
Updated 7/27/2020