## tech_params_lms
AREA | TECH_PARAMS | HR_SUM_LMS | HR_WIN_LMS | VOC_NG_LMS | VOC_OIL_LMS | ICAP_SUM_LMS | ICAP_WIN_LMS | STARTUP_FUEL_LMS | STARTUP_VOM_LMS | NOX_NG_SUM_LMS | SO2_NG_SUM_LMS | CO2_NG_SUM_LMS | NOX_NG_WIN_LMS | SO2_NG_WIN_LMS | CO2_NG_WIN_LMS | NOX_OIL_SUM_LMS | SO2_OIL_SUM_LMS | CO2_OIL_SUM_LMS | NOX_OIL_WIN_LMS | SO2_OIL_WIN_LMS | CO2_OIL_WIN_LMS | EFORd_LMS
K | K - Long Island | 9130 | 8980 | 5.597 | 9.6195 | 101.79 | 109.395 | 61 | 0 | 8.2712 | 2.0446 | 109000 | 8.7431 | 2.1612 | 115000 | 18.9597 | 1.4736 | 160000 | 18.9597 | 1.4736 | 160000 | 0.9783
J | J - NYC | 9200 | 9040 | 5.6203 | 9.6662 | 100.7662 | 108.7125 | 61 | 0 | 8.2507 | 2.0395 | 108000 | 8.7466 | 2.1621 | 115000 | 18.9673 | 1.4741 | 160000 | 18.9673 | 1.4741 | 160000 | 0.9783
G1 | G - LHV (Dutchess) | 9160 | 8990 | 5.4836 | 9.3927 | 100.7175 | 108.9075 | 61 | 0 | 8.2109 | 2.0297 | 108000 | 8.7138 | 2.154 | 115000 | 18.8962 | 1.4686 | 160000 | 18.8962 | 1.4686 | 160000 | 0.9783
G2 | G - LHV (Rockland) | 9170 | 8990 | 5.5036 | 9.4327 | 100.8637 | 108.81 | 61 | 0 | 8.2318 | 2.0348 | 108000 | 8.706 | 2.152 | 114000 | 18.8793 | 1.4673 | 159000 | 18.8793 | 1.4673 | 159000 | 0.9783
F | F - Capital | 9140 | 8980 | 5.3935 | 9.2126 | 101.1075 | 108.615 | 61 | 0 | 8.2247 | 2.0331 | 108000 | 8.6807 | 2.1458 | 114000 | 18.8245 | 1.463 | 159000 | 18.8245 | 1.463 | 159000 | 0.9783
C | C - Central | 9120 | 8980 | 5.3702 | 9.1659 | 100.8053 | 108.1275 | 61 | 0 | 8.1822 | 2.0226 | 108000 | 8.6418 | 2.1362 | 114000 | 18.74 | 1.4565 | 158000 | 18.74 | 1.4565 | 158000 | 0.9783

## tech_params_f
AREA | TECH_PARAMS | HR_SUM_F | HR_WIN_F | VOC_NG_F | VOC_OIL_F | ICAP_SUM_F | ICAP_WIN_F | STARTUP_FUEL_F | STARTUP_VOM_F | NOX_NG_SUM_F | SO2_NG_SUM_F | CO2_NG_SUM_F | NOX_NG_WIN_F | SO2_NG_WIN_F | CO2_NG_WIN_F | NOX_OIL_SUM_F | SO2_OIL_SUM_F | CO2_OIL_SUM_F | NOX_OIL_WIN_F | SO2_OIL_WIN_F | CO2_OIL_WIN_F | EFORd_F
K | K - Long Island | 10180 | 10040 | 0.75639 | 2.57 | 230.278 | 230.278 | 350 | 10900 | 20.8636 | 5.1573 | 274000 | 20.5767 | 5.0864 | 271000 | 44.6214 | 3.468 | 377000 | 44.6214 | 3.468 | 377000 | 0.9783
J | J - NYC | 10230 | 10110 | 0.75639 | 2.57 | 229.017 | 228.726 | 350 | 11000 | 20.8513 | 5.1543 | 274000 | 20.5805 | 5.0873 | 271000 | 44.6297 | 3.4686 | 377000 | 44.6297 | 3.4686 | 377000 | 0.9783
G1 | G - LHV (Dutchess) | 10190 | 10030 | 0.75639 | 2.57 | 230.278 | 230.278 | 350 | 10500 | 20.8841 | 5.1624 | 275000 | 20.5562 | 5.0813 | 270000 | 44.577 | 3.4645 | 376000 | 44.577 | 3.4645 | 376000 | 0.9783
G2 | G - LHV (Rockland) | 10190 | 10030 | 0.75639 | 2.57 | 230.278 | 230.278 | 350 | 10600 | 20.8841 | 5.1624 | 275000 | 20.5562 | 5.0813 | 270000 | 44.577 | 3.4645 | 376000 | 44.577 | 3.4645 | 376000 | 0.9783
F | F - Capital | 10180 | 10020 | 0.75639 | 2.57 | 230.278 | 230.278 | 350 | 10300 | 20.8636 | 5.1573 | 274000 | 20.5357 | 5.0762 | 270000 | 44.5325 | 3.4611 | 376000 | 44.5325 | 3.4611 | 376000 | 0.9783
C | C - Central | 10190 | 10010 | 0.75639 | 2.57 | 230.278 | 230.278 | 350 | 10200 | 20.8841 | 5.1624 | 275000 | 20.5152 | 5.0712 | 270000 | 44.4881 | 3.4576 | 376000 | 44.4881 | 3.4576 | 376000 | 0.9783

## tech_params_w
AREA | TECH_PARAMS | HR_SUM_W | HR_WIN_W | VOC_NG_W | VOC_OIL_W | ICAP_SUM_W | ICAP_WIN_W | STARTUP_FUEL_W | STARTUP_VOM_W | NOX_NG_SUM_W | SO2_NG_SUM_W | CO2_NG_SUM_W | NOX_NG_WIN_W | SO2_NG_WIN_W | CO2_NG_WIN_W | NOX_OIL_SUM_W | SO2_OIL_SUM_W | CO2_OIL_SUM_W | NOX_OIL_WIN_W | SO2_OIL_WIN_W | CO2_OIL_WIN_W | EFORd_W
K | K - Long Island | 8410 | 8350 | 8.1863 | 8.1863 | 16.681 | 16.803 | 7.5 | 0 | 1.97 | 0.30863 | 16400 | 1.97 | 0.30867 | 16400 | 11.22 | 0.21046 | 22900 | 11.22 | 0.21046 | 22900 | 0.99
J | J - NYC | 8410 | 8350 | 8.2444 | 8.2444 | 16.681 | 16.803 | 7.5 | 0 | 1.97 | 0.30863 | 16400 | 1.97 | 0.30867 | 16400 | 11.22 | 0.21046 | 22900 | 11.22 | 0.21046 | 22900 | 0.99
G1 | G - LHV (Dutchess) | 8410 | 8350 | 7.9041 | 7.9041 | 16.681 | 16.803 | 7.5 | 0 | 1.97 | 0.30863 | 16400 | 1.97 | 0.30867 | 16400 | 11.22 | 0.21046 | 22900 | 11.22 | 0.21046 | 22900 | 0.99
G2 | G - LHV (Rockland) | 8410 | 8350 | 7.9539 | 7.9539 | 16.681 | 16.803 | 7.5 | 0 | 1.97 | 0.30863 | 16400 | 1.97 | 0.30867 | 16400 | 11.22 | 0.21046 | 22900 | 11.22 | 0.21046 | 22900 | 0.99
F | F - Capital | 8410 | 8350 | 7.68 | 7.68 | 16.681 | 16.803 | 7.5 | 0 | 1.97 | 0.30863 | 16400 | 1.97 | 0.30867 | 16400 | 11.22 | 0.21046 | 22900 | 11.22 | 0.21046 | 22900 | 0.99
C | C - Central | 8410 | 8350 | 7.6219 | 7.6219 | 16.681 | 16.803 | 7.5 | 0 | 1.97 | 0.30863 | 16400 | 1.97 | 0.30867 | 16400 | 11.22 | 0.21046 | 22900 | 11.22 | 0.21046 | 22900 | 0.99

## tech_params_wg
AREA | TECH_PARAMS | HR_SUM_WG | HR_WIN_WG | VOC_NG_WG | VOC_OIL_WG | ICAP_SUM_WG | ICAP_WIN_WG | STARTUP_FUEL_WG | STARTUP_VOM_WG | NOX_NG_SUM_WG | SO2_NG_SUM_WG | CO2_NG_SUM_WG | NOX_NG_WIN_WG | SO2_NG_WIN_WG | CO2_NG_WIN_WG | NOX_OIL_SUM_WG | SO2_OIL_SUM_WG | CO2_OIL_SUM_WG | NOX_OIL_WIN_WG | SO2_OIL_WIN_WG | CO2_OIL_WIN_WG | EFORd_WG
K | K - Long Island | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
J | J - NYC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
G1 | G - LHV (Dutchess) | 8330 | 8280 | 7.9041 | 0 | 18.4 | 18.5 | 7.5 | 0 | 1.3 | 0.3372 | 17900 | 1.3 | 0.337 | 17900 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99
G2 | G - LHV (Rockland) | 8330 | 8280 | 7.9539 | 0 | 18.4 | 18.5 | 7.5 | 0 | 1.3 | 0.3372 | 17900 | 1.3 | 0.337 | 17900 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99
F | F - Capital | 8330 | 8280 | 7.68 | 0 | 18.4 | 18.5 | 7.5 | 0 | 1.3 | 0.3372 | 17900 | 1.3 | 0.337 | 17900 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99
C | C - Central | 8330 | 8280 | 7.6219 | 0 | 18.4 | 18.5 | 7.5 | 0 | 1.3 | 0.3372 | 17900 | 1.3 | 0.337 | 17900 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99

## tech_params_h
AREA | TECH_PARAMS | HR_SUM_H | HR_WIN_H | VOC_NG_H | VOC_OIL_H | ICAP_SUM_H | ICAP_WIN_H | STARTUP_FUEL_H | STARTUP_VOM_H | NOX_NG_SUM_H | SO2_NG_SUM_H | CO2_NG_SUM_H | NOX_NG_WIN_H | SO2_NG_WIN_H | CO2_NG_WIN_H | NOX_OIL_SUM_H | SO2_OIL_SUM_H | CO2_OIL_SUM_H | NOX_OIL_WIN_H | SO2_OIL_WIN_H | CO2_OIL_WIN_H | EFORd_H
K | K - Long Island | 9360 | 9200 | 1.02 | 4.92 | 327.763 | 340.664 | 391 | 16800 | 27.304 | 6.7493 | 359000 | 27.8936 | 6.895 | 367000 | 60.4883 | 4.7012 | 511000 | 60.4883 | 4.7012 | 511000 | 0.9783
J | J - NYC | 9410 | 9260 | 1.02 | 4.92 | 326.017 | 338.336 | 391 | 16900 | 27.3036 | 6.7492 | 359000 | 27.8836 | 6.8926 | 367000 | 60.4667 | 4.6995 | 511000 | 60.4667 | 4.6995 | 511000 | 0.9783
G1 | G - LHV (Dutchess) | 9360 | 9190 | 1.02 | 4.92 | 325.92 | 339.306 | 391 | 16200 | 27.1504 | 6.7113 | 357000 | 27.7522 | 6.8601 | 365000 | 60.1817 | 4.6773 | 508000 | 60.1817 | 4.6773 | 508000 | 0.9783
G2 | G - LHV (Rockland) | 9360 | 9190 | 1.02 | 4.92 | 325.92 | 339.306 | 391 | 16300 | 27.1504 | 6.7113 | 357000 | 27.7522 | 6.8601 | 365000 | 60.1817 | 4.6773 | 508000 | 60.1817 | 4.6773 | 508000 | 0.9783
F | F - Capital | 9350 | 9180 | 1.02 | 4.92 | 325.047 | 338.53 | 391 | 15800 | 27.0488 | 6.6862 | 356000 | 27.6586 | 6.837 | 364000 | 59.9787 | 4.6616 | 507000 | 59.9787 | 4.6616 | 507000 | 0.9783
C | C - Central | 9350 | 9180 | 1.02 | 4.92 | 323.398 | 336.784 | 391 | 15700 | 26.9116 | 6.6523 | 354000 | 27.5159 | 6.8017 | 362000 | 59.6694 | 4.6375 | 504000 | 59.6694 | 4.6375 | 504000 | 0.9783

## tech_params_ccf
AREA | TECH_PARAMS | HR_SUM_CCF | HR_WIN_CCF | VOC_NG_CCF | VOC_OIL_CCF | ICAP_SUM_CCF | ICAP_WIN_CCF | STARTUP_FUEL_CCF | STARTUP_VOM_CCF | NOX_NG_SUM_CCF | SO2_NG_SUM_CCF | CO2_NG_SUM_CCF | NOX_NG_WIN_CCF | SO2_NG_WIN_CCF | CO2_NG_WIN_CCF | NOX_OIL_SUM_CCF | SO2_OIL_SUM_CCF | CO2_OIL_SUM_CCF | NOX_OIL_WIN_CCF | SO2_OIL_WIN_CCF | CO2_OIL_WIN_CCF | EFORd_CCF | HR_SUM_MIN_CCF | HR_WIN_MIN_CCF | ICAP_SUM_MIN_CCF | ICAP_WIN_MIN_CCF
K | K - Long Island | 6820 | 6760 | 1.0569 | 1.4053 | 343.9946 | 342.6198 | 3100 | 10900 | 16.6569 | 5.1613 | 274000 | 16.4444 | 5.0954 | 271000 | 44.7009 | 3.4742 | 378000 | 44.7009 | 3.4742 | 378000 | 0.97 | 8280 | 8330 | 164.7619 | 163.1198
J | J - NYC | 6880 | 6780 | 1.0653 | 1.4137 | 341.8342 | 341.3432 | 3100 | 11000 | 16.6979 | 5.174 | 275000 | 16.4316 | 5.0915 | 271000 | 44.6661 | 3.4715 | 377000 | 44.6661 | 3.4715 | 377000 | 0.97 | 8370 | 8360 | 162.9085 | 162.5605
G1 | G - LHV (Dutchess) | 6840 | 6760 | 1.0161 | 1.3645 | 341.1468 | 342.0306 | 3100 | 10500 | 16.5675 | 5.1336 | 273000 | 16.4161 | 5.0867 | 271000 | 44.624 | 3.4682 | 377000 | 44.624 | 3.4682 | 377000 | 0.97 | 8300 | 8340 | 163.9827 | 162.6321
G2 | G - LHV (Rockland) | 6830 | 6760 | 1.0233 | 1.3717 | 341.6378 | 341.9324 | 3100 | 10600 | 16.567 | 5.1334 | 273000 | 16.4114 | 5.0852 | 270000 | 44.6112 | 3.4672 | 377000 | 44.6112 | 3.4672 | 377000 | 0.97 | 8290 | 8350 | 164.2744 | 162.5339
F | F - Capital | 6820 | 6770 | 0.98367 | 1.3321 | 342.0306 | 341.3432 | 3100 | 10300 | 16.5618 | 5.1318 | 273000 | 16.4073 | 5.084 | 270000 | 44.6002 | 3.4663 | 377000 | 44.6002 | 3.4663 | 377000 | 0.97 | 8270 | 8360 | 164.2751 | 162.0464
C | C - Central | 6790 | 6770 | 1.251 | 1.5994 | 342.1288 | 341.0486 | 3100 | 10200 | 16.4937 | 5.1107 | 272000 | 16.3932 | 5.0796 | 270000 | 44.5618 | 3.4633 | 376000 | 44.5618 | 3.4633 | 376000 | 0.97 | 8210 | 8290 | 165.1533 | 163.1084

## tech_params_cch
AREA | TECH_PARAMS | HR_SUM_CCH | HR_WIN_CCH | VOC_NG_CCH | VOC_OIL_CCH | ICAP_SUM_CCH | ICAP_WIN_CCH | STARTUP_FUEL_CCH | STARTUP_VOM_CCH | NOX_NG_SUM_CCH | SO2_NG_SUM_CCH | CO2_NG_SUM_CCH | NOX_NG_WIN_CCH | SO2_NG_WIN_CCH | CO2_NG_WIN_CCH | NOX_OIL_SUM_CCH | SO2_OIL_SUM_CCH | CO2_OIL_SUM_CCH | NOX_OIL_WIN_CCH | SO2_OIL_WIN_CCH | CO2_OIL_WIN_CCH | EFORd_CCH | HR_SUM_MIN_CCH | HR_WIN_MIN_CCH | ICAP_SUM_MIN_CCH | ICAP_WIN_MIN_CCH
K | K - Long Island | 6660 | 6610 | 1.0237 | 1.2524 | 406.9408 | 434.6332 | 4000 | 16500 | 19.2426 | 5.9625 | 317000 | 20.3978 | 6.3204 | 336000 | 55.4475 | 4.3094 | 468000 | 55.4475 | 4.3094 | 468000 | 0.97 | 7530 | 7490 | 221.2448 | 234.2219
J | J - NYC | 6720 | 6640 | 1.0306 | 1.2593 | 404.093 | 431.1962 | 4000 | 16600 | 19.2801 | 5.9741 | 318000 | 20.3283 | 6.2989 | 335000 | 55.2587 | 4.2947 | 467000 | 55.2587 | 4.2947 | 467000 | 0.97 | 7600 | 7520 | 219.3629 | 232.4073
G1 | G - LHV (Dutchess) | 6670 | 6620 | 0.99005 | 1.2188 | 403.7984 | 433.8476 | 4000 | 15900 | 19.1227 | 5.9253 | 315000 | 20.3917 | 6.3186 | 336000 | 55.431 | 4.3081 | 468000 | 55.431 | 4.3081 | 468000 | 0.97 | 7560 | 7490 | 219.0033 | 233.6372
G2 | G - LHV (Rockland) | 6670 | 6620 | 0.99598 | 1.2247 | 404.093 | 434.1422 | 4000 | 16000 | 19.1366 | 5.9297 | 315000 | 20.4056 | 6.3228 | 336000 | 55.4686 | 4.311 | 468000 | 55.4686 | 4.311 | 468000 | 0.97 | 7550 | 7500 | 219.3931 | 233.8321
F | F - Capital | 6660 | 6630 | 0.96334 | 1.1921 | 404.093 | 434.2404 | 4000 | 15500 | 19.1079 | 5.9208 | 315000 | 20.441 | 6.3338 | 337000 | 55.565 | 4.3185 | 469000 | 55.565 | 4.3185 | 469000 | 0.97 | 7540 | 7470 | 219.3931 | 237.7313
C | C - Central | 6570 | 6550 | 1.2202 | 1.4336 | 408.2174 | 437.5792 | 4000 | 15400 | 19.0421 | 5.9004 | 314000 | 20.3496 | 6.3055 | 335000 | 55.3166 | 4.2992 | 467000 | 55.3166 | 4.2992 | 467000 | 0.97 | 7400 | 7320 | 222.8032 | 238.5095

## 2x0 LMS100PA+
2x0 LMS100PA+ Dual Fuel All Zones
Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Performance Values (per unit)
Net Plant Capacity, Degraded
Net Plant Capacity - Summer | MW | 101.79 | 100.7662 | 100.7175 | 100.8637 | 101.1075 | 100.8053
Net Plant Capacity - Winter | MW | 109.395 | 108.7125 | 108.9075 | 108.81 | 108.615 | 108.1275
DMNC Summer | MW | 96.7687 | 96.0862 | 96.3787 | 96.7687 | 95.7938 | 95.7938
DMNC Winter | MW | 109.395 | 108.615 | 108.9075 | 108.9075 | 108.42 | 107.835
ICAP | MW | 94.4492 | 93.793 | 93.8974 | 93.8974 | 93.4888 | 92.9477
Net Plant Heat Rate (HHV basis), Degraded
Net Plant Heat Rate - Summer | Btu/kWh | 9130 | 9200 | 9160 | 9170 | 9140 | 9120
Net Plant Heat Rate - Winter | Btu/kWh | 8980 | 9040 | 8990 | 8990 | 8980 | 8980
Net Plant Heat Rate - DMNC Summer | Btu/kWh | 9240 | 9280 | 9210 | 9220 | 9230 | 9210
Net Plant Heat Rate - DMNC Winter | Btu/kWh | 8980 | 9040 | 8990 | 8990 | 8990 | 8990
Net Plant Heat Rate - ICAP | Btu/kWh | 9260 | 9320 | 9260 | 9260 | 9260 | 9260
Natural Gas Emission Rates - Summer
NOX Emissions Rate | lb/hr | 8.2712 | 8.2507 | 8.2109 | 8.2318 | 8.2247 | 8.1822
SO2 Emissions Rate | lb/hr | 2.0446 | 2.0395 | 2.0297 | 2.0348 | 2.0331 | 2.0226
CO2 Emissions Rate | lb/hr | 109000 | 108000 | 108000 | 108000 | 108000 | 108000
Natural Gas Emission Rates - Winter
NOX Emissions Rate | lb/hr | 8.7431 | 8.7466 | 8.7138 | 8.706 | 8.6807 | 8.6418
SO2 Emissions Rate | lb/hr | 2.1612 | 2.1621 | 2.154 | 2.152 | 2.1458 | 2.1362
CO2 Emissions Rate | lb/hr | 115000 | 115000 | 115000 | 114000 | 114000 | 114000
ULSD Emission Rates - Winter
NOX Emissions Rate | lb/hr | 18.9597 | 18.9673 | 18.8962 | 18.8793 | 18.8245 | 18.74
SO2 Emissions Rate | lb/hr | 1.4736 | 1.4741 | 1.4686 | 1.4673 | 1.463 | 1.4565
CO2 Emissions Rate | lb/hr | 160000 | 160000 | 160000 | 159000 | 159000 | 158000
Other Performance Values (per unit)
Fuel Required per Start | MMBtu/Start | 61 | 61 | 61 | 61 | 61 | 61
Can startup in time for 10-minute non-spinning reserve? | Yes/No | Yes | Yes | Yes | Yes | Yes | Yes
EFORd outage rate | % | 2.17% | 2.17% | 2.17% | 2.17% | 2.17% | 2.17%
Fixed and Variable O&M Costs (per unit)
Variable Cost per Hour - NG Firing | $/MWh | 5.597 | 5.6203 | 5.4836 | 5.5036 | 5.3935 | 5.3702
Variable Cost per Hour - ULSD Firing | $/MWh | 9.6195 | 9.6662 | 9.3927 | 9.4327 | 9.2126 | 9.1659
Variable Cost per Start | $/Start | na | na | na | na | na | na
Updated 8/09/2016

## 1x0 5000F5
1x0 Siemens 5000F5, Dual Fuel All Zones
Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Performance Values (per unit) |  | note: Siemens 5000F5 is designed to minimize ambient temperature impact on output; machine reaches mechanical limit at 59F- lower ambient temerature does not increase output
Net Plant Capacity, Degraded
Net Plant Capacity - Summer | MW | 230.278 | 229.017 | 230.278 | 230.278 | 230.278 | 230.278
Net Plant Capacity - Winter | MW | 230.278 | 228.726 | 230.278 | 230.278 | 230.278 | 230.278
DMNC Summer | MW | 224.943 | 226.883 | 226.786 | 226.107 | 224.555 | 224.361
DMNC Winter | MW | 230.278 | 228.726 | 230.278 | 230.278 | 230.278 | 230.278
ICAP | MW | 219.123 | 217.571 | 217.959 | 217.959 | 216.989 | 215.825
Net Plant Heat Rate (HHV basis), Degraded
Net Plant Heat Rate - Summer | Btu/kWh | 10180 | 10230 | 10190 | 10190 | 10180 | 10190
Net Plant Heat Rate - Winter | Btu/kWh | 10040 | 10110 | 10030 | 10030 | 10020 | 10010
Net Plant Heat Rate - DMNC Summer | Btu/kWh | 10280 | 10310 | 10240 | 10250 | 10260 | 10250
Net Plant Heat Rate - DMNC Winter | Btu/kWh | 10050 | 10110 | 10040 | 10040 | 10040 | 10030
Net Plant Heat Rate - ICAP | Btu/kWh | 10310 | 10380 | 10300 | 10300 | 10310 | 10310
Natural Gas Emission Rates - Summer
NOX Emissions Rate | lb/hr | 20.8636 | 20.8513 | 20.8841 | 20.8841 | 20.8636 | 20.8841
SO2 Emissions Rate | lb/hr | 5.1573 | 5.1543 | 5.1624 | 5.1624 | 5.1573 | 5.1624
CO2 Emissions Rate | lb/hr | 274000 | 274000 | 275000 | 275000 | 274000 | 275000
Natural Gas Emission Rates - Winter
NOX Emissions Rate | lb/hr | 20.5767 | 20.5805 | 20.5562 | 20.5562 | 20.5357 | 20.5152
SO2 Emissions Rate | lb/hr | 5.0864 | 5.0873 | 5.0813 | 5.0813 | 5.0762 | 5.0712
CO2 Emissions Rate | lb/hr | 271000 | 271000 | 270000 | 270000 | 270000 | 270000
ULSD Emission Rates - Winter
NOX Emissions Rate | lb/hr | 44.6214 | 44.6297 | 44.577 | 44.577 | 44.5325 | 44.4881
SO2 Emissions Rate | lb/hr | 3.468 | 3.4686 | 3.4645 | 3.4645 | 3.4611 | 3.4576
CO2 Emissions Rate | lb/hr | 377000 | 377000 | 376000 | 376000 | 376000 | 376000
Other Performance Values (per unit)
Fuel Required per Start (fast start - 11 min. full load) | MMBtu/Start | 160 | 160 | 160 | 160 | 160 | 160
Fuel Required per Start (regular start - 28 min. to full load) | MMBtu/Start | 350 | 350 | 350 | 350 | 350 | 350
Can startup in time for 10-minute non-spinning reserve? | Yes/No | No | No | No | No | No | No
EFORd outage rate | % | 2.17% | 2.17% | 2.17% | 2.17% | 2.17% | 2.17%
Fixed and Variable O&M Costs (per unit)
Variable Cost per Hour - NG Firing | $/MWh | 0.75639 | 0.75639 | 0.75639 | 0.75639 | 0.75639 | 0.75639
Variable Cost per Hour - ULSD Firing | $/MWh | 2.57 | 2.57 | 2.57 | 2.57 | 2.57 | 2.57
Variable Cost per Start | $/Start | 10900 | 11000 | 10500 | 10600 | 10300 | 10200
Updated 8/09/2016

## 12x0 Wartsila 18V50DF
12x0 Wartsila 18V50DF, Dual Fuel All Zones
Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Performance Values (per unit)
Net Plant Capacity (no degradation)
Net Plant Capacity - Summer | MW | 16.681 | 16.681 | 16.681 | 16.681 | 16.681 | 16.681
Net Plant Capacity - Winter | MW | 16.803 | 16.803 | 16.803 | 16.803 | 16.803 | 16.803
DMNC Summer | MW | 16.681 | 16.681 | 16.681 | 16.681 | 16.681 | 16.681
DMNC Winter | MW | 16.803 | 16.803 | 16.803 | 16.803 | 16.803 | 16.803
ICAP | MW | 16.681 | 16.681 | 16.681 | 16.681 | 16.681 | 16.681
Net Plant Heat Rate (HHV basis), Degraded
Net Plant Heat Rate - Summer | Btu/kWh | 8410 | 8410 | 8410 | 8410 | 8410 | 8410
Net Plant Heat Rate - Winter | Btu/kWh | 8350 | 8350 | 8350 | 8350 | 8350 | 8350
Net Plant Heat Rate - DMNC Summer | Btu/kWh | 8410 | 8410 | 8410 | 8410 | 8410 | 8410
Net Plant Heat Rate - DMNC Winter | Btu/kWh | 8350 | 8350 | 8350 | 8350 | 8350 | 8350
Net Plant Heat Rate - ICAP | Btu/kWh | 8380 | 8380 | 8380 | 8380 | 8380 | 8380
Natural Gas Emission Rates - Summer
NOX Emissions Rate | lb/hr | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97
SO2 Emissions Rate | lb/hr | 0.30863 | 0.30863 | 0.30863 | 0.30863 | 0.30863 | 0.30863
CO2 Emissions Rate | lb/hr | 16400 | 16400 | 16400 | 16400 | 16400 | 16400
Natural Gas Emission Rates - Winter
NOX Emissions Rate | lb/hr | 1.97 | 1.97 | 1.97 | 1.97 | 1.97 | 1.97
SO2 Emissions Rate | lb/hr | 0.30867 | 0.30867 | 0.30867 | 0.30867 | 0.30867 | 0.30867
CO2 Emissions Rate | lb/hr | 16400 | 16400 | 16400 | 16400 | 16400 | 16400
ULSD Emission Rates - Winter
NOX Emissions Rate | lb/hr | 11.22 | 11.22 | 11.22 | 11.22 | 11.22 | 11.22
SO2 Emissions Rate | lb/hr | 0.21046 | 0.21046 | 0.21046 | 0.21046 | 0.21046 | 0.21046
CO2 Emissions Rate | lb/hr | 22900 | 22900 | 22900 | 22900 | 22900 | 22900
Other Performance Values (per unit)
Fuel Required per Start | MMBtu/Start | 7.5 | 7.5 | 7.5 | 7.5 | 7.5 | 7.5
Can startup in time for 10-minute non-spinning reserve? | Yes/No | Yes | Yes | Yes | Yes | Yes | Yes
EFORd outage rate | % | 1% | 1% | 1% | 1% | 1% | 1%
Fixed and Variable O&M Costs (per unit)
Variable Cost per Hour - NG Firing | $/MWh | 8.1863 | 8.2444 | 7.9041 | 7.9539 | 7.68 | 7.6219
Variable Cost per Hour - ULSD Firing | $/MWh | 8.1863 | 8.2444 | 7.9041 | 7.9539 | 7.68 | 7.6219
Variable Cost per Start | $/Start | na | na | na | na | na | na
Updated 8/09/2016

## 12x0 Wartsila 18V50SG
12x0 Wartsila 18V50SG, Gas Only
Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Performance Values (per unit)
Net Plant Capacity (no degradation)
Net Plant Capacity - Summer | MW |  |  | 18.4 | 18.4 | 18.4 | 18.4
Net Plant Capacity - Winter | MW |  |  | 18.5 | 18.5 | 18.5 | 18.5
DMNC Summer | MW |  |  | 18.4 | 18.4 | 18.4 | 18.4
DMNC Winter | MW |  |  | 18.5 | 18.5 | 18.5 | 18.5
ICAP | MW |  |  | 18.4 | 18.4 | 18.4 | 18.4
Net Plant Heat Rate (HHV basis), Degraded
Net Plant Heat Rate - Summer | Btu/kWh |  |  | 8330 | 8330 | 8330 | 8330
Net Plant Heat Rate - Winter | Btu/kWh |  |  | 8280 | 8280 | 8280 | 8280
Net Plant Heat Rate - DMNC Summer | Btu/kWh |  |  | 8330 | 8330 | 8330 | 8330
Net Plant Heat Rate - DMNC Winter | Btu/kWh |  |  | 8280 | 8280 | 8280 | 8280
Net Plant Heat Rate - ICAP | Btu/kWh |  |  | 8330 | 8330 | 8330 | 8330
Natural Gas Emission Rates - Summer
NOX Emissions Rate | lb/hr |  |  | 1.3 | 1.3 | 1.3 | 1.3
SO2 Emissions Rate | lb/hr |  |  | 0.3372 | 0.3372 | 0.3372 | 0.3372
CO2 Emissions Rate | lb/hr |  |  | 17900 | 17900 | 17900 | 17900
Natural Gas Emission Rates - Winter
NOX Emissions Rate | lb/hr |  |  | 1.3 | 1.3 | 1.3 | 1.3
SO2 Emissions Rate | lb/hr |  |  | 0.337 | 0.337 | 0.337 | 0.337
CO2 Emissions Rate | lb/hr |  |  | 17900 | 17900 | 17900 | 17900
ULSD Emission Rates - Winter
NOX Emissions Rate | lb/hr
SO2 Emissions Rate | lb/hr
CO2 Emissions Rate | lb/hr
Other Performance Values (per unit)
Fuel Required per Start | MMBtu/Start |  |  | 7.5 | 7.5 | 7.5 | 7.5
Can startup in time for 10-minute non-spinning reserve? | Yes/No |  |  | Yes | Yes | Yes | Yes
EFORd outage rate | % |  |  | 1% | 1% | 1% | 1%
Fixed and Variable O&M Costs (per unit)
Variable Cost per Hour - NG Firing | $/MWh |  |  | 7.9041 | 7.9539 | 7.68 | 7.6219
Variable Cost per Hour - ULSD Firing | $/MWh
Variable Cost per Start | $/Start | na | na | na | na | na | na
Updated 8/09/2016

## 1x0 7HA02
1x0 GE, 7HA02 Dual Fuel All Zones
Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Performance Values (per unit)
Net Plant Capacity, Degraded
Net Plant Capacity - Summer | MW | 327.763 | 326.017 | 325.92 | 325.92 | 325.047 | 323.398
Net Plant Capacity - Winter | MW | 340.664 | 338.336 | 339.306 | 339.306 | 338.53 | 336.784
DMNC Summer | MW | 325.532 | 314.183 | 318.354 | 322.234 | 320.585 | 321.846
DMNC Winter | MW | 343.574 | 340.567 | 342.216 | 342.313 | 341.149 | 339.306
ICAP | MW | 318.0023 | 316.3354 | 316.3397 | 316.3397 | 315.1153 | 313.4955
Net Plant Heat Rate (HHV basis), Degraded
Net Plant Heat Rate - Summer | Btu/kWh | 9360 | 9410 | 9360 | 9360 | 9350 | 9350
Net Plant Heat Rate - Winter | Btu/kWh | 9200 | 9260 | 9190 | 9190 | 9180 | 9180
Net Plant Heat Rate - DMNC Summer | Btu/kWh | 9420 | 9450 | 9400 | 9400 | 9410 | 9390
Net Plant Heat Rate - DMNC Winter | Btu/kWh | 9140 | 9210 | 9140 | 9130 | 9130 | 9130
Net Plant Heat Rate - ICAP | Btu/kWh | 9570 | 9620 | 9570 | 9570 | 9570 | 9570
Natural Gas Emission Rates - Summer
NOX Emissions Rate | lb/hr | 27.304 | 27.3036 | 27.1504 | 27.1504 | 27.0488 | 26.9116
SO2 Emissions Rate | lb/hr | 6.7493 | 6.7492 | 6.7113 | 6.7113 | 6.6862 | 6.6523
CO2 Emissions Rate | lb/hr | 359000 | 359000 | 357000 | 357000 | 356000 | 354000
Natural Gas Emission Rates - Winter
NOX Emissions Rate | lb/hr | 27.8936 | 27.8836 | 27.7522 | 27.7522 | 27.6586 | 27.5159
SO2 Emissions Rate | lb/hr | 6.895 | 6.8926 | 6.8601 | 6.8601 | 6.837 | 6.8017
CO2 Emissions Rate | lb/hr | 367000 | 367000 | 365000 | 365000 | 364000 | 362000
ULSD Emission Rates - Winter
NOX Emissions Rate | lb/hr | 60.4883 | 60.4667 | 60.1817 | 60.1817 | 59.9787 | 59.6694
SO2 Emissions Rate | lb/hr | 4.7012 | 4.6995 | 4.6773 | 4.6773 | 4.6616 | 4.6375
CO2 Emissions Rate | lb/hr | 511000 | 511000 | 508000 | 508000 | 507000 | 504000
Other Performance Values (per unit)
Fuel Required per Start (fast start - 10 min. full load) | MMBtu/Start | 204 | 204 | 204 | 204 | 204 | 204
Fuel Required per Start (regular start - 21 min. to full load) | MMBtu/Start | 391 | 391 | 391 | 391 | 391 | 391
Can startup in time for 10-minute non-spinning reserve? | Yes/No | No | No | No | No | No | No
EFORd outage rate | % | 2.17% | 2.17% | 2.17% | 2.17% | 2.17% | 2.17%
Fixed and Variable O&M Costs (per unit)
Variable Cost per Hour - NG Firing | $/MWh | 1.02 | 1.02 | 1.02 | 1.02 | 1.02 | 1.02
Variable Cost per Hour - ULSD Firing | $/MWh | 4.92 | 4.92 | 4.92 | 4.92 | 4.92 | 4.92
Variable Cost per Start | $/Start | 16800 | 16900 | 16200 | 16300 | 15800 | 15700
Updated 8/09/2016

## 1x1x1 5000F5 CC Unfired
1x1x1 5000F5 CC, Unfired
Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Performance Values (per unit)
Net Plant Capacity
Net Plant Capacity - Summer | MW | 343.9946 | 341.8342 | 341.1468 | 341.6378 | 342.0306 | 342.1288
Net Plant Capacity - Winter | MW | 342.6198 | 341.3432 | 342.0306 | 341.9324 | 341.3432 | 341.0486
DMNC Summer | MW | 330.6394 | 328.97 | 329.1664 | 329.8538 | 327.3006 | 334.4692
DMNC Winter | MW | 340.754 | 339.5756 | 340.263 | 340.1648 | 339.8702 | 339.6738
ICAP | MW | 329.3628 | 327.6934 | 327.497 | 327.497 | 326.024 | 328.5772
Net Plant Heat Rate (HHV basis)
Net Plant Heat Rate - Summer | Btu/kWh | 6820 | 6880 | 6840 | 6830 | 6820 | 6790
Net Plant Heat Rate - Winter | Btu/kWh | 6760 | 6780 | 6760 | 6760 | 6770 | 6770
Net Plant Heat Rate - DMNC Summer | Btu/kWh | 6930 | 7040 | 6990 | 6960 | 6970 | 6810
Net Plant Heat Rate - DMNC Winter | Btu/kWh | 6790 | 6810 | 6790 | 6800 | 6800 | 6800
Net Plant Heat Rate - ICAP | Btu/kWh | 6930 | 6960 | 6930 | 6930 | 6940 | 6850
Natural Gas Emission Rates - Summer
NOX Emissions Rate | lb/hr | 16.6569 | 16.6979 | 16.5675 | 16.567 | 16.5618 | 16.4937
SO2 Emissions Rate | lb/hr | 5.1613 | 5.174 | 5.1336 | 5.1334 | 5.1318 | 5.1107
CO2 Emissions Rate | lb/hr | 274000 | 275000 | 273000 | 273000 | 273000 | 272000
Natural Gas Emission Rates - Winter
NOX Emissions Rate | lb/hr | 16.4444 | 16.4316 | 16.4161 | 16.4114 | 16.4073 | 16.3932
SO2 Emissions Rate | lb/hr | 5.0954 | 5.0915 | 5.0867 | 5.0852 | 5.084 | 5.0796
CO2 Emissions Rate | lb/hr | 271000 | 271000 | 271000 | 270000 | 270000 | 270000
ULSD Emission Rates - Winter
NOX Emissions Rate | lb/hr | 44.7009 | 44.6661 | 44.624 | 44.6112 | 44.6002 | 44.5618
SO2 Emissions Rate | lb/hr | 3.4742 | 3.4715 | 3.4682 | 3.4672 | 3.4663 | 3.4633
CO2 Emissions Rate | lb/hr | 378000 | 377000 | 377000 | 377000 | 377000 | 376000
Other Performance Values (per unit)
Fuel Required per Start (warm start) | MMBtu/Start | 3100 | 3100 | 3100 | 3100 | 3100 | 3100
Can startup in time for 10-minute non-spinning reserve? | Yes/No | No | No | No | No | No | No
EFORd outage rate | % | 3% | 3% | 3% | 3% | 3% | 3%
Fixed and Variable O&M Costs (per unit)
Variable Cost per Hour - NG Firing | $/MWh | 1.0569 | 1.0653 | 1.0161 | 1.0233 | 0.98367 | 1.251
Variable Cost per Hour - ULSD Firing | $/MWh | 1.4053 | 1.4137 | 1.3645 | 1.3717 | 1.3321 | 1.5994
Variable Cost per Start | $/Start | 10900 | 11000 | 10500 | 10600 | 10300 | 10200
Updated 8/09/2016

## 1x1x1 8000H CC Unfired
1x1x1 8000H CC, Unfired
Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Performance Values (per unit)
Net Plant Capacity
Net Plant Capacity - Summer | MW | 406.9408 | 404.093 | 403.7984 | 404.093 | 404.093 | 408.2174
Net Plant Capacity - Winter | MW | 434.6332 | 431.1962 | 433.8476 | 434.1422 | 434.2404 | 437.5792
DMNC Summer | MW | 393.4874 | 392.309 | 392.309 | 392.7018 | 389.854 | 399.2812
DMNC Winter | MW | 442.0964 | 440.0342 | 441.9982 | 441.7036 | 441.409 | 447.3992
ICAP | MW | 385.2386 | 382.7836 | 382.6854 | 382.6854 | 381.016 | 385.2386
Net Plant Heat Rate (HHV basis)
Net Plant Heat Rate - Summer | Btu/kWh | 6660 | 6720 | 6670 | 6670 | 6660 | 6570
Net Plant Heat Rate - Winter | Btu/kWh | 6610 | 6640 | 6620 | 6620 | 6630 | 6550
Net Plant Heat Rate - DMNC Summer | Btu/kWh | 6750 | 6830 | 6790 | 6770 | 6780 | 6600
Net Plant Heat Rate - DMNC Winter | Btu/kWh | 6650 | 6670 | 6650 | 6650 | 6660 | 6590
Net Plant Heat Rate - ICAP | Btu/kWh | 6750 | 6790 | 6760 | 6760 | 6760 | 6650
Natural Gas Emission Rates - Summer
NOX Emissions Rate | lb/hr | 19.2426 | 19.2801 | 19.1227 | 19.1366 | 19.1079 | 19.0421
SO2 Emissions Rate | lb/hr | 5.9625 | 5.9741 | 5.9253 | 5.9297 | 5.9208 | 5.9004
CO2 Emissions Rate | lb/hr | 317000 | 318000 | 315000 | 315000 | 315000 | 314000
Natural Gas Emission Rates - Winter
NOX Emissions Rate | lb/hr | 20.3978 | 20.3283 | 20.3917 | 20.4056 | 20.441 | 20.3496
SO2 Emissions Rate | lb/hr | 6.3204 | 6.2989 | 6.3186 | 6.3228 | 6.3338 | 6.3055
CO2 Emissions Rate | lb/hr | 336000 | 335000 | 336000 | 336000 | 337000 | 335000
ULSD Emission Rates - Winter
NOX Emissions Rate | lb/hr | 55.4475 | 55.2587 | 55.431 | 55.4686 | 55.565 | 55.3166
SO2 Emissions Rate | lb/hr | 4.3094 | 4.2947 | 4.3081 | 4.311 | 4.3185 | 4.2992
CO2 Emissions Rate | lb/hr | 468000 | 467000 | 468000 | 468000 | 469000 | 467000
Other Performance Values (per unit)
Fuel Required per Start (warm start) | MMBtu/Start | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
Can startup in time for 10-minute non-spinning reserve? | Yes/No | No | No | No | No | No | No
EFORd outage rate | % | 3% | 3% | 3% | 3% | 3% | 3%
Fixed and Variable O&M Costs (per unit)
Variable Cost per Hour - NG Firing | $/MWh | 1.0237 | 1.0306 | 0.99005 | 0.99598 | 0.96334 | 1.2202
Variable Cost per Hour - ULSD Firing | $/MWh | 1.2524 | 1.2593 | 1.2188 | 1.2247 | 1.1921 | 1.4336
Variable Cost per Start | $/Start | 16500 | 16600 | 15900 | 16000 | 15500 | 15400
Updated 8/09/2016

## 1x1 5000F5 CC Unfired MECL
1x1x1 5000F5 CC, Unfired Minimum Emissions Compliance Load (MECL)
Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Performance Values (per unit)
Net Plant Capacity
Net Plant Capacity - Summer | MW | 164.7619 | 162.9085 | 163.9827 | 164.2744 | 164.2751 | 165.1533
Net Plant Capacity - Winter | MW | 163.1198 | 162.5605 | 162.6321 | 162.5339 | 162.0464 | 163.1084
DMNC Summer | MW | 159.6939 | 157.5705 | 158.0368 | 158.8166 | 157.3544 | 162.813
DMNC Winter | MW | 161.6575 | 161.2006 | 161.2674 | 161.1699 | 160.8773 | 162.0361
DMNC ICAP | MW | 156.7697 | 156.0191 | 156.5746 | 156.5746 | 156.3796 | 159.1087
Net Plant Heat Rate (HHV basis)
Net Plant Heat Rate - Summer | Btu/kWh | 8280 | 8370 | 8300 | 8290 | 8270 | 8210
Net Plant Heat Rate - Winter | Btu/kWh | 8330 | 8360 | 8340 | 8350 | 8360 | 8290
Net Plant Heat Rate - DMNC Summer | Btu/kWh | 8490 | 8670 | 8600 | 8540 | 8570 | 8260
Net Plant Heat Rate - DMNC Winter | Btu/kWh | 8430 | 8450 | 8440 | 8450 | 8460 | 8380
Net Plant Heat Rate - DMNC ICAP | Btu/kWh | 8540 | 8580 | 8530 | 8530 | 8530 | 8360

## 1x1 8000H CC Unfired MECL
1x1x1 8000H CC, Unfired Minimum Emissions Compliance Load (MECL)
Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Performance Values (per unit)
Net Plant Capacity
Net Plant Capacity - Summer | MW | 221.2448 | 219.3629 | 219.0033 | 219.3931 | 219.3931 | 222.8032
Net Plant Capacity - Winter | MW | 234.2219 | 232.4073 | 233.6372 | 233.8321 | 237.7313 | 238.5095
DMNC Summer | MW | 213.0586 | 212.0857 | 212.0848 | 212.4746 | 210.7204 | 217.3458
DMNC Winter | MW | 239.2898 | 236.8715 | 238.9001 | 238.9001 | 238.6077 | 243.48
DMNC ICAP | MW | 208.3815 | 207.3325 | 207.1146 | 207.1146 | 206.1401 | 207.8927
Net Plant Heat Rate (HHV basis)
Net Plant Heat Rate - Summer | Btu/kWh | 7530 | 7600 | 7560 | 7550 | 7540 | 7400
Net Plant Heat Rate - Winter | Btu/kWh | 7490 | 7520 | 7490 | 7500 | 7470 | 7320
Net Plant Heat Rate - DMNC Summer | Btu/kWh | 7680 | 7780 | 7730 | 7700 | 7720 | 7470
Net Plant Heat Rate - DMNC Winter | Btu/kWh | 7510 | 7540 | 7520 | 7520 | 7530 | 7340
Net Plant Heat Rate - DMNC ICAP | Btu/kWh | 7710 | 7750 | 7720 | 7720 | 7720 | 7620