## tech_params_f
AREA | TECH_PARAMS | HR_SUM_F | HR_WIN_F | VOC_NG_F | VOC_OIL_F | ICAP_SUM_F | ICAP_WIN_F | STARTUP_FUEL_F | STARTUP_VOM_F | NOX_NG_SUM_F | SO2_NG_SUM_F | CO2_NG_SUM_F | NOX_NG_WIN_F | SO2_NG_WIN_F | CO2_NG_WIN_F | NOX_OIL_SUM_F | SO2_OIL_SUM_F | CO2_OIL_SUM_F | NOX_OIL_WIN_F | SO2_OIL_WIN_F | CO2_OIL_WIN_F | EFORd_F
K | K - Long Island | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
J | J - NYC | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
G1 | G - LHV (Dutchess) | 10190 | 10030 | 0.18639 | 0 | 230.278 | 230.278 | 350 | 10500 | 75 | 5.1624 | 275000 | 75 | 5.0813 | 270000 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9783
G2 | G - LHV (Rockland) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
F | F - Capital | 10180 | 10020 | 0.18639 | 0 | 230.278 | 230.278 | 350 | 10300 | 75 | 5.1573 | 274000 | 75 | 5.0762 | 270000 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9783
C | C - Central | 10190 | 10010 | 0.18639 | 0 | 230.278 | 230.278 | 350 | 10200 | 75 | 5.1624 | 275000 | 75 | 5.0712 | 270000 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9783

## 1x0 5000F5
1x0 Siemens 5000F5, Gas Only No SCR
Item | Units | K - Long Island | J - NYC | G - LHV (Dutchess) | G - LHV (Rockland) | F - Capital | C - Central
Performance Values (per unit) |  | note: Siemens 5000F5 is designed to minimize ambient temperature impact on output; machine reaches mechanical limit at 59F- lower ambient temerature does not increase output
Net Plant Capacity, Degraded
Net Plant Capacity - Summer | MW |  |  | 230.278 |  | 230.278 | 230.278
Net Plant Capacity - Winter | MW |  |  | 230.278 |  | 230.278 | 230.278
DMNC Summer | MW |  |  | 226.786 |  | 224.555 | 224.361
DMNC Winter | MW |  |  | 230.278 |  | 230.278 | 230.278
ICAP | MW |  |  | 217.959 |  | 216.989 | 215.825
Net Plant Heat Rate (HHV basis), Degraded
Net Plant Heat Rate - Summer | Btu/kWh |  |  | 10190 |  | 10180 | 10190
Net Plant Heat Rate - Winter | Btu/kWh |  |  | 10030 |  | 10020 | 10010
Net Plant Heat Rate - DMNC Summer | Btu/kWh |  |  | 10240 |  | 10260 | 10250
Net Plant Heat Rate - DMNC Winter | Btu/kWh |  |  | 10040 |  | 10040 | 10030
Net Plant Heat Rate - ICAP | Btu/kWh |  |  | 10300 |  | 10310 | 10310
Natural Gas Emission Rates - Summer
NOX Emissions Rate | lb/hr |  |  | 75 |  | 75 | 75
SO2 Emissions Rate | lb/hr |  |  | 5.1624 |  | 5.1573 | 5.1624
CO2 Emissions Rate | lb/hr |  |  | 275000 |  | 274000 | 275000
Natural Gas Emission Rates - Winter
NOX Emissions Rate | lb/hr |  |  | 75 |  | 75 | 75
SO2 Emissions Rate | lb/hr |  |  | 5.0813 |  | 5.0762 | 5.0712
CO2 Emissions Rate | lb/hr |  |  | 270000 |  | 270000 | 270000
ULSD Emission Rates - Winter
NOX Emissions Rate | lb/hr
SO2 Emissions Rate | lb/hr
CO2 Emissions Rate | lb/hr
Other Performance Values (per unit)
Fuel Required per Start (fast start - 11 min. full load) | MMBtu/Start |  |  | 160 |  | 160 | 160
Fuel Required per Start (regular start - 28 min. to full load) | MMBtu/Start |  |  | 350 |  | 350 | 350
Can startup in time for 10-minute non-spinning reserve? | Yes/No |  |  | No |  | No | No
EFORd outage rate | % |  |  | 2.17% |  | 2.17% | 2.17%
Fixed and Variable O&M Costs (per unit)
Variable Cost per Hour - NG Firing | $/MWh |  |  | 0.18639 |  | 0.18639 | 0.18639
Variable Cost per Hour - ULSD Firing | $/MWh
Variable Cost per Start | $/Start |  |  | 10500 |  | 10300 | 10200
Updated 8/09/2016