## Legend
** This document is for informational purposes only. The baseline assessment that Developers should rely on in developing proposals will be posted concurrently with the formal solicitation. **
The table below describes the results shown in each tab
Sheet Name | Scenario | Results Type | Transmission Security Analysis | Load Level | Zone K Offshore Wind (MW) | Public Policy Transmission Need Criteria
N-1_SLL_Base | Baseline | Thermal | N-0 & N-1 | Spring Light Load | 3000 | Minimum Criteria
N-1-1_SLL_Base | Baseline | Thermal | N-1-1 | Spring Light Load | 3000 | Minimum Criteria
Ncov_SLL_Base | Baseline | Non-converged contingencies (possible voltage collapse) | N-1 & N-1-1 | Spring Light Load | 3000 | Minimum Criteria
N-1_SUM_Base | Baseline | Thermal | N-0 & N-1 | Summer Peak | 3000 | Minimum Criteria
N-1-1_SUM_Base | Baseline | Thermal | N-1-1 | Summer Peak | 3000 | Minimum Criteria
Ncov_SUM_Base | Baseline | Non-converged contingencies (possible voltage collapse) | N-1 & N-1-1 | Summer Peak | 3000 | Minimum Criteria
N-1_SLL_Alt | Alternate | Thermal | N-0 & N-1 | Spring Light Load | 6000 | Beyond Sufficency Criteria
N-1-1_SLL_Alt | Alternate | Thermal | N-1-1 | Spring Light Load | 6000 | Beyond Sufficency Criteria
Ncov_SLL_Alt | Alternate | Non-converged contingencies (possible voltage collapse) | N-1 & N-1-1 | Spring Light Load | 6000 | Beyond Sufficency Criteria
N-1_SUM_Alt | Alternate | Thermal | N-0 & N-1 | Summer Peak | 6000 | Beyond Sufficency Criteria
N-1-1_SUM_Alt | Alternate | Thermal | N-1-1 | Summer Peak | 6000 | Beyond Sufficency Criteria
Ncov_SUM_Alt | Alternate | Non-converged contingencies (possible voltage collapse) | N-1 & N-1-1 | Summer Peak | 6000 | Beyond Sufficency Criteria
The Baseline Scenario will be used in Viability & Sufficency Analysis (VSA). The Alternate Scenario will be studied in the evaluation phase and results are provided for information
Notes on viewing results:
Certain results shown in tables may be beyond Sufficency Criteria and are provided for information purposes. See additional PPTN materials for details on Sufficency Criteria
Only the worst (highest loading percentage) 20 thermal overloads are shown for each branch
Security Constrainted Dispatch function of TARA utilized in simulations. See auxilary files for more details
Voltage violations not shown given severity of thermal constraints. Voltage analysis will be performed in VSA

## N-1_SLL_Base
Monitored Facility | Areas | Cont Name | Rate Base (MVA) | Rate Cont (MVA) | SCD AC %Loading
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | P5_EGC_138_M | 31 | 31 | 173.68
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | ALPSBERK393 | 31 | 31 | 172.25
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | BS:345:ALPS99K | 31 | 31 | 171.7
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | B:ALPS345 | 31 | 31 | 171.7
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | T:W89&W90_UC20 | 31 | 31 | 163.01
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | Base Case | 31 | 31 | 147.19
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 Max |  |  |  |  | 173.68
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | B:EGC345 | 780 | 1028 | 170.31
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | 780 | 1028 | 170.31
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | SB:SPRA345_RNS2 | 780 | 1028 | 167.85
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Base Case | 780 | 1028 | 166.53
126266 DUNWOODIE 345 128835 SHORE RD 345 1 Max |  |  |  |  | 170.31
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | P5_SHORERD_138 | 1046 | 1194 | 113.62
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | Y50 | 1046 | 1194 | 105.45
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | SB:DUNW345_6 | 1046 | 1194 | 104.64
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | SB:DUNW345_4 | 1046 | 1194 | 104.59
126298 SPRAINBROOK 345 126299 REACBUS 345 SR Max |  |  |  |  | 113.62
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | P5_SHORERD_138 | 770 | 990 | 141.74
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | Y50 | 770 | 990 | 132.71
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | SB:DUNW345_6 | 770 | 990 | 131.8
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | SB:DUNW345_4 | 770 | 990 | 131.75
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | Base Case | 770 | 990 | 125.74
126299 REACBUS 345 147857 DVNPT NK 345 1 Max |  |  |  |  | 141.74
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | P5_EGC_138_M | 319 | 375 | 225.92
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | P5_SHORERD_138 | 319 | 375 | 128.41
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 139:EGC-CP2C | 319 | 375 | 112.38
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 140:CP-ROS2C | 319 | 375 | 110.27
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 141:ROS-GL2C | 319 | 375 | 109.76
126455 JAMAICA 138 129235 V STRM P 138 1 Max |  |  |  |  | 225.92
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | Y50 | 285 | 368 | 187.54
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | SB:DUNW345_4 | 285 | 368 | 184.97
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | SB:DUNW345_6 | 285 | 368 | 184.91
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | T:W89&W90_UC20 | 285 | 368 | 182.25
126455 JAMAICA 138 129249 L SUCSPH 138 1 Max |  |  |  |  | 187.54
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | P5_SHORERD_138 | 770 | 990 | 136.01
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | 770 | 990 | 126.04
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | SB:DUNW345_6 | 770 | 990 | 125.08
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | SB:DUNW345_4 | 770 | 990 | 125.03
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Base Case | 770 | 990 | 113.82
128824 EGC DUM 345 128825 EGC PAR 345 1 Max |  |  |  |  | 136.01
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | P5_SHORERD_138 | 770 | 990 | 136.54
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | Y50 | 770 | 990 | 126.7
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | SB:DUNW345_6 | 770 | 990 | 125.73
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | SB:DUNW345_4 | 770 | 990 | 125.67
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | Base Case | 770 | 990 | 114.27
128824 EGC DUM 345 128830 HMP HRBR 345 1 Max |  |  |  |  | 136.54
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | P5_SHORERD_138 | 770 | 990 | 137.77
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | Y50 | 770 | 990 | 128.15
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | SB:DUNW345_6 | 770 | 990 | 127.19
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | SB:DUNW345_4 | 770 | 990 | 127.13
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | Base Case | 770 | 990 | 116.97
128830 HMP HRBR 345 147857 DVNPT NK 345 1 Max |  |  |  |  | 137.77
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 450 | 563 | 172.34
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | B:EGC345 | 450 | 563 | 156.85
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | Y49 | 450 | 563 | 156.85
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | 21 :SRD BUS2 | 450 | 563 | 153.3
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | 18 :SRD1380 | 450 | 563 | 152.5
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | Base Case | 450 | 563 | 146.51
128835 SHORE RD 345 129293 SHORE RD 138 1 Max |  |  |  |  | 172.34
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | 540 | 562 | 167.94
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | 20 :SRD BUS1 | 540 | 562 | 150.3
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | 17 :SRD1370 | 540 | 562 | 149.56
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | Base Case | 540 | 562 | 115.43
128835 SHORE RD 345 129294 SHORE RD2 138 2 Max |  |  |  |  | 167.94
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Barrett Bus Tie | 218 | 308 | 388.95
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 12 :BRT BUS2 | 218 | 308 | 384.16
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 9 :BRT 1380 | 218 | 308 | 383.46
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 5 :VST NEW1 | 218 | 308 | 300.27
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-292 | 218 | 308 | 300.27
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Base Case | 218 | 308 | 217.19
129202 BARRETT1 138 129233 VLY STRM 138 1 Max |  |  |  |  | 388.95
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | P5_VALLEYSTREAM_138_M | 195 | 275 | 350.78
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 2 :VST 1420 | 195 | 275 | 102.55
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 1 :VST 1410 | 195 | 275 | 101.26
129203 BARRETT2 138 129204 BRRT PH 138 1 Max |  |  |  |  | 350.78
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 213 | 305 | 307.79
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 8 :VST BUS1 | 213 | 305 | 297.98
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 213 | 305 | 297.88
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | Base Case | 213 | 305 | 247.1
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | Valley Stream Bus Tie | 213 | 305 | 240.18
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 4 :VST NEW1 | 213 | 305 | 239.52
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | P5_EGC_138_M | 213 | 305 | 227.13
129203 BARRETT2 138 129234 VLY STRM2 138 2 Max |  |  |  |  | 307.79
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | P5_VALLEYSTREAM_138_M | 195 | 275 | 343.92
129204 BRRT PH 138 129276 FREEPORT 138 1 Max |  |  |  |  | 343.92
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 133 | 164 | 124.42
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 Max |  |  |  |  | 124.42
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | P5_EGC_138_M | 320 | 375 | 230.87
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | P5_SHORERD_138 | 320 | 375 | 132.28
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 139:EGC-CP2C | 320 | 375 | 116.05
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 140:CP-ROS2C | 320 | 375 | 113.87
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 141:ROS-GL2C | 320 | 375 | 113.35
129233 VLY STRM 138 129235 V STRM P 138 1 Max |  |  |  |  | 230.87
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | NEW_VS1430 | 194 | 284 | 229.5
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | Base Case | 194 | 284 | 217.42
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 194 | 284 | 215.75
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | NEW_EGC 1390 | 194 | 284 | 204.1
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | NEW_EGC 1370 | 194 | 284 | 182.72
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 12 :BRT BUS2 | 194 | 284 | 182.67
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 Max |  |  |  |  | 229.5
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 2 :VST 1420 | 280 | 442 | 127.51
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 21 :EGC 1330 | 280 | 442 | 120.85
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 280 | 442 | 119.2
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 1 :VST 1410 | 280 | 442 | 113.06
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 29 :EGC 1450 | 280 | 442 | 109.93
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 Max |  |  |  |  | 127.51
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | Y50 | 285 | 368 | 192.97
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | SB:DUNW345_4 | 285 | 368 | 190.2
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | SB:DUNW345_6 | 285 | 368 | 190.14
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | T:W89&W90_UC20 | 285 | 368 | 186.31
129248 L SUCS2 138 129249 L SUCSPH 138 1 Max |  |  |  |  | 192.97
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 24 :EGC 1360 | 320 | 352 | 254.56
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 33 :GLN 1340 | 320 | 352 | 238.07
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 31 :GLN 1350 | 320 | 352 | 238.07
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 36 :GLNNO BUS | 320 | 352 | 238.07
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | 320 | 352 | 238.07
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Base Case | 320 | 352 | 183.78
129265 CARLE PL 138 129270 E.G.C. 138 1 Max |  |  |  |  | 254.56
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 24 :EGC 1360 | 325 | 388 | 227.72
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 33 :GLN 1340 | 325 | 388 | 212.76
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | 325 | 388 | 212.76
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 36 :GLNNO BUS | 325 | 388 | 212.76
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 31 :GLN 1350 | 325 | 388 | 212.76
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Base Case | 325 | 388 | 177.14
129265 CARLE PL 138 129283 GLNWD SO 138 1 Max |  |  |  |  | 227.72
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | P5_SHORERD_138 | 450 | 585 | 118.3
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 450 | 585 | 117.3
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 450 | 585 | 117.3
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 450 | 585 | 117.3
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | 29 :EGC 1450 | 450 | 585 | 115.96
129270 E.G.C. 138 128822 E.G.C.-1 345 1 Max |  |  |  |  | 118.3
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | 320 | 352 | 232.82
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 35 :GLNSO BUS | 320 | 352 | 232.82
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 30 :GLN1320 | 320 | 352 | 232.82
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 320 | 352 | 229.47
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-361 | 320 | 352 | 228.14
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Base Case | 320 | 352 | 177.75
129270 E.G.C. 138 129288 ROSLYN 138 1 Max |  |  |  |  | 232.82
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | P5_VALLEYSTREAM_138_M | 194 | 284 | 216.08
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | Base Case | 194 | 284 | 207.18
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 46 :NBR 1400 | 194 | 284 | 192.51
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | 194 | 284 | 188.43
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-463 | 194 | 284 | 187.59
129270 E.G.C. 138 129310 NEWBRGE 138 1 Max |  |  |  |  | 216.08
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | P5_VALLEYSTREAM_138_M | 216 | 306 | 193.3
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | Base Case | 216 | 306 | 179.93
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 46 :NBR 1400 | 216 | 306 | 172.45
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | 216 | 306 | 170.79
129270 E.G.C. 138 129310 NEWBRGE 138 3 Max |  |  |  |  | 193.3
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | 24 :EGC 1360 | 450 | 585 | 128.77
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | P5_SHORERD_138 | 450 | 585 | 117.8
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | 28 :EGC 1420 | 450 | 585 | 117.17
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | 450 | 585 | 117.17
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | 33 :EGC BUS2 | 450 | 585 | 117.17
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | Y50 | 450 | 585 | 109.77
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 Max |  |  |  |  | 128.77
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | P5_VALLEYSTREAM_138_M | 210 | 302 | 199.81
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | Base Case | 210 | 302 | 184.37
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | 210 | 302 | 172.89
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 41 :NBR 1350 | 210 | 302 | 172.37
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 23 :EGC 1350 | 210 | 302 | 171.3
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 Max |  |  |  |  | 199.81
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | Base Case | 270 | 474 | 106.31
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 Max |  |  |  |  | 106.31
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | P5_VALLEYSTREAM_138_M | 229 | 299 | 300.17
129276 FREEPORT 138 129310 NEWBRGE 138 1 Max |  |  |  |  | 300.17
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 30 :GLN1320 | 351 | 388 | 209.44
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | 351 | 388 | 209.44
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 35 :GLNSO BUS | 351 | 388 | 209.44
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 351 | 388 | 206.4
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-361 | 351 | 388 | 205.2
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Base Case | 351 | 388 | 160.1
129281 GLNWD GT 138 129282 GLNWD NO 138 1 Max |  |  |  |  | 209.44
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | 351 | 388 | 209.46
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 35 :GLNSO BUS | 351 | 388 | 209.46
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 30 :GLN1320 | 351 | 388 | 209.46
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 351 | 388 | 206.42
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-361 | 351 | 388 | 205.22
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Base Case | 351 | 388 | 160.11
129281 GLNWD GT 138 129288 ROSLYN 138 1 Max |  |  |  |  | 209.46
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 381 | 446 | 209.46
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 35 :GLNSO BUS | 381 | 446 | 209.19
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | 381 | 446 | 209.19
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 30 :GLN1320 | 381 | 446 | 209.19
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-361 | 381 | 446 | 199.94
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Base Case | 381 | 446 | 166.14
129282 GLNWD NO 138 129293 SHORE RD 138 1 Max |  |  |  |  | 209.46
129282 GLNWD NO 138 129587 GLNWD NO 69.0 1 | 11 | P5_EGC_138_M | 134 | 164 | 154.06
129282 GLNWD NO 138 129587 GLNWD NO 69.0 1 | 11 | 139:EGC-CP2C | 134 | 164 | 106.7
129282 GLNWD NO 138 129587 GLNWD NO 69.0 1 | 11 | 140:CP-ROS2C | 134 | 164 | 106.4
129282 GLNWD NO 138 129587 GLNWD NO 69.0 1 | 11 | 141:ROS-GL2C | 134 | 164 | 106.06
129282 GLNWD NO 138 129587 GLNWD NO 69.0 1 Max |  |  |  |  | 154.06
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 24 :EGC 1360 | 351 | 388 | 252.63
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 351 | 388 | 242.26
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 31 :GLN 1350 | 351 | 388 | 242.08
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 36 :GLNNO BUS | 351 | 388 | 242.08
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | 351 | 388 | 242.08
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Base Case | 351 | 388 | 183.05
129283 GLNWD SO 138 129294 SHORE RD2 138 1 Max |  |  |  |  | 252.63
129283 GLNWD SO 138 129588 GLNWD SO 69.0 1 | 11 | P5_EGC_138_M | 135 | 164 | 144.95
129283 GLNWD SO 138 129588 GLNWD SO 69.0 1 Max |  |  |  |  | 144.95
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 79 :RUL 1340 | 302 | 331 | 114.66
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 77 :RUL 1310 | 302 | 331 | 113.41
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | 302 | 331 | 111.84
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | 302 | 331 | 111.53
129310 NEWBRGE 138 129361 RULND RD 138 1 Max |  |  |  |  | 114.66
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 54 :NBR 1480 | 302 | 331 | 125.5
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 77 :RUL 1310 | 302 | 331 | 113.4
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | 302 | 331 | 111.84
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | 302 | 331 | 111.53
129310 NEWBRGE 138 129361 RULND RD 138 2 Max |  |  |  |  | 125.5
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 135:RUL-NB2C | 259 | 388 | 135.15
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | Base Case | 259 | 388 | 108.29
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 54 :NBR 1480 | 259 | 388 | 105.52
129310 NEWBRGE 138 129361 RULND RD 138 3 Max |  |  |  |  | 135.15
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 | 11 | P5_EGC_138_M | 136 | 167 | 156.29
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 156.29
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | ELWOOD 138/69 kV Bank #3 | 265 | 368 | 103.28
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 80 :ELD BUS1 | 265 | 368 | 103.28
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-674 | 265 | 368 | 102.16
129315 SYOSSET 138 129333 GRENLAWN 138 1 Max |  |  |  |  | 103.28
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 136:HOL-RU2C | 215 | 288 | 117.65
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 Max |  |  |  |  | 117.65
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | P5_RULANDRD_138_M | 517 | 591 | 105.29
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 Max |  |  |  |  | 105.29
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | P5_EGC_138_M | 465 | 599 | 101.86
129344 NRTHPT1 138 129343 NRTHPT P 138 1 Max |  |  |  |  | 101.86
129501 BARRETT 69.0 129572 BALDWIN1 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 126 | 168 | 111.73
129501 BARRETT 69.0 129572 BALDWIN1 69.0 1 Max |  |  |  |  | 111.73
129507 CORONA 69.0 129565 WHITESDE 69.0 1 | 11 | P5_EGC_138_M | 101 | 112 | 108.25
129507 CORONA 69.0 129565 WHITESDE 69.0 1 Max |  |  |  |  | 108.25
129527 VLYSTRM1 69.0 129565 WHITESDE 69.0 1 | 11 | P5_EGC_138_M | 101 | 112 | 105.01
129527 VLYSTRM1 69.0 129565 WHITESDE 69.0 1 Max |  |  |  |  | 105.01
129528 VLYSTRM2 69.0 129592 LAKEVIEW 69.0 1 | 11 | P5_EGC_138_M | 63 | 72 | 129.73
129528 VLYSTRM2 69.0 129592 LAKEVIEW 69.0 1 Max |  |  |  |  | 129.73
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | P5_EGC_138_M | 101 | 112 | 215.13
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | 140:CP-ROS2C | 101 | 112 | 193.15
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | 139:EGC-CP2C | 101 | 112 | 192.73
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | 141:ROS-GL2C | 101 | 112 | 192.58
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | P5_SHORERD_138 | 101 | 112 | 135.99
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | Base Case | 101 | 112 | 107.08
129540 HERRICK 69.0 129558 SPERRY 69.0 1 Max |  |  |  |  | 215.13
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | P5_EGC_138_M | 118 | 139 | 178.74
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | 140:CP-ROS2C | 118 | 139 | 161.03
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | 139:EGC-CP2C | 118 | 139 | 160.69
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | 141:ROS-GL2C | 118 | 139 | 160.58
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | P5_SHORERD_138 | 118 | 139 | 114.97
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 Max |  |  |  |  | 178.74
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | P5_EGC_138_M | 127 | 145 | 201.29
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | 140:CP-ROS2C | 127 | 145 | 168.8
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | 139:EGC-CP2C | 127 | 145 | 168.41
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | 141:ROS-GL2C | 127 | 145 | 168.33
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | P5_SHORERD_138 | 127 | 145 | 151.6
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 Max |  |  |  |  | 201.29
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | P5_EGC_138_M | 93 | 106 | 209.32
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 139:EGC-CP2C | 93 | 106 | 153.04
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 140:CP-ROS2C | 93 | 106 | 151.37
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 141:ROS-GL2C | 93 | 106 | 150.93
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 24 :EGC 1360 | 93 | 106 | 104.55
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 Max |  |  |  |  | 209.32
129546 MALVERN 69.0 129561 W.HEMP 1 69.0 1 | 11 | P5_EGC_138_M | 63 | 72 | 122.31
129546 MALVERN 69.0 129561 W.HEMP 1 69.0 1 Max |  |  |  |  | 122.31
129562 W.HEMP 2 69.0 129592 LAKEVIEW 69.0 1 | 11 | P5_EGC_138_M | 63 | 72 | 129.38
129562 W.HEMP 2 69.0 129592 LAKEVIEW 69.0 1 Max |  |  |  |  | 129.38
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | P5_EGC_138_M | 93 | 106 | 210.18
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 139:EGC-CP2C | 93 | 106 | 153.87
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 140:CP-ROS2C | 93 | 106 | 152.21
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 141:ROS-GL2C | 93 | 106 | 151.76
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 24 :EGC 1360 | 93 | 106 | 105.37
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 Max |  |  |  |  | 210.18
129572 BALDWIN1 69.0 129617 BELMR 1 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 126 | 168 | 106.3
129572 BALDWIN1 69.0 129617 BELMR 1 69.0 1 Max |  |  |  |  | 106.3
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 | 11 | P5_EGC_138_M | 149 | 183 | 159.43
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 | 11 | 139:EGC-CP2C | 149 | 183 | 113.49
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 | 11 | 140:CP-ROS2C | 149 | 183 | 113.25
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 | 11 | 141:ROS-GL2C | 149 | 183 | 112.91
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 Max |  |  |  |  | 159.43
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | P5_EGC_138_M | 149 | 183 | 148.26
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | 139:EGC-CP2C | 149 | 183 | 103.8
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | 140:CP-ROS2C | 149 | 183 | 103.58
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | 141:ROS-GL2C | 149 | 183 | 103.26
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 148.26
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 | 11 | P5_EGC_138_M | 101 | 112 | 193.82
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 | 11 | 139:EGC-CP2C | 101 | 112 | 119.64
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 | 11 | 140:CP-ROS2C | 101 | 112 | 119.32
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 | 11 | 141:ROS-GL2C | 101 | 112 | 119.02
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 Max |  |  |  |  | 193.82
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 | 11 | P5_EGC_138_M | 101 | 112 | 216.1
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 101 | 112 | 137.61
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 | 11 | 139:EGC-CP2C | 101 | 112 | 129.33
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 Max |  |  |  |  | 216.1
129619 BELMR 2 69.0 129639 NEWBRGE1 69.0 1 | 11 | P5_EGC_138_M | 110 | 135 | 116.87
129619 BELMR 2 69.0 129639 NEWBRGE1 69.0 1 Max |  |  |  |  | 116.87
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 | 11 | P5_EGC_138_M | 127 | 145 | 111.06
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 111.06
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | P5_EGC_138_M | 101 | 112 | 197.59
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | 139:EGC-CP2C | 101 | 112 | 123.3
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | 140:CP-ROS2C | 101 | 112 | 122.97
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | 141:ROS-GL2C | 101 | 112 | 122.67
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 Max |  |  |  |  | 197.59
129635 N.BELLMR 69.0 129640 NEWBRGE2 69.0 1 | 11 | P5_EGC_138_M | 139 | 154 | 152.68
129635 N.BELLMR 69.0 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 152.68
129642 OYSTRBAY 69.0 129650 SYOSSET 69.0 1 | 11 | P5_EGC_138_M | 173 | 185 | 122.46
129642 OYSTRBAY 69.0 129650 SYOSSET 69.0 1 Max |  |  |  |  | 122.46
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 | 11 | P5_VALLEYSTREAM_138_M | 87 | 96 | 107.99
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 Max |  |  |  |  | 107.99
130718 Q535_POI 138 130675 RIVHEAD_PSU 138 1 | 11 | 129488 EDWRDSAV 138 130718 Q535_POI 138 1 | 25 | 25 | 166.06
130718 Q535_POI 138 130675 RIVHEAD_PSU 138 1 Max |  |  |  |  | 166.06
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 | 11 | Base Case | 40 | 40 | 107.79
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 | 11 | 110:NEW WLD 138 BREAKER | 40 | 40 | 105.18
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 | 11 | 129483 CANAL 138 129493 RVRHD 138 1 | 40 | 40 | 104.89
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 | 11 | 133:CAN 1310 | 40 | 40 | 104.89
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 | 11 | 283:WLD 650 | 40 | 40 | 104.88
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 | 11 | WLDWDBUS1 | 40 | 40 | 104.8
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 Max |  |  |  |  | 107.79

## N-1-1_SLL_Base
Monitored Facility | Areas | First Level Scenario | Cont Name | Rate Base (MVA) | Rate Cont (MVA) | SCD AC %Loading
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | Y50 | Y49 | 155 | 210 | 152.74
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | Y50 | NNC-B | 155 | 210 | 123
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | Y50 | NNC-C | 155 | 210 | 122.61
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | Y50 | Base Case | 155 | 210 | 113.04
121408 NE_601_NY 138 129343 NRTHPT P 138 1 Max | [5 empty] | 152.74
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | Y50 | Y49 | 155 | 210 | 152.28
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | Y50 | NNC-1C | 155 | 210 | 122.81
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | Y50 | NNC-A | 155 | 210 | 122.81
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | Y50 | NNC-C | 155 | 210 | 122.25
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | Y50 | Base Case | 155 | 210 | 112.71
121409 NE_602_NY 138 129343 NRTHPT P 138 2 Max | [5 empty] | 152.28
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | Y50 | Y49 | 155 | 210 | 151.28
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | Y50 | NNC-1C | 155 | 210 | 122.01
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | Y50 | NNC-A | 155 | 210 | 122.01
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | Y50 | NNC-B | 155 | 210 | 121.83
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | Y50 | Base Case | 155 | 210 | 111.99
121410 NE_603_NY 138 129343 NRTHPT P 138 3 Max | [5 empty] | 151.28
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:W49_5 | 823 | 953 | 101.15
126266 DUNWOODIE 345 126600 REAC71 345 BY Max | [5 empty] | 101.15
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | Base Case | 780 | 1028 | 251.22
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | 901 L&M | 780 | 1028 | 205.77
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | JAMCA - VLLYSTRM 901L&M 138 | 780 | 1028 | 205.77
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | VLY STRM 138 kV P.A.R. | 780 | 1028 | 205.47
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | VLY STRM 138/69 kV Bank #5 | 780 | 1028 | 205.24
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | 8 :VST BUS1 | 780 | 1028 | 205.11
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | 903 | 780 | 1028 | 203.73
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | JAMCA - LKSUCCESS 903 138 | 780 | 1028 | 203.73
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | LKE SCSS 138 kV P.A.R. | 780 | 1028 | 203.62
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | P5_VALLEYSTREAM_138_M | 780 | 1028 | 203.28
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | 16 :LKS BUS2 | 780 | 1028 | 202.87
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | P5_LAKESUCCES_138 | 780 | 1028 | 200.86
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | SB:ASTO345_5 | 780 | 1028 | 193.6
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | SB:ASTO345_3 | 780 | 1028 | 193.59
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | ASTORIA 345/138 PS | 780 | 1028 | 193.58
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | SIN:350 Hellgate#4-Astoria E | 780 | 1028 | 193.14
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | SIN:340-Hellgate#1-Astoria E | 780 | 1028 | 193.12
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | GEN: OSW W49 Street 5 | 780 | 1028 | 193.09
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | SB:RAINEY_6W | 780 | 1028 | 193.09
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | SB:RAIN345_6E | 780 | 1028 | 193.05
126266 DUNWOODIE 345 128835 SHORE RD 345 1 Max | [5 empty] | 251.22
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | Y49 | Y50 | 143 | 178 | 165.8
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | Y49 | SB:DUNW345_4 | 143 | 178 | 162.77
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | Y49 | SB:DUNW345_6 | 143 | 178 | 162.3
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | Y49 | T:W89&W90_UC20 | 143 | 178 | 157.4
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | Y49 | P5_SHORERD_138 | 143 | 178 | 153.06
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | Y50 | SB:SPRA345_RNS2 | 143 | 178 | 103.18
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | Y50 | Y49 | 143 | 178 | 102.96
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 Max | [5 empty] | 165.8
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | Y50 | Northport-Norwalk NNC-3C | 1046 | 1194 | 138.4
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | Y50 | NNC-3C | 1046 | 1194 | 138.4
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | Y50 | 74 :NPT 1410 | 1046 | 1194 | 138.3
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | Y50 | 67 :NPT 1300 | 1046 | 1194 | 138.3
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | Y50 | 72 :NPT BUS1-2 | 1046 | 1194 | 138.3
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | Y50 | Base Case | 1046 | 1194 | 134.8
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | VLY STRM 138/69 kV Bank #5 | P5_SHORERD_138 | 1046 | 1194 | 133.06
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 903 | P5_SHORERD_138 | 1046 | 1194 | 132.92
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 903 | Y50 | 1046 | 1194 | 132.92
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | JAMCA - LKSUCCESS 903 138 | P5_SHORERD_138 | 1046 | 1194 | 132.92
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | JAMCA - LKSUCCESS 903 138 | Y50 | 1046 | 1194 | 132.92
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | LKE SCSS 138 kV P.A.R. | P5_SHORERD_138 | 1046 | 1194 | 132.91
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | LKE SCSS 138 kV P.A.R. | Y50 | 1046 | 1194 | 132.9
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | JAMCA - VLLYSTRM 901L&M 138 | P5_SHORERD_138 | 1046 | 1194 | 132.76
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 901 L&M | P5_SHORERD_138 | 1046 | 1194 | 132.76
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | VLY STRM 138 kV P.A.R. | P5_SHORERD_138 | 1046 | 1194 | 132.66
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | JAMCA - LKSUCCESS 903 138 | SB:DUNW345_4 | 1046 | 1194 | 131.71
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 903 | SB:DUNW345_4 | 1046 | 1194 | 131.71
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | LKE SCSS 138 kV P.A.R. | SB:DUNW345_4 | 1046 | 1194 | 131.69
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | JAMCA - LKSUCCESS 903 138 | SB:DUNW345_6 | 1046 | 1194 | 131.66
126298 SPRAINBROOK 345 126299 REACBUS 345 SR Max | [5 empty] | 138.4
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_5 | 887 | 1062 | 119.42
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_7 | 887 | 1062 | 119.25
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1062 | 115.25
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RS3 | 887 | 1062 | 111.72
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | T:W89&W90_UC20 | 887 | 1062 | 110.51
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_5 | 887 | 1062 | 109.55
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RNS3 | 887 | 1062 | 108.68
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | T:F38&F39_UC02 | 887 | 1062 | 108.02
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_3 | 887 | 1062 | 106.57
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SPRNBRK - W49ST 345 M52 | 887 | 1062 | 106.46
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:RAIN345_1E | 887 | 1062 | 102.05
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | DNWDIE - MOTTHAVEN 345 71 | SB:W49_5 | 887 | 1062 | 101.54
126298 SPRAINBROOK 345 126517 REACM51 345 BY Max | [5 empty] | 119.42
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_5 | 887 | 1062 | 118.26
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_7 | 887 | 1062 | 118.08
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1062 | 114.05
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RS3 | 887 | 1062 | 110.78
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | T:W89&W90_UC20 | 887 | 1062 | 110.51
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | T:F38&F39_UC02 | 887 | 1062 | 108.02
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RNS3 | 887 | 1062 | 107.5
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_BTN | 887 | 1062 | 106.61
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_2 | 887 | 1062 | 106.61
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SPRNBRK - W49ST 345 M51 | 887 | 1062 | 106.46
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:RAIN345_1E | 887 | 1062 | 101.17
126298 SPRAINBROOK 345 126518 REACM52 345 BY Max | [5 empty] | 118.26
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | Y50 | Base Case | 770 | 990 | 187.95
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | Y50 | Northport-Norwalk NNC-3C | 770 | 990 | 169
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | Y50 | NNC-3C | 770 | 990 | 169
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | Y50 | 74 :NPT 1410 | 770 | 990 | 168.89
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | Y50 | 67 :NPT 1300 | 770 | 990 | 168.88
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | Y50 | 72 :NPT BUS1-2 | 770 | 990 | 168.88
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | VLY STRM 138/69 kV Bank #5 | P5_SHORERD_138 | 770 | 990 | 163.61
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 901 L&M | P5_SHORERD_138 | 770 | 990 | 163.55
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | JAMCA - VLLYSTRM 901L&M 138 | P5_SHORERD_138 | 770 | 990 | 163.55
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | VLY STRM 138 kV P.A.R. | P5_SHORERD_138 | 770 | 990 | 163.43
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 903 | Y50 | 770 | 990 | 163.27
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | JAMCA - LKSUCCESS 903 138 | Y50 | 770 | 990 | 163.27
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | LKE SCSS 138 kV P.A.R. | Y50 | 770 | 990 | 163.25
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 903 | P5_SHORERD_138 | 770 | 990 | 163.06
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | JAMCA - LKSUCCESS 903 138 | P5_SHORERD_138 | 770 | 990 | 163.06
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | LKE SCSS 138 kV P.A.R. | P5_SHORERD_138 | 770 | 990 | 163.05
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | JAMCA - LKSUCCESS 903 138 | SB:DUNW345_4 | 770 | 990 | 161.89
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 903 | SB:DUNW345_4 | 770 | 990 | 161.89
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | LKE SCSS 138 kV P.A.R. | SB:DUNW345_4 | 770 | 990 | 161.88
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 903 | SB:DUNW345_6 | 770 | 990 | 161.83
126299 REACBUS 345 147857 DVNPT NK 345 1 Max | [5 empty] | 187.95
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_5 | 887 | 1061 | 121.09
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_7 | 887 | 1061 | 120.9
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | T:W89&W90_UC20 | 887 | 1061 | 117.65
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1061 | 116.74
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | T:F38&F39_UC02 | 887 | 1061 | 114.23
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RS3 | 887 | 1061 | 113.65
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_5 | 887 | 1061 | 113.13
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RNS3 | 887 | 1061 | 111.24
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_3 | 887 | 1061 | 110.26
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SPRNBRK - W49ST 345 M52 | 887 | 1061 | 110.18
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:SPRA345_RNS4 | 887 | 1061 | 105.15
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:SPRA345_RS4 | 887 | 1061 | 104.21
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SB:RAIN345_1E | 887 | 1061 | 102.45
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | DNWDIE - MOTTHAVEN 345 71 | SB:W49_5 | 887 | 1061 | 101.88
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | GEN: OSW Holbrook 2 | SB:W49_5 | 887 | 1061 | 101.69
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | GEN: OSW Barret 2 | SB:W49_5 | 887 | 1061 | 101.69
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | Y49 | SB:DUNW345_5 | 887 | 1061 | 101.6
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | MOTTHAVEN - RAINEY Q12 345 | SB:RAIN345_1E | 887 | 1061 | 101.53
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | Y49 | SB:DUNW345_7 | 887 | 1061 | 101.53
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | DNWDIE - MOTTHAVEN 345 72 | SB:W49_5 | 887 | 1061 | 101.16
126304 W 49 ST 345 126517 REACM51 345 1 Max | [5 empty] | 121.09
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_5 | 887 | 1061 | 120.21
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_7 | 887 | 1061 | 120.02
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | T:W89&W90_UC20 | 887 | 1061 | 117.65
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1061 | 115.84
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | T:F38&F39_UC02 | 887 | 1061 | 114.23
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RS3 | 887 | 1061 | 113.03
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RNS3 | 887 | 1061 | 110.38
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_BTN | 887 | 1061 | 110.3
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_2 | 887 | 1061 | 110.29
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SPRNBRK - W49ST 345 M51 | 887 | 1061 | 110.18
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:SPRA345_RNS5 | 887 | 1061 | 104.76
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:SPRA345_RS5 | 887 | 1061 | 104.21
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | Y49 | SB:DUNW345_5 | 887 | 1061 | 101.6
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:RAIN345_1E | 887 | 1061 | 101.57
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | MOTTHAVEN - RAINEY Q12 345 | SB:RAIN345_1E | 887 | 1061 | 101.53
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | Y49 | SB:DUNW345_7 | 887 | 1061 | 101.53
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | GEN: OSW Barret 2 | SB:W49_2 | 887 | 1061 | 101.08
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | GEN: OSW Holbrook 2 | SB:W49_BTN | 887 | 1061 | 101.08
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | GEN: OSW Holbrook 2 | SB:W49_2 | 887 | 1061 | 101.08
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | GEN: OSW Barret 2 | SB:W49_BTN | 887 | 1061 | 101.08
126304 W 49 ST 345 126518 REACM52 345 2 Max | [5 empty] | 120.21
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 217 | 348 | 129.69
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 217 | 348 | 128.36
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 217 | 348 | 124.02
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SIN:340-Hellgate#1-Astoria E | Base Case | 217 | 348 | 115.87
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | MOTTHAVEN - RAINEY Q11 345 | Base Case | 217 | 348 | 115.6
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | GEN: OSW Barret 2 | Base Case | 217 | 348 | 115.05
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | GEN: OSW Holbrook 2 | Base Case | 217 | 348 | 115.05
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | MOTTHAVEN - RAINEY Q12 345 | Base Case | 217 | 348 | 113.92
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SIN:340-Hellgate#1-Astoria E | 217 | 348 | 111.47
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SIN:340-Hellgate#1-Astoria E | 217 | 348 | 110.35
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | Y50 | Base Case | 217 | 348 | 108.53
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | DNWDIE - MOTTHAVEN 345 72 | Base Case | 217 | 348 | 107
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | DNWDIE - MOTTHAVEN 345 71 | Base Case | 217 | 348 | 106.88
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | SIN:340-Hellgate#1-Astoria E | 217 | 348 | 105.7
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | Y49 | Y50 | 217 | 348 | 102.69
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | GEN: OSW Holbrook 1 | Base Case | 217 | 348 | 101.78
126334 ASTE-ERG 138 126445 HG 4 138 1 Max | [5 empty] | 129.69
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 217 | 348 | 128.87
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 217 | 348 | 127.53
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 217 | 348 | 123.54
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SIN:350 Hellgate#4-Astoria E | Base Case | 217 | 348 | 115.76
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | MOTTHAVEN - RAINEY Q11 345 | Base Case | 217 | 348 | 114.93
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | GEN: OSW Holbrook 2 | Base Case | 217 | 348 | 114.3
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | GEN: OSW Barret 2 | Base Case | 217 | 348 | 114.3
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | MOTTHAVEN - RAINEY Q12 345 | Base Case | 217 | 348 | 113.18
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SIN:350 Hellgate#4-Astoria E | 217 | 348 | 111.15
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SIN:350 Hellgate#4-Astoria E | 217 | 348 | 110.02
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | Y50 | Base Case | 217 | 348 | 107.76
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | DNWDIE - MOTTHAVEN 345 72 | Base Case | 217 | 348 | 106.26
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | DNWDIE - MOTTHAVEN 345 71 | Base Case | 217 | 348 | 106.13
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | SIN:350 Hellgate#4-Astoria E | 217 | 348 | 105.5
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | Y49 | Y50 | 217 | 348 | 102.23
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | GEN: OSW Holbrook 1 | Base Case | 217 | 348 | 101.06
126352 ASTE-WRG 138 126442 HG 1 138 1 Max | [5 empty] | 128.87
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | Y49 | Y50 | 186 | 250 | 152.27
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | Y50 | Y49 | 186 | 250 | 140.98
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | Y50 | GEN: OSW Astoria 2 | 186 | 250 | 135.39
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | Y49 | GEN: OSW Astoria 2 | 186 | 250 | 110.43
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | 138-361 | GEN: OSW Astoria 2 | 186 | 250 | 101.07
126364 CORONA1R 138 126455 JAMAICA 138 1 Max | [5 empty] | 152.27
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | Y49 | Y50 | 186 | 250 | 162.19
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | Y50 | Y49 | 186 | 250 | 145.82
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | Y50 | GEN: OSW Astoria 2 | 186 | 250 | 139.52
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | Y49 | GEN: OSW Astoria 2 | 186 | 250 | 115.9
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | 138-361 | GEN: OSW Astoria 2 | 186 | 250 | 112.33
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | 138-366 | GEN: OSW Astoria 2 | 186 | 250 | 111.03
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | 138-364 | GEN: OSW Astoria 2 | 186 | 250 | 108.75
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | 138-362 | GEN: OSW Astoria 2 | 186 | 250 | 108.59
126365 CORONA2R 138 126455 JAMAICA 138 1 Max | [5 empty] | 162.19
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 208 | 342 | 135.3
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 208 | 342 | 133.94
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 208 | 342 | 129.74
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SIN:340-Hellgate#1-Astoria E | Base Case | 208 | 342 | 121
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | MOTTHAVEN - RAINEY Q11 345 | Base Case | 208 | 342 | 120.59
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | GEN: OSW Barret 2 | Base Case | 208 | 342 | 120.02
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | GEN: OSW Holbrook 2 | Base Case | 208 | 342 | 120.02
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | MOTTHAVEN - RAINEY Q12 345 | Base Case | 208 | 342 | 118.85
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | Y50 | Base Case | 208 | 342 | 113.54
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SIN:340-Hellgate#1-Astoria E | 208 | 342 | 113.42
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SIN:340-Hellgate#1-Astoria E | 208 | 342 | 112.28
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | DNWDIE - MOTTHAVEN 345 72 | Base Case | 208 | 342 | 111.77
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | DNWDIE - MOTTHAVEN 345 71 | Base Case | 208 | 342 | 111.67
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | SIN:340-Hellgate#1-Astoria E | 208 | 342 | 107.5
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | GEN: OSW Holbrook 1 | Base Case | 208 | 342 | 106.17
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SHORE RD 345/138 Bank #1 | Base Case | 208 | 342 | 105.18
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | GEN: OSW Ruland 3 | Base Case | 208 | 342 | 105.04
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | 138-366 | Base Case | 208 | 342 | 104.61
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SHORE RD 345/138 Bank #2 | Base Case | 208 | 342 | 104.52
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | Y49 | Y50 | 208 | 342 | 104.49
126385 E179 ST W 138 126445 HG 4 138 1 Max | [5 empty] | 135.3
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | Y49 | Y50 | 165 | 165 | 167.77
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | Y50 | Y49 | 165 | 165 | 106.62
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | SIN:350 Hellgate#4-Astoria E | Y50 | 165 | 165 | 101.75
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | SIN:340-Hellgate#1-Astoria E | Y50 | 165 | 165 | 101.75
126399 TAP X9 138 126437 FGT_X9 138 1 Max | [5 empty] | 167.77
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | Y49 | Y50 | 293 | 355 | 114.91
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | Y50 | Y49 | 293 | 355 | 103.68
126415 CORONA-N 138 126365 CORONA2R 138 1 Max | [5 empty] | 114.91
126418 FRESH KILLS 138 126520 WILOWBK1 138 1 | 10 | SHORE RD 345/138 Bank #2 | Base Case | 230 | 403 | 101.97
126418 FRESH KILLS 138 126520 WILOWBK1 138 1 Max | [5 empty] | 101.97
126418 FRESH KILLS 138 126521 WILOWBK2 138 1 | 10 | SHORE RD 345/138 Bank #2 | Base Case | 230 | 403 | 101.28
126418 FRESH KILLS 138 126521 WILOWBK2 138 1 Max | [5 empty] | 101.28
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 217 | 310 | 118.62
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 217 | 310 | 118.62
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | 138-361 | Base Case | 217 | 310 | 102.33
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | RAINEYW - FARRAGUTE 345 61 | Base Case | 217 | 310 | 102.3
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 217 | 310 | 102.19
126434 GRENWOOD N 138 126454 KENTTAP 138 1 Max | [5 empty] | 118.62
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 208 | 342 | 134.46
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 208 | 342 | 133.08
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 208 | 342 | 129.24
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SIN:350 Hellgate#4-Astoria E | Base Case | 208 | 342 | 120.87
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | MOTTHAVEN - RAINEY Q11 345 | Base Case | 208 | 342 | 119.89
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | GEN: OSW Barret 2 | Base Case | 208 | 342 | 119.24
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | GEN: OSW Holbrook 2 | Base Case | 208 | 342 | 119.24
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | MOTTHAVEN - RAINEY Q12 345 | Base Case | 208 | 342 | 118.08
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SIN:350 Hellgate#4-Astoria E | 208 | 342 | 113.09
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | Y50 | Base Case | 208 | 342 | 112.73
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SIN:350 Hellgate#4-Astoria E | 208 | 342 | 111.95
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | DNWDIE - MOTTHAVEN 345 72 | Base Case | 208 | 342 | 111.01
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | DNWDIE - MOTTHAVEN 345 71 | Base Case | 208 | 342 | 110.89
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | SIN:350 Hellgate#4-Astoria E | 208 | 342 | 107.3
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | GEN: OSW Holbrook 1 | Base Case | 208 | 342 | 105.42
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SHORE RD 345/138 Bank #1 | Base Case | 208 | 342 | 104.41
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | GEN: OSW Ruland 3 | Base Case | 208 | 342 | 104.3
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | Y49 | Y50 | 208 | 342 | 104.02
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | 138-366 | Base Case | 208 | 342 | 103.82
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SHORE RD 345/138 Bank #2 | Base Case | 208 | 342 | 103.75
126442 HG 1 138 126647 E179 ST E 138 1 Max | [5 empty] | 134.46
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | Y49 | Y50 | 178 | 363 | 143.84
126452 HUDAVE E 138 126455 JAMAICA 138 1 Max | [5 empty] | 143.84
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | Y49 | Y50 | 178 | 363 | 143.84
126452 HUDAVE E 138 126455 JAMAICA 138 2 Max | [5 empty] | 143.84
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 217 | 310 | 116.88
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 217 | 310 | 116.88
126454 KENTTAP 138 126507 VERNON-W 138 1 Max | [5 empty] | 116.88
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y50 | Y49 | 319 | 375 | 247.5
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | Y50 | 319 | 375 | 235.2
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 20 :SRD BUS1 | 319 | 375 | 170.86
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 903 | Y50 | 319 | 375 | 170.01
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | JAMCA - LKSUCCESS 903 138 | Y50 | 319 | 375 | 170.01
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | LKE SCSS 138 kV P.A.R. | Y50 | 319 | 375 | 170
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 21 :SRD BUS2 | 319 | 375 | 169.62
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y50 | Northport-Norwalk NNC-3C | 319 | 375 | 162.79
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y50 | NNC-3C | 319 | 375 | 162.79
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y50 | 72 :NPT BUS1-2 | 319 | 375 | 162.59
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 35 :GLNSO BUS | 319 | 375 | 147.51
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 138-365 | 319 | 375 | 147.51
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 138-366 | 319 | 375 | 146.22
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 36 :GLNNO BUS | 319 | 375 | 146.22
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 319 | 375 | 145.47
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y50 | 16 :LKS BUS2 | 319 | 375 | 145.16
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y50 | LKE SCSS 138 kV P.A.R. | 319 | 375 | 144.83
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y50 | 903 | 319 | 375 | 144.49
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y50 | JAMCA - LKSUCCESS 903 138 | 319 | 375 | 144.49
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 319 | 375 | 144.22
126455 JAMAICA 138 129235 V STRM P 138 1 Max | [5 empty] | 247.5
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | Y49 | Y50 | 285 | 368 | 294.97
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 901 L&M | Y50 | 285 | 368 | 230.33
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | JAMCA - VLLYSTRM 901L&M 138 | Y50 | 285 | 368 | 230.33
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | VLY STRM 138/69 kV Bank #5 | Y50 | 285 | 368 | 230.2
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | VLY STRM 138 kV P.A.R. | Y50 | 285 | 368 | 230.19
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | E.G.C. 345 kV P.A.R. #1 | Y50 | 285 | 368 | 208.69
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | EGC REA | Y50 | 285 | 368 | 208.68
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | E.G.C. 345 kV P.A.R. #2 | Y50 | 285 | 368 | 208.42
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | NNC-3C | Y50 | 285 | 368 | 207.61
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | Northport-Norwalk NNC-3C | Y50 | 285 | 368 | 207.61
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-365 | Y50 | 285 | 368 | 204.69
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-366 | Y50 | 285 | 368 | 196.38
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-361 | Y50 | 285 | 368 | 194.9
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-364 | Y50 | 285 | 368 | 194.59
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-362 | Y50 | 285 | 368 | 194.39
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-363 | Y50 | 285 | 368 | 186.18
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | GEN: OSW W49 Street 5 | Y50 | 285 | 368 | 184.89
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-467 | Y50 | 285 | 368 | 184.87
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-463 | Y50 | 285 | 368 | 184.39
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | GEN: OSW Gowanus 1 | Y50 | 285 | 368 | 183.46
126455 JAMAICA 138 129249 L SUCSPH 138 1 Max | [5 empty] | 294.97
126506 VERNON-E 138 126646 GRENWOOD S 138 1 | 10 | 138-361 | Base Case | 217 | 310 | 101.84
126506 VERNON-E 138 126646 GRENWOOD S 138 1 Max | [5 empty] | 101.84
126581 HG TAP 138 126730 15055 SR 138 1 | 10 | GEN: OSW Holbrook 2 | Base Case | 269 | 400 | 107.1
126581 HG TAP 138 126730 15055 SR 138 1 | 10 | GEN: OSW Barret 2 | Base Case | 269 | 400 | 107.1
126581 HG TAP 138 126730 15055 SR 138 1 | 10 | 138-363 | Base Case | 269 | 400 | 101.51
126581 HG TAP 138 126730 15055 SR 138 1 Max | [5 empty] | 107.1
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:W49_5 | 822 | 953 | 102.44
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:W49_BTN | 822 | 953 | 101.07
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:W49_2 | 822 | 953 | 101.06
126600 REAC71 345 126641 MOTT HAVEN 345 3 Max | [5 empty] | 102.44
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M52 | MOTTHAVEN - RAINEY Q11 345 | 822 | 953 | 123.03
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:W49_5 | 822 | 953 | 123.02
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_1 | 822 | 953 | 122.99
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_BTW | 822 | 953 | 122.99
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:W49_2 | 822 | 953 | 122.96
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:W49_BTN | 822 | 953 | 122.96
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:W49_3 | 822 | 953 | 122.94
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M51 | MOTTHAVEN - RAINEY Q11 345 | 822 | 953 | 122.93
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SPRNBRK - W49ST 345 M52 | 822 | 953 | 122.93
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M52 | SB:RAIN345_2E | 822 | 953 | 122.93
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SPRNBRK - W49ST 345 M51 | 822 | 953 | 122.93
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:SPRA345_RS4 | 822 | 953 | 122.91
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:SPRA345_RS5 | 822 | 953 | 122.91
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_1 | 822 | 953 | 122.89
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_BTW | 822 | 953 | 122.89
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M51 | SB:RAIN345_2E | 822 | 953 | 122.83
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:SPRA345_RNS4 | 822 | 953 | 121.62
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:SPRA345_RNS5 | 822 | 953 | 121.51
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | Y50 | 822 | 953 | 115.35
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | Y50 | MOTTHAVEN - RAINEY Q11 345 | 822 | 953 | 114.54
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 Max | [5 empty] | 123.03
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M52 | SB:RAINEY_7W | 822 | 953 | 125.5
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M51 | SB:RAINEY_7W | 822 | 953 | 125.38
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M52 | MOTTHAVEN - RAINEY Q12 345 | 822 | 953 | 125.35
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_9 | 822 | 953 | 125.31
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_4 | 822 | 953 | 125.29
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M51 | MOTTHAVEN - RAINEY Q12 345 | 822 | 953 | 125.23
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_9 | 822 | 953 | 125.19
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_4 | 822 | 953 | 125.16
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SB:W49_5 | 822 | 953 | 123.79
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SB:W49_BTN | 822 | 953 | 123.71
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SB:W49_2 | 822 | 953 | 123.71
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SB:W49_3 | 822 | 953 | 123.7
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SPRNBRK - W49ST 345 M52 | 822 | 953 | 123.69
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SPRNBRK - W49ST 345 M51 | 822 | 953 | 123.69
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SB:SPRA345_RS4 | 822 | 953 | 123.66
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SB:SPRA345_RS5 | 822 | 953 | 123.66
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M52 | SB:RAINEY_6W | 822 | 953 | 122.79
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SB:SPRA345_RNS4 | 822 | 953 | 122.34
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SB:SPRA345_RNS5 | 822 | 953 | 122.24
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M51 | SB:RAINEY_6W | 822 | 953 | 121.74
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 Max | [5 empty] | 125.5
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | SPRNBRK - W49ST 345 M52 | SB:RAIN345_1E | 775 | 932 | 120.61
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | GEN: OSW Holbrook 1 | SB:RAIN345_1E | 775 | 932 | 120.09
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | GEN: OSW Ruland 3 | SB:RAIN345_1E | 775 | 932 | 119.41
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | SPRNBRK - W49ST 345 M51 | SB:RAIN345_1E | 775 | 932 | 118.17
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | GOWANUS-GREENWOOD PAR 3 | SB:RAIN345_1E | 775 | 932 | 117.16
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | GOWANUS 345/138 14TR | SB:RAIN345_1E | 775 | 932 | 117.06
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | GOWANUS 345/138 2TR | SB:RAIN345_1E | 775 | 932 | 116.84
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | GEN: OSW Barret 2 | SB:RAIN345_1E | 775 | 932 | 115.38
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | GEN: OSW Holbrook 2 | SB:RAIN345_1E | 775 | 932 | 115.38
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | SIN:350 Hellgate#4-Astoria E | SB:RAIN345_1E | 775 | 932 | 114.57
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | SIN:340-Hellgate#1-Astoria E | SB:RAIN345_1E | 775 | 932 | 114.56
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | S:E13TH_45 | SB:RAIN345_1E | 775 | 932 | 114.22
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | S:E13TH_46 | SB:RAIN345_1E | 775 | 932 | 112.99
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | S:E13TH_M54 | SB:RAIN345_1E | 775 | 932 | 112.82
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | S:E13TH_M55 | SB:RAIN345_1E | 775 | 932 | 112.07
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | Y50 | SB:RAIN345_1E | 775 | 932 | 110.15
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | Northport Unit 1* | SB:RAIN345_1E | 775 | 932 | 109.71
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | GEN:NRTPTG1 | SB:RAIN345_1E | 775 | 932 | 109.71
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | RAINEY-CORONA PAR 2 | SB:RAIN345_1E | 775 | 932 | 103.38
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | RAINEY - CORONA PAR | SB:RAIN345_1E | 775 | 932 | 103.24
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 Max | [5 empty] | 120.61
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | Y49 | Y50 | 143 | 177 | 174.29
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | Y49 | SB:DUNW345_4 | 143 | 177 | 171.17
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | Y49 | SB:DUNW345_6 | 143 | 177 | 170.69
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | Y49 | T:W89&W90_UC20 | 143 | 177 | 165.77
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | Y49 | P5_SHORERD_138 | 143 | 177 | 161.8
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | Y50 | SB:SPRA345_RNS2 | 143 | 177 | 108.99
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | Y50 | Y49 | 143 | 177 | 108.77
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | NNC-3C | P5_EGC_138_M | 143 | 177 | 105.86
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | Northport-Norwalk NNC-3C | P5_EGC_138_M | 143 | 177 | 105.86
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | SIN:340-Hellgate#1-Astoria E | Y50 | 143 | 177 | 101.6
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | SIN:350 Hellgate#4-Astoria E | Y50 | 143 | 177 | 101.6
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 Max | [5 empty] | 174.29
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | Y49 | Y50 | 143 | 178 | 169.54
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | Y49 | SB:DUNW345_4 | 143 | 178 | 166.47
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | Y49 | SB:DUNW345_6 | 143 | 178 | 165.99
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | Y49 | T:W89&W90_UC20 | 143 | 178 | 161.09
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | Y49 | P5_SHORERD_138 | 143 | 178 | 156.95
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | Y50 | SB:SPRA345_RNS2 | 143 | 178 | 105.68
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | Y50 | Y49 | 143 | 178 | 105.46
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | Northport-Norwalk NNC-3C | P5_EGC_138_M | 143 | 178 | 101.35
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | NNC-3C | P5_EGC_138_M | 143 | 178 | 101.35
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 Max | [5 empty] | 169.54
126647 E179 ST E 138 126730 15055 SR 138 SR | 10 | GEN: OSW Barret 2 | Base Case | 268 | 400 | 107.5
126647 E179 ST E 138 126730 15055 SR 138 SR | 10 | GEN: OSW Holbrook 2 | Base Case | 268 | 400 | 107.5
126647 E179 ST E 138 126730 15055 SR 138 SR | 10 | 138-363 | Base Case | 268 | 400 | 101.89
126647 E179 ST E 138 126730 15055 SR 138 SR Max | [5 empty] | 107.5
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | P5_EGC_138_M | 750 | 800 | 121.7
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | T:W89&W90_UC20 | 750 | 800 | 111
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | P5_SHORERD_138 | 750 | 800 | 109.95
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | SB:DUNW345_4 | 750 | 800 | 108.58
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | SB:DUNW345_6 | 750 | 800 | 108.54
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | Y50 | 750 | 800 | 107.21
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | Y49 | 750 | 800 | 106.85
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | 24 :EGC 1360 | 750 | 800 | 106.76
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | SB:SPRA345_RNS2 | 750 | 800 | 106.54
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | 17 :SRD1370 | 750 | 800 | 105.49
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | 20 :SRD BUS1 | 750 | 800 | 105.26
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | 31 :GLN 1350 | 750 | 800 | 104.26
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | 36 :GLNNO BUS | 750 | 800 | 104.26
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | 33 :GLN 1340 | 750 | 800 | 104.26
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | 138-366 | 750 | 800 | 104.26
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | Base Case | 750 | 800 | 104.08
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 750 | 800 | 103.96
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | 20 :EGC 1320 | 750 | 800 | 103.57
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | 140:CP-ROS2C | 750 | 800 | 103.49
128662 DOVER 345 128668 DOVER PAR 345 1 | 7 | 138-361 | 138-362 | 750 | 800 | 103.49
128662 DOVER 345 128668 DOVER PAR 345 1 Max | [5 empty] | 121.7
128662 DOVER 345 128668 DOVER PAR 345 2 | 7 | 138-361 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 750 | 800 | 104.17
128662 DOVER 345 128668 DOVER PAR 345 2 | 7 | 138-361 | GEN: OSW Holbrook 1 | 750 | 800 | 104.16
128662 DOVER 345 128668 DOVER PAR 345 2 | 7 | 138-361 | Base Case | 750 | 800 | 103.5
128662 DOVER 345 128668 DOVER PAR 345 2 | 7 | 138-361 | 8 :BRT 1330 | 750 | 800 | 102.79
128662 DOVER 345 128668 DOVER PAR 345 2 | 7 | 138-361 | 1102 BAR_138_OSW2 138 129202 BARRETT1 138 1 | 750 | 800 | 102.73
128662 DOVER 345 128668 DOVER PAR 345 2 | 7 | 138-361 | GEN: OSW Holbrook 2 | 750 | 800 | 102.72
128662 DOVER 345 128668 DOVER PAR 345 2 | 7 | 138-361 | GEN: OSW Barret 2 | 750 | 800 | 102.72
128662 DOVER 345 128668 DOVER PAR 345 2 | 7 | 138-361 | 1103 RUL_138_OSW3 138 129361 RULND RD 138 1 | 750 | 800 | 102.49
128662 DOVER 345 128668 DOVER PAR 345 2 | 7 | 138-361 | GEN: OSW Ruland 3 | 750 | 800 | 102.48
128662 DOVER 345 128668 DOVER PAR 345 2 Max | [5 empty] | 104.17
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | Base Case | 450 | 855 | 173.9
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | Y50 | Base Case | 450 | 855 | 149.46
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | SPRNBRK - W49ST 345 M51 | Base Case | 450 | 855 | 122.65
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | Y50 | 450 | 855 | 120.99
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | Y50 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 450 | 855 | 120.42
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | Y50 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 450 | 855 | 120.42
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | Y50 | E.G.C. 345 kV P.A.R. #2 | 450 | 855 | 120.42
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | SPRNBRK - W49ST 345 M52 | Base Case | 450 | 855 | 120.29
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | LKE SCSS 138/69 Bank #5 | Base Case | 450 | 855 | 118.88
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 450 | 855 | 118.28
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN: OSW Gowanus 1 | Base Case | 450 | 855 | 117.78
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | 138-262 | Base Case | 450 | 855 | 117.78
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN: OSW Farragut 4 | Base Case | 450 | 855 | 117.72
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN: OSW Farragut 3 | Base Case | 450 | 855 | 117.71
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | DUNWOODIE-PLEASANTVILLE W90/W74 | Base Case | 450 | 855 | 117.65
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN: OSW W49 Street 5 | Base Case | 450 | 855 | 117.64
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN: COGEN 2 | Base Case | 450 | 855 | 117.58
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN:ERG7 | Base Case | 450 | 855 | 117.58
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | LINDEN 345/13.8 TR4 | Base Case | 450 | 855 | 117.58
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN: COGEN 1 | Base Case | 450 | 855 | 117.58
128822 E.G.C.-1 345 128825 EGC PAR 345 1 Max | [5 empty] | 173.9
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | EGC REA | Base Case | 450 | 855 | 173.86
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | Base Case | 450 | 855 | 173.86
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | Y50 | Base Case | 450 | 855 | 151.88
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | LKE SCSS 138/69 Bank #5 | Base Case | 450 | 855 | 120.86
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | Y50 | 450 | 855 | 120.81
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | EGC REA | Y50 | 450 | 855 | 120.81
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 450 | 855 | 120.66
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | SPRNBRK - W49ST 345 M51 | Base Case | 450 | 855 | 120.56
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | Y50 | EGC REA | 450 | 855 | 120.52
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | Y50 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 450 | 855 | 120.52
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | Y50 | E.G.C. 345 kV P.A.R. #1 | 450 | 855 | 120.52
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | Y50 | 33 :EGC BUS2 | 450 | 855 | 120.52
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | Y50 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 450 | 855 | 120.52
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | SPRNBRK - W49ST 345 M52 | Base Case | 450 | 855 | 118.19
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | GEN: OSW Astoria 2 | Base Case | 450 | 855 | 118.03
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | NB REA | Base Case | 450 | 855 | 118.01
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | 69-567 | Base Case | 450 | 855 | 117.95
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | 69-371 | Base Case | 450 | 855 | 117.95
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | 69-566 | Base Case | 450 | 855 | 117.95
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | 69-372 | Base Case | 450 | 855 | 117.94
128823 E.G.C.-2 345 128825 EGC PAR 345 1 Max | [5 empty] | 173.86
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | Base Case | 770 | 990 | 182.27
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | NNC-3C | 770 | 990 | 166.35
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | Northport-Norwalk NNC-3C | 770 | 990 | 166.35
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | 72 :NPT BUS1-2 | 770 | 990 | 166.24
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | JAMCA - LKSUCCESS 903 138 | Y50 | 770 | 990 | 159.43
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 903 | Y50 | 770 | 990 | 159.43
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | LKE SCSS 138 kV P.A.R. | Y50 | 770 | 990 | 159.41
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | 901 L&M | 770 | 990 | 155.86
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | JAMCA - VLLYSTRM 901L&M 138 | 770 | 990 | 155.86
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | VLY STRM 138 kV P.A.R. | 770 | 990 | 155.73
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | VLY STRM 138/69 kV Bank #5 | 770 | 990 | 155.7
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | 8 :VST BUS1 | 770 | 990 | 155.6
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | 903 | 770 | 990 | 148.95
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | JAMCA - LKSUCCESS 903 138 | 770 | 990 | 148.95
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | 16 :LKS BUS2 | 770 | 990 | 148.91
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | LKE SCSS 138 kV P.A.R. | 770 | 990 | 148.87
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | GEN: OSW W49 Street 5 | 770 | 990 | 143.47
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | RAINEY - CORONA PAR | 770 | 990 | 143.46
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | SIN:350 Hellgate#4-Astoria E | 770 | 990 | 143.44
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | SIN:340-Hellgate#1-Astoria E | 770 | 990 | 143.43
128824 EGC DUM 345 128825 EGC PAR 345 1 Max | [5 empty] | 182.27
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | Y50 | Base Case | 770 | 990 | 182.47
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | Y50 | NNC-3C | 770 | 990 | 166.35
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | Y50 | Northport-Norwalk NNC-3C | 770 | 990 | 166.35
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | Y50 | 67 :NPT 1300 | 770 | 990 | 166.24
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | Y50 | 72 :NPT BUS1-2 | 770 | 990 | 166.24
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | Y50 | 74 :NPT 1410 | 770 | 990 | 166.23
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | VLY STRM 138/69 kV Bank #5 | P5_SHORERD_138 | 770 | 990 | 159.84
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | JAMCA - LKSUCCESS 903 138 | P5_SHORERD_138 | 770 | 990 | 159.76
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 903 | P5_SHORERD_138 | 770 | 990 | 159.76
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 903 | Y50 | 770 | 990 | 159.75
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | JAMCA - LKSUCCESS 903 138 | Y50 | 770 | 990 | 159.75
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | LKE SCSS 138 kV P.A.R. | P5_SHORERD_138 | 770 | 990 | 159.74
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | LKE SCSS 138 kV P.A.R. | Y50 | 770 | 990 | 159.73
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | P5_SHORERD_138 | 770 | 990 | 159.54
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 901 L&M | P5_SHORERD_138 | 770 | 990 | 159.54
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | VLY STRM 138 kV P.A.R. | P5_SHORERD_138 | 770 | 990 | 159.42
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | JAMCA - LKSUCCESS 903 138 | SB:DUNW345_4 | 770 | 990 | 158.29
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 903 | SB:DUNW345_4 | 770 | 990 | 158.29
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | LKE SCSS 138 kV P.A.R. | SB:DUNW345_4 | 770 | 990 | 158.27
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | JAMCA - LKSUCCESS 903 138 | SB:DUNW345_6 | 770 | 990 | 158.23
128824 EGC DUM 345 128830 HMP HRBR 345 1 Max | [5 empty] | 182.47
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | Y50 | Base Case | 770 | 990 | 183.67
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | Y50 | Northport-Norwalk NNC-3C | 770 | 990 | 166.87
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | Y50 | NNC-3C | 770 | 990 | 166.87
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | Y50 | 74 :NPT 1410 | 770 | 990 | 166.75
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | Y50 | 67 :NPT 1300 | 770 | 990 | 166.75
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | Y50 | 72 :NPT BUS1-2 | 770 | 990 | 166.75
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | VLY STRM 138/69 kV Bank #5 | P5_SHORERD_138 | 770 | 990 | 160.62
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | JAMCA - LKSUCCESS 903 138 | Y50 | 770 | 990 | 160.53
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 903 | Y50 | 770 | 990 | 160.53
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | LKE SCSS 138 kV P.A.R. | Y50 | 770 | 990 | 160.51
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | JAMCA - VLLYSTRM 901L&M 138 | P5_SHORERD_138 | 770 | 990 | 160.49
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 901 L&M | P5_SHORERD_138 | 770 | 990 | 160.49
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | JAMCA - LKSUCCESS 903 138 | P5_SHORERD_138 | 770 | 990 | 160.46
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 903 | P5_SHORERD_138 | 770 | 990 | 160.46
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | LKE SCSS 138 kV P.A.R. | P5_SHORERD_138 | 770 | 990 | 160.45
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | VLY STRM 138 kV P.A.R. | P5_SHORERD_138 | 770 | 990 | 160.37
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 903 | SB:DUNW345_4 | 770 | 990 | 159.1
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | JAMCA - LKSUCCESS 903 138 | SB:DUNW345_4 | 770 | 990 | 159.1
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | LKE SCSS 138 kV P.A.R. | SB:DUNW345_4 | 770 | 990 | 159.08
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 903 | SB:DUNW345_6 | 770 | 990 | 159.03
128830 HMP HRBR 345 147857 DVNPT NK 345 1 Max | [5 empty] | 183.67
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | Y49 | SHORE RD 345/138 Bank #2 | 450 | 563 | 267.59
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | Y49 | 450 | 563 | 263.51
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | Y49 | 21 :SRD BUS2 | 450 | 563 | 244.09
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | Base Case | 450 | 563 | 239.48
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | Y49 | Base Case | 450 | 563 | 218.83
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | EGC REA | 450 | 563 | 208.9
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 33 :EGC BUS2 | 450 | 563 | 208.9
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 450 | 563 | 208.9
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 450 | 563 | 208.9
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | E.G.C. 345 kV P.A.R. #1 | 450 | 563 | 208.89
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | E.G.C. 345 kV P.A.R. #2 | 450 | 563 | 208.7
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 450 | 563 | 208.7
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 450 | 563 | 208.7
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | JAMCA - LKSUCCESS 903 138 | 450 | 563 | 206.49
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 903 | 450 | 563 | 206.49
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | LKE SCSS 138 kV P.A.R. | 450 | 563 | 206.43
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 16 :LKS BUS2 | 450 | 563 | 205.26
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | JAMCA - VLLYSTRM 901L&M 138 | 450 | 563 | 197.39
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 901 L&M | 450 | 563 | 197.39
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | VLY STRM 138 kV P.A.R. | 450 | 563 | 197.25
128835 SHORE RD 345 129293 SHORE RD 138 1 Max | [5 empty] | 267.59
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | Y49 | 540 | 562 | 268.34
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | Y49 | SHORE RD 345/138 Bank #1 | 540 | 562 | 261.94
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | Y49 | 20 :SRD BUS1 | 540 | 562 | 239.99
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | 33 :EGC BUS2 | 540 | 562 | 220.12
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | E.G.C. 345 kV P.A.R. #1 | 540 | 562 | 220.12
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 540 | 562 | 220.12
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | EGC REA | 540 | 562 | 220.12
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 540 | 562 | 220.12
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 540 | 562 | 219.73
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | E.G.C. 345 kV P.A.R. #2 | 540 | 562 | 219.73
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 540 | 562 | 219.73
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | JAMCA - LKSUCCESS 903 138 | 540 | 562 | 219.5
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | 903 | 540 | 562 | 219.5
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | LKE SCSS 138 kV P.A.R. | 540 | 562 | 219.42
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | 16 :LKS BUS2 | 540 | 562 | 218.19
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | Base Case | 540 | 562 | 213.19
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | 901 L&M | 540 | 562 | 212.09
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | JAMCA - VLLYSTRM 901L&M 138 | 540 | 562 | 212.09
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | VLY STRM 138 kV P.A.R. | 540 | 562 | 211.93
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | VLY STRM 138/69 kV Bank #5 | 540 | 562 | 211.23
128835 SHORE RD 345 129294 SHORE RD2 138 2 Max | [5 empty] | 268.34
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-292 | Base Case | 218 | 308 | 447
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Barrett G1-8* | Barrett Bus Tie | 218 | 308 | 408.55
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Barrett G1-8* | 12 :BRT BUS2 | 218 | 308 | 406.25
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GEN: OSW Ruland 3 | Barrett Bus Tie | 218 | 308 | 402.29
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GEN: OSW Holbrook 1 | Barrett Bus Tie | 218 | 308 | 398.18
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-359 | Barrett Bus Tie | 218 | 308 | 397.26
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GEN: OSW Ruland 3 | 12 :BRT BUS2 | 218 | 308 | 396.67
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-459 | Barrett Bus Tie | 218 | 308 | 395.26
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | BELMR 69/34.5 kV BK#5 | Barrett Bus Tie | 218 | 308 | 395.2
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GEN:NRTPTG1 | Barrett Bus Tie | 218 | 308 | 394.75
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Northport Unit 1* | Barrett Bus Tie | 218 | 308 | 394.75
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-574 | Barrett Bus Tie | 218 | 308 | 393.64
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-576 | Barrett Bus Tie | 218 | 308 | 393.26
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GOWANUS 345/138 2TR | Barrett Bus Tie | 218 | 308 | 392.81
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | MOTTHAVEN - RAINEY Q11 345 | Barrett Bus Tie | 218 | 308 | 392.65
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GOWANUS 345/138 14TR | Barrett Bus Tie | 218 | 308 | 392.64
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | S:E13TH_45 | Barrett Bus Tie | 218 | 308 | 392.51
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | S:E13TH_M54 | Barrett Bus Tie | 218 | 308 | 392.49
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GOWANUS-GREENWOOD PAR 3 | Barrett Bus Tie | 218 | 308 | 392.48
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-559 | Barrett Bus Tie | 218 | 308 | 392.48
129202 BARRETT1 138 129233 VLY STRM 138 1 Max | [5 empty] | 447
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-291 | 138-292 | 195 | 275 | 349.85
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | 138-291 | 195 | 275 | 348.96
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | 8 :VST BUS1 | 195 | 275 | 347.88
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 347.87
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 195 | 275 | 347.71
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | Valley Stream Bus Tie | 195 | 275 | 195.24
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Holbrook 1 | Base Case | 195 | 275 | 143.66
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Ruland 3 | Base Case | 195 | 275 | 142.71
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-262 | 138-261 | 195 | 275 | 137.92
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-261 | 138-262 | 195 | 275 | 128.74
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Ruland 3 | 138-262 | 195 | 275 | 128.15
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Holbrook 1 | 138-262 | 195 | 275 | 127.64
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Holbrook 1 | 138-292 | 195 | 275 | 123.29
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Ruland 3 | 138-292 | 195 | 275 | 122.87
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Holbrook 1 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 122.6
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Holbrook 1 | 8 :VST BUS1 | 195 | 275 | 122.52
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Ruland 3 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 121.85
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Holbrook 1 | 1103 RUL_138_OSW3 138 129361 RULND RD 138 1 | 195 | 275 | 121.81
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Holbrook 1 | GEN: OSW Ruland 3 | 195 | 275 | 121.79
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Ruland 3 | 8 :VST BUS1 | 195 | 275 | 121.77
129203 BARRETT2 138 129204 BRRT PH 138 1 Max | [5 empty] | 349.85
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | Base Case | 213 | 305 | 460.56
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | Base Case | 213 | 305 | 450.15
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | 138-291 | 213 | 305 | 380.27
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | BARRETT 138 kV P.A.R. | 213 | 305 | 380.25
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | 138-291 | 213 | 305 | 379.92
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 129204 BRRT PH 138 129276 FREEPORT 138 1 | 213 | 305 | 379.84
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 138-459 | 213 | 305 | 379.84
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | BARRETT 138 kV P.A.R. | 213 | 305 | 373.94
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | 8 :VST BUS1 | 213 | 305 | 373.88
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | VLY STRM 138/69 kV Bank #5 | 213 | 305 | 373.85
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 138-459 | 213 | 305 | 373.59
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 129204 BRRT PH 138 129276 FREEPORT 138 1 | 213 | 305 | 373.59
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | 8 :VST BUS1 | 213 | 305 | 373.59
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | VLY STRM 138/69 kV Bank #5 | 213 | 305 | 373.56
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-261 | 138-291 | 213 | 305 | 371.31
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-461 | 138-291 | 213 | 305 | 365.14
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 138-461 | 213 | 305 | 365.09
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-461 | 8 :VST BUS1 | 213 | 305 | 358.95
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-461 | VLY STRM 138/69 kV Bank #5 | 213 | 305 | 358.91
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 138-461 | 213 | 305 | 358.8
129203 BARRETT2 138 129234 VLY STRM2 138 2 Max | [5 empty] | 460.56
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-291 | 138-292 | 195 | 275 | 342.59
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | 138-291 | 195 | 275 | 341.71
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | 8 :VST BUS1 | 195 | 275 | 341.15
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 341.14
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 195 | 275 | 340.4
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | Valley Stream Bus Tie | 195 | 275 | 189.56
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Holbrook 1 | Base Case | 195 | 275 | 138.98
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Ruland 3 | Base Case | 195 | 275 | 137.68
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-262 | 138-261 | 195 | 275 | 134.02
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-261 | 138-262 | 195 | 275 | 125.12
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Holbrook 1 | 138-262 | 195 | 275 | 123.14
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Ruland 3 | 138-262 | 195 | 275 | 123.09
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Holbrook 1 | 138-292 | 195 | 275 | 119.26
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Holbrook 1 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 118.67
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Holbrook 1 | 8 :VST BUS1 | 195 | 275 | 118.59
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Ruland 3 | 138-292 | 195 | 275 | 118.51
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Ruland 3 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 117.64
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Ruland 3 | 8 :VST BUS1 | 195 | 275 | 117.56
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Holbrook 1 | 1103 RUL_138_OSW3 138 129361 RULND RD 138 1 | 195 | 275 | 116.66
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Holbrook 1 | GEN: OSW Ruland 3 | 195 | 275 | 116.64
129204 BRRT PH 138 129276 FREEPORT 138 1 Max | [5 empty] | 342.59
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y50 | Y49 | 320 | 375 | 250.15
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | Y50 | 320 | 375 | 237.34
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | LKE SCSS 138 kV P.A.R. | Y50 | 320 | 375 | 174.75
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 903 | Y50 | 320 | 375 | 174.42
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | JAMCA - LKSUCCESS 903 138 | Y50 | 320 | 375 | 174.42
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 20 :SRD BUS1 | 320 | 375 | 173.84
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 21 :SRD BUS2 | 320 | 375 | 172.66
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y50 | Northport-Norwalk NNC-3C | 320 | 375 | 166.39
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y50 | NNC-3C | 320 | 375 | 166.39
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y50 | 72 :NPT BUS1-2 | 320 | 375 | 166.19
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 138-365 | 320 | 375 | 151.39
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 35 :GLNSO BUS | 320 | 375 | 151.39
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y50 | 16 :LKS BUS2 | 320 | 375 | 150.39
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 138-366 | 320 | 375 | 150.09
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 36 :GLNNO BUS | 320 | 375 | 150.09
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y50 | LKE SCSS 138 kV P.A.R. | 320 | 375 | 150.08
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 320 | 375 | 149.31
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y50 | JAMCA - LKSUCCESS 903 138 | 320 | 375 | 149.18
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y50 | 903 | 320 | 375 | 149.18
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 320 | 375 | 148.05
129233 VLY STRM 138 129235 V STRM P 138 1 Max | [5 empty] | 250.15
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | Base Case | 194 | 284 | 447.91
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 1103 RUL_138_OSW3 138 129361 RULND RD 138 1 | 194 | 284 | 346.16
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | GEN: OSW Ruland 3 | 194 | 284 | 346.1
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 194 | 284 | 344.02
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | GEN: OSW Holbrook 1 | 194 | 284 | 343.95
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | VLY STRM 138 kV P.A.R. | 194 | 284 | 330.19
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | JAMCA - VLLYSTRM 901L&M 138 | 194 | 284 | 330.14
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 901 L&M | 194 | 284 | 330.14
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | VLY STRM 138/69 kV Bank #5 | 194 | 284 | 327.07
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 8 :VST BUS1 | 194 | 284 | 326.52
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | VSBUS2 | 194 | 284 | 322.64
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | VLY STRM 138/69 Bank #6 | 194 | 284 | 320.87
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | VS BUS 1 | 194 | 284 | 320.55
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | Barrett Bus Tie | 194 | 284 | 319.33
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 129527 VLYSTRM1 69.0 129233 VLY STRM 138 1 | 194 | 284 | 318.81
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | LKS BUS1 | 194 | 284 | 316.5
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 129202 BARRETT1 138 129205 BRTGT1-8 138 1 | 194 | 284 | 316.29
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | BRT69KV | 194 | 284 | 316.25
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | Northport Unit 1* | 194 | 284 | 316.22
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | GEN:NRTPTG1 | 194 | 284 | 316.22
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 Max | [5 empty] | 447.91
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | Base Case | 280 | 442 | 268.84
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 1103 RUL_138_OSW3 138 129361 RULND RD 138 1 | 280 | 442 | 191.77
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | GEN: OSW Ruland 3 | 280 | 442 | 191.74
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 280 | 442 | 190.39
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | GEN: OSW Holbrook 1 | 280 | 442 | 190.35
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | VLY STRM 138/69 kV Bank #5 | 280 | 442 | 184.44
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | VLY STRM 138 kV P.A.R. | 280 | 442 | 184.2
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 901 L&M | 280 | 442 | 184.19
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | JAMCA - VLLYSTRM 901L&M 138 | 280 | 442 | 184.19
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 8 :VST BUS1 | 280 | 442 | 184.11
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | VSBUS2 | 280 | 442 | 180.88
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | VLY STRM 138/69 Bank #6 | 280 | 442 | 179.58
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | VS BUS 1 | 280 | 442 | 179.39
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 129527 VLYSTRM1 69.0 129233 VLY STRM 138 1 | 280 | 442 | 178.28
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | Barrett Bus Tie | 280 | 442 | 177.97
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | BRT69KV | 280 | 442 | 177.12
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 129202 BARRETT1 138 129205 BRTGT1-8 138 1 | 280 | 442 | 176.85
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | LKS BUS1 | 280 | 442 | 176.67
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | Barrett G1-8* | 280 | 442 | 176.32
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 129205 BRTGT1-8 138 129501 BARRETT 69.0 1 | 280 | 442 | 176.32
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 Max | [5 empty] | 268.84
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-366 | 21 :SRD BUS2 | 260 | 380 | 136.72
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-368 | Y50 | 260 | 380 | 127.97
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-366 | Shore Road Bus Tie | 260 | 380 | 119.73
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | Y49 | Y50 | 260 | 380 | 119.29
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #1 | Shore Road Bus Tie | 260 | 380 | 108.3
129247 L SUCS 138 129293 SHORE RD 138 1 Max | [5 empty] | 136.72
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | Y49 | Y50 | 285 | 368 | 286.86
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | VLY STRM 138 kV P.A.R. | Y50 | 285 | 368 | 233.42
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Y50 | 285 | 368 | 233.16
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Y50 | 285 | 368 | 232.73
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 901 L&M | Y50 | 285 | 368 | 232.73
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | EGC REA | Y50 | 285 | 368 | 211.49
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | E.G.C. 345 kV P.A.R. #1 | Y50 | 285 | 368 | 211.49
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | E.G.C. 345 kV P.A.R. #2 | Y50 | 285 | 368 | 211.22
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | NNC-3C | Y50 | 285 | 368 | 210.21
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | Northport-Norwalk NNC-3C | Y50 | 285 | 368 | 210.21
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-365 | Y50 | 285 | 368 | 208.03
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-366 | Y50 | 285 | 368 | 199.64
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-361 | Y50 | 285 | 368 | 198.4
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-364 | Y50 | 285 | 368 | 198.23
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-362 | Y50 | 285 | 368 | 198.11
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-363 | Y50 | 285 | 368 | 190.93
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-467 | Y50 | 285 | 368 | 189.01
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | GEN: OSW W49 Street 5 | Y50 | 285 | 368 | 188.82
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-463 | Y50 | 285 | 368 | 188.26
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | GEN: OSW Gowanus 1 | Y50 | 285 | 368 | 187.49
129248 L SUCS2 138 129249 L SUCSPH 138 1 Max | [5 empty] | 286.86
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-365 | 20 :SRD BUS1 | 260 | 380 | 141.12
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | LKE SCSS 138/69 Bank #5 | Y50 | 260 | 380 | 137.78
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-367 | Y50 | 260 | 380 | 128.14
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | Y49 | Y50 | 260 | 380 | 120.62
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-365 | Shore Road Bus Tie | 260 | 380 | 119.25
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #2 | Shore Road Bus Tie | 260 | 380 | 104.82
129248 L SUCS2 138 129294 SHORE RD2 138 2 Max | [5 empty] | 141.12
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 36 :GLNNO BUS | 320 | 352 | 357.1
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 138-366 | 320 | 352 | 357.1
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | Y49 | 320 | 352 | 353.2
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 320 | 352 | 351.45
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 138-362 | 320 | 352 | 346.98
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 320 | 352 | 346.06
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 138-364 | 320 | 352 | 346.06
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 37 :GLNGT BUS | 320 | 352 | 346.06
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | Y49 | 320 | 352 | 341.16
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-364 | Y49 | 320 | 352 | 340.26
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 20 :SRD BUS1 | 320 | 352 | 313.92
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | Base Case | 320 | 352 | 287.38
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | VLY STRM 138/69 kV Bank #5 | 320 | 352 | 285.22
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | 8 :VST BUS1 | 320 | 352 | 285.01
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | E.G.C. 345 kV P.A.R. #2 | 320 | 352 | 282.79
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 320 | 352 | 282.72
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 320 | 352 | 282.72
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | E.G.C. 345 kV P.A.R. #1 | 320 | 352 | 282.33
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 320 | 352 | 282.27
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | EGC REA | 320 | 352 | 282.27
129265 CARLE PL 138 129270 E.G.C. 138 1 Max | [5 empty] | 357.1
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 36 :GLNNO BUS | 325 | 388 | 320.67
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 138-366 | 325 | 388 | 320.67
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | Y49 | 325 | 388 | 317.13
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 325 | 388 | 315.54
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 138-362 | 325 | 388 | 311.49
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 37 :GLNGT BUS | 325 | 388 | 310.65
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 325 | 388 | 310.65
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 138-364 | 325 | 388 | 310.65
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | Y49 | 325 | 388 | 306.22
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-364 | Y49 | 325 | 388 | 305.4
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 20 :SRD BUS1 | 325 | 388 | 281.56
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | Base Case | 325 | 388 | 279.12
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | Base Case | 325 | 388 | 267.92
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-364 | Base Case | 325 | 388 | 266.95
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | Base Case | 325 | 388 | 256.83
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | VLY STRM 138/69 kV Bank #5 | 325 | 388 | 255.5
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | 8 :VST BUS1 | 325 | 388 | 255.31
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 325 | 388 | 253.24
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 325 | 388 | 253.24
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | E.G.C. 345 kV P.A.R. #2 | 325 | 388 | 253.19
129265 CARLE PL 138 129283 GLNWD SO 138 1 Max | [5 empty] | 320.67
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | Y50 | 450 | 585 | 190.25
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | Y50 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 450 | 585 | 190.1
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | Y50 | E.G.C. 345 kV P.A.R. #2 | 450 | 585 | 190.1
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | Y50 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 450 | 585 | 190.1
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | Base Case | 450 | 585 | 175.78
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | Y50 | Base Case | 450 | 585 | 158.55
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 20 :SRD BUS1 | 450 | 585 | 158.28
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 21 :SRD BUS2 | 450 | 585 | 157.54
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | SHORE RD 345/138 Bank #1 | 450 | 585 | 149.53
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | SHORE RD 345/138 Bank #2 | 450 | 585 | 148.23
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 35 :GLNSO BUS | 450 | 585 | 147.63
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 138-365 | 450 | 585 | 147.63
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 36 :GLNNO BUS | 450 | 585 | 147.32
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 138-366 | 450 | 585 | 147.32
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 450 | 585 | 147.16
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 450 | 585 | 146.83
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 138-361 | 450 | 585 | 146.75
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 138-363 | 450 | 585 | 146.53
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 138-362 | 450 | 585 | 146.28
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 138-364 | 450 | 585 | 146.16
129270 E.G.C. 138 128822 E.G.C.-1 345 1 Max | [5 empty] | 190.25
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | Y49 | 320 | 352 | 355.54
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 35 :GLNSO BUS | 320 | 352 | 350.53
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-365 | 320 | 352 | 350.53
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 320 | 352 | 344.92
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-361 | 320 | 352 | 341.94
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-363 | 320 | 352 | 340.3
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-361 | Y49 | 320 | 352 | 336.95
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 21 :SRD BUS2 | 320 | 352 | 312.09
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-363 | Y49 | 320 | 352 | 301.97
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | Base Case | 320 | 352 | 293.09
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | VLY STRM 138/69 kV Bank #5 | 320 | 352 | 287.38
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | 33 :EGC BUS2 | 320 | 352 | 287.34
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | E.G.C. 345 kV P.A.R. #1 | 320 | 352 | 287.34
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 320 | 352 | 287.34
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 320 | 352 | 287.34
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | EGC REA | 320 | 352 | 287.34
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | 8 :VST BUS1 | 320 | 352 | 287.17
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 320 | 352 | 287.08
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | E.G.C. 345 kV P.A.R. #2 | 320 | 352 | 287.08
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 320 | 352 | 287.08
129270 E.G.C. 138 129288 ROSLYN 138 1 Max | [5 empty] | 355.54
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | 138-463 | 194 | 284 | 287.29
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-463 | 138-465 | 194 | 284 | 285.64
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | Base Case | 194 | 284 | 282.18
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-463 | Base Case | 194 | 284 | 279.36
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-467 | Base Case | 194 | 284 | 252.8
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-463 | 138-467 | 194 | 284 | 252
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | 138-467 | 194 | 284 | 250.32
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-467 | 138-463 | 194 | 284 | 249.58
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-467 | 138-465 | 194 | 284 | 246.46
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-291 | 138-292 | 194 | 284 | 220.25
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 138-291 | 194 | 284 | 220.17
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 8 :VST BUS1 | 194 | 284 | 219.45
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 194 | 284 | 219.4
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 194 | 284 | 218.69
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 69-533 | Base Case | 194 | 284 | 217.93
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 69-532 | Base Case | 194 | 284 | 217.47
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 69-531 | Base Case | 194 | 284 | 217.07
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | BELMR 69/34.5 kV BK#5 | Base Case | 194 | 284 | 215.68
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | NB REA | Base Case | 194 | 284 | 214.89
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | NEWBRGE 138/69 Bank #6 | Base Case | 194 | 284 | 214.88
129270 E.G.C. 138 129310 NEWBRGE 138 1 Max | [5 empty] | 287.29
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | 138-463 | 216 | 306 | 260.27
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-463 | 138-462 | 216 | 306 | 257.38
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | Base Case | 216 | 306 | 248.69
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-463 | Base Case | 216 | 306 | 242.11
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | 138-467 | 216 | 306 | 230.65
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-467 | 138-462 | 216 | 306 | 225.93
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-463 | 138-467 | 216 | 306 | 225.83
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-467 | 138-463 | 216 | 306 | 223.66
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-467 | Base Case | 216 | 306 | 219.61
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-291 | 138-292 | 216 | 306 | 196.99
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-292 | 138-291 | 216 | 306 | 196.92
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-292 | 8 :VST BUS1 | 216 | 306 | 196.36
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 216 | 306 | 196.31
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 216 | 306 | 195.57
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 69-533 | Base Case | 216 | 306 | 189.35
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 69-532 | Base Case | 216 | 306 | 188.95
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 69-531 | Base Case | 216 | 306 | 188.6
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | BELMR 69/34.5 kV BK#5 | Base Case | 216 | 306 | 187.35
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | NB REA | Base Case | 216 | 306 | 186.77
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | NEWBRGE 138/69 Bank #6 | Base Case | 216 | 306 | 186.59
129270 E.G.C. 138 129310 NEWBRGE 138 3 Max | [5 empty] | 260.27
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | Y50 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 450 | 585 | 190.72
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | Y50 | E.G.C. 345 kV P.A.R. #1 | 450 | 585 | 190.72
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | Y50 | EGC REA | 450 | 585 | 190.72
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | Y50 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 450 | 585 | 190.72
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | Y50 | 33 :EGC BUS2 | 450 | 585 | 190.72
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | Y50 | 450 | 585 | 190.04
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | Y50 | 450 | 585 | 190.04
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | Base Case | 450 | 585 | 175.77
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | Base Case | 450 | 585 | 175.77
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | Y50 | Base Case | 450 | 585 | 161.29
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | 20 :SRD BUS1 | 450 | 585 | 158.18
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | 20 :SRD BUS1 | 450 | 585 | 158.18
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | 21 :SRD BUS2 | 450 | 585 | 157.44
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | 21 :SRD BUS2 | 450 | 585 | 157.43
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | SHORE RD 345/138 Bank #1 | 450 | 585 | 149.47
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | SHORE RD 345/138 Bank #1 | 450 | 585 | 149.47
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | SHORE RD 345/138 Bank #2 | 450 | 585 | 148.18
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | SHORE RD 345/138 Bank #2 | 450 | 585 | 148.18
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | 138-365 | 450 | 585 | 147.57
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | 35 :GLNSO BUS | 450 | 585 | 147.57
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 Max | [5 empty] | 190.72
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | 138-465 | 210 | 302 | 268.99
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-465 | 138-462 | 210 | 302 | 267.57
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | Base Case | 210 | 302 | 256.32
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-465 | Base Case | 210 | 302 | 252.1
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | 138-467 | 210 | 302 | 237.2
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-467 | 138-462 | 210 | 302 | 231.97
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-465 | 138-467 | 210 | 302 | 230.74
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-467 | Base Case | 210 | 302 | 228.51
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-467 | 138-465 | 210 | 302 | 226.9
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-291 | 138-292 | 210 | 302 | 204.71
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-292 | 138-291 | 210 | 302 | 204.63
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-292 | 8 :VST BUS1 | 210 | 302 | 203.78
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 210 | 302 | 203.72
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 210 | 302 | 202.53
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 69-533 | Base Case | 210 | 302 | 194.8
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 69-532 | Base Case | 210 | 302 | 194.38
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 69-531 | Base Case | 210 | 302 | 194.03
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | BELMR 69/34.5 kV BK#5 | Base Case | 210 | 302 | 192.54
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | NB REA | Base Case | 210 | 302 | 192.3
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | NEWBRGE 138/69 Bank #6 | Base Case | 210 | 302 | 191.99
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 Max | [5 empty] | 268.99
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-462 | Base Case | 270 | 474 | 147.36
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-463 | Base Case | 270 | 474 | 145.46
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-465 | Base Case | 270 | 474 | 145.15
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-462 | 138-465 | 270 | 474 | 126.57
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-462 | 138-463 | 270 | 474 | 126.38
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-465 | 138-462 | 270 | 474 | 125.9
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-465 | 138-463 | 270 | 474 | 124.93
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-463 | 138-462 | 270 | 474 | 124.76
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-463 | 138-465 | 270 | 474 | 124.05
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 69-533 | Base Case | 270 | 474 | 112.31
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 69-532 | Base Case | 270 | 474 | 112.07
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 69-531 | Base Case | 270 | 474 | 111.87
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | BELMR 69/34.5 kV BK#5 | Base Case | 270 | 474 | 111.02
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | NB REA | Base Case | 270 | 474 | 110.87
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | NEWBRGE 138/69 Bank #6 | Base Case | 270 | 474 | 110.67
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | GEN: OSW W49 Street 5 | Base Case | 270 | 474 | 110.41
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | GEN: OSW Farragut 4 | Base Case | 270 | 474 | 110.4
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | GEN: OSW Farragut 3 | Base Case | 270 | 474 | 110.4
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | GEN: OSW Astoria 2 | Base Case | 270 | 474 | 110.28
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-292 | Base Case | 270 | 474 | 110.24
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 Max | [5 empty] | 147.36
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-291 | 138-292 | 229 | 299 | 298.95
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 138-291 | 229 | 299 | 298.14
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 8 :VST BUS1 | 229 | 299 | 297.61
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 229 | 299 | 297.6
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 229 | 299 | 296.95
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | Valley Stream Bus Tie | 229 | 299 | 158.24
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-262 | 138-261 | 229 | 299 | 107.13
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW Holbrook 2 | Base Case | 229 | 299 | 102.95
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW Barret 2 | Base Case | 229 | 299 | 102.95
129276 FREEPORT 138 129310 NEWBRGE 138 1 Max | [5 empty] | 298.95
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | Y49 | 351 | 388 | 320.69
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 138-365 | 351 | 388 | 316.14
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 35 :GLNSO BUS | 351 | 388 | 316.14
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 351 | 388 | 311.06
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 138-361 | 351 | 388 | 308.35
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 138-363 | 351 | 388 | 306.87
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-361 | Y49 | 351 | 388 | 303.83
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 21 :SRD BUS2 | 351 | 388 | 281.25
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-363 | Y49 | 351 | 388 | 272.14
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | Base Case | 351 | 388 | 265.23
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | VLY STRM 138/69 kV Bank #5 | 351 | 388 | 258.91
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | E.G.C. 345 kV P.A.R. #1 | 351 | 388 | 258.87
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | EGC REA | 351 | 388 | 258.87
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 351 | 388 | 258.87
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | 33 :EGC BUS2 | 351 | 388 | 258.87
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 351 | 388 | 258.87
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | 8 :VST BUS1 | 351 | 388 | 258.72
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 351 | 388 | 258.64
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | E.G.C. 345 kV P.A.R. #2 | 351 | 388 | 258.64
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 351 | 388 | 258.64
129281 GLNWD GT 138 129282 GLNWD NO 138 1 Max | [5 empty] | 320.69
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | Y49 | 351 | 388 | 320.7
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-365 | 351 | 388 | 316.15
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 35 :GLNSO BUS | 351 | 388 | 316.15
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 351 | 388 | 311.06
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-361 | 351 | 388 | 308.36
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-363 | 351 | 388 | 306.88
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-361 | Y49 | 351 | 388 | 303.84
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 21 :SRD BUS2 | 351 | 388 | 281.25
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-363 | Y49 | 351 | 388 | 272.15
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | Base Case | 351 | 388 | 265.24
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | VLY STRM 138/69 kV Bank #5 | 351 | 388 | 258.93
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 351 | 388 | 258.89
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | 33 :EGC BUS2 | 351 | 388 | 258.89
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | EGC REA | 351 | 388 | 258.89
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | E.G.C. 345 kV P.A.R. #1 | 351 | 388 | 258.89
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 351 | 388 | 258.89
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | 8 :VST BUS1 | 351 | 388 | 258.74
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 351 | 388 | 258.65
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | E.G.C. 345 kV P.A.R. #2 | 351 | 388 | 258.65
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 351 | 388 | 258.65
129281 GLNWD GT 138 129288 ROSLYN 138 1 Max | [5 empty] | 320.7
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | Y49 | 381 | 446 | 318.96
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 138-365 | 381 | 446 | 315.57
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 35 :GLNSO BUS | 381 | 446 | 315.57
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 381 | 446 | 315.42
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 138-361 | 381 | 446 | 300.33
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 138-363 | 381 | 446 | 298.89
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-361 | Y49 | 381 | 446 | 295.51
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 21 :SRD BUS2 | 381 | 446 | 285.53
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | Base Case | 381 | 446 | 279.89
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-363 | Y49 | 381 | 446 | 264.04
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | LKS BUS2 | 381 | 446 | 259.2
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | 33 :EGC BUS2 | 381 | 446 | 257.8
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | EGC REA | 381 | 446 | 257.8
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 381 | 446 | 257.8
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | E.G.C. 345 kV P.A.R. #1 | 381 | 446 | 257.8
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 381 | 446 | 257.8
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 381 | 446 | 257.6
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 381 | 446 | 257.6
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | E.G.C. 345 kV P.A.R. #2 | 381 | 446 | 257.6
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | VLY STRM 138/69 kV Bank #5 | 381 | 446 | 256.79
129282 GLNWD NO 138 129293 SHORE RD 138 1 Max | [5 empty] | 318.96
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 138-366 | 351 | 388 | 364.78
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 36 :GLNNO BUS | 351 | 388 | 364.78
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 351 | 388 | 364.39
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | Y49 | 351 | 388 | 359.45
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 138-362 | 351 | 388 | 345.76
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 138-364 | 351 | 388 | 344.84
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 37 :GLNGT BUS | 351 | 388 | 344.84
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 351 | 388 | 344.84
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | Y49 | 351 | 388 | 339.42
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-364 | Y49 | 351 | 388 | 338.52
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 20 :SRD BUS1 | 351 | 388 | 325.47
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | Base Case | 351 | 388 | 293.48
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | VLY STRM 138/69 kV Bank #5 | 351 | 388 | 288.83
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | 8 :VST BUS1 | 351 | 388 | 288.61
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | LKS BUS2 | 351 | 388 | 287.59
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 351 | 388 | 287.42
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 351 | 388 | 287.42
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | E.G.C. 345 kV P.A.R. #2 | 351 | 388 | 287.4
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | 33 :EGC BUS2 | 351 | 388 | 286.93
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | EGC REA | 351 | 388 | 286.93
129283 GLNWD SO 138 129294 SHORE RD2 138 1 Max | [5 empty] | 364.78
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | SHORE RD 345/138 Bank #2 | Base Case | 365 | 602 | 118.4
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 138-366 | Base Case | 365 | 602 | 113.89
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 138-364 | Base Case | 365 | 602 | 113.34
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 138-362 | Base Case | 365 | 602 | 113.26
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 138-361 | Base Case | 365 | 602 | 113.12
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 69-533 | Base Case | 365 | 602 | 104.02
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 69-532 | Base Case | 365 | 602 | 103.44
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 69-531 | Base Case | 365 | 602 | 102.93
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW Barret 2 | Base Case | 365 | 602 | 101.51
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW Holbrook 2 | Base Case | 365 | 602 | 101.51
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 138-564 | Base Case | 365 | 602 | 101.27
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 138-563 | Base Case | 365 | 602 | 101.19
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 138-561 | Base Case | 365 | 602 | 101.03
129305 LCST GRV 138 129310 NEWBRGE 138 1 Max | [5 empty] | 118.4
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | 138-562 | 302 | 331 | 166.82
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | 138-567 | 302 | 331 | 166.76
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | 138-559 | 302 | 331 | 141.32
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-559 | 138-562 | 302 | 331 | 141.07
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | 138-559 | 302 | 331 | 140.74
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-559 | 138-567 | 302 | 331 | 140.5
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | 138-558 | 302 | 331 | 140.5
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-558 | 138-562 | 302 | 331 | 140.21
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | 138-558 | 302 | 331 | 139.9
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-558 | 138-567 | 302 | 331 | 139.62
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-562 | 302 | 331 | 138.7
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-567 | 302 | 331 | 138.18
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | 75 :NPT BUS3 | 302 | 331 | 136.24
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | NRTHPRT P.A.R. #2 (Bus) | 302 | 331 | 136.23
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | 74 :NPT BUS2 | 302 | 331 | 136.14
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | NRTHPRT P.A.R. #2 (Bus) | 302 | 331 | 135.73
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | 75 :NPT BUS3 | 302 | 331 | 135.71
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | 74 :NPT BUS2 | 302 | 331 | 135.63
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-564 | 138-562 | 302 | 331 | 134.88
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-564 | 138-567 | 302 | 331 | 134.38
129310 NEWBRGE 138 129361 RULND RD 138 1 Max | [5 empty] | 166.82
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | 138-561 | 302 | 331 | 166.82
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | 138-567 | 302 | 331 | 166.52
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | 138-559 | 302 | 331 | 141.28
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-559 | 138-561 | 302 | 331 | 141.07
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | 138-559 | 302 | 331 | 140.73
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-559 | 138-567 | 302 | 331 | 140.49
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | 138-558 | 302 | 331 | 140.46
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-558 | 138-561 | 302 | 331 | 140.2
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | 138-558 | 302 | 331 | 139.89
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-558 | 138-567 | 302 | 331 | 139.61
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-561 | 302 | 331 | 138.69
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-567 | 302 | 331 | 138.17
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | 75 :NPT BUS3 | 302 | 331 | 136.21
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | NRTHPRT P.A.R. #2 (Bus) | 302 | 331 | 136.2
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | 74 :NPT BUS2 | 302 | 331 | 136.11
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | NRTHPRT P.A.R. #2 (Bus) | 302 | 331 | 135.72
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | 75 :NPT BUS3 | 302 | 331 | 135.7
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | 74 :NPT BUS2 | 302 | 331 | 135.62
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-564 | 138-561 | 302 | 331 | 134.88
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-564 | 138-567 | 302 | 331 | 134.37
129310 NEWBRGE 138 129361 RULND RD 138 2 Max | [5 empty] | 166.82
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-562 | Base Case | 259 | 388 | 146.61
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-561 | Base Case | 259 | 388 | 146.41
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-562 | 138-561 | 259 | 388 | 140.77
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-561 | 138-562 | 259 | 388 | 140.57
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-559 | Base Case | 259 | 388 | 133.11
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | NRTHPRT P.A.R. #2 (Bus) | Base Case | 259 | 388 | 132.56
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-558 | Base Case | 259 | 388 | 132.27
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-564 | Base Case | 259 | 388 | 127.67
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-563 | Base Case | 259 | 388 | 126.86
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | ELWOOD 138/69 kV Bank #3 | Base Case | 259 | 388 | 121.55
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-674 | Base Case | 259 | 388 | 121.21
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-675 | Base Case | 259 | 388 | 120.55
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-676 | Base Case | 259 | 388 | 120.38
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-562 | 138-559 | 259 | 388 | 118.77
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-561 | 138-559 | 259 | 388 | 118.75
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-559 | 138-561 | 259 | 388 | 118.56
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-559 | 138-562 | 259 | 388 | 118.56
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-678 | Base Case | 259 | 388 | 118.51
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-673 | Base Case | 259 | 388 | 118.35
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-681 | Base Case | 259 | 388 | 118.18
129310 NEWBRGE 138 129361 RULND RD 138 3 Max | [5 empty] | 146.61
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | SHORE RD 345/138 Bank #2 | ELWOOD 138/69 kV Bank #3 | 265 | 368 | 120.22
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-361 | ELWOOD 138/69 kV Bank #3 | 265 | 368 | 120.22
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-361 | 80 :ELD BUS1 | 265 | 368 | 120.22
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | SHORE RD 345/138 Bank #2 | 80 :ELD BUS1 | 265 | 368 | 120.22
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-364 | ELWOOD 138/69 kV Bank #3 | 265 | 368 | 120.18
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-364 | 80 :ELD BUS1 | 265 | 368 | 120.18
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-362 | 80 :ELD BUS1 | 265 | 368 | 120.15
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-362 | ELWOOD 138/69 kV Bank #3 | 265 | 368 | 120.15
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-366 | ELWOOD 138/69 kV Bank #3 | 265 | 368 | 119.07
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-366 | 80 :ELD BUS1 | 265 | 368 | 119.07
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | SHORE RD 345/138 Bank #2 | 138-674 | 265 | 368 | 118.45
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-361 | 138-674 | 265 | 368 | 118.4
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-364 | 138-674 | 265 | 368 | 118.38
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-362 | 138-674 | 265 | 368 | 118.36
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-361 | 138-681 | 265 | 368 | 117.36
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | SHORE RD 345/138 Bank #2 | 138-681 | 265 | 368 | 117.34
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-364 | 138-681 | 265 | 368 | 117.32
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-362 | 138-681 | 265 | 368 | 117.28
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-366 | 138-674 | 265 | 368 | 117.27
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | SHORE RD 345/138 Bank #2 | 138-675 | 265 | 368 | 116.72
129315 SYOSSET 138 129333 GRENLAWN 138 1 Max | [5 empty] | 120.22
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 138-678 | 265 | 368 | 115.62
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 76 :NPT BUS4 | 265 | 368 | 115.62
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 81 :ELD BUS2 | 265 | 368 | 115.62
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-361 | 81 :ELD BUS2 | 265 | 368 | 115.62
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-362 | 81 :ELD BUS2 | 265 | 368 | 115.61
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-364 | 81 :ELD BUS2 | 265 | 368 | 115.6
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-362 | 76 :NPT BUS4 | 265 | 368 | 115.58
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-362 | 138-678 | 265 | 368 | 115.58
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-361 | 138-678 | 265 | 368 | 115.57
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-361 | 76 :NPT BUS4 | 265 | 368 | 115.57
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-364 | 138-678 | 265 | 368 | 115.56
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-364 | 76 :NPT BUS4 | 265 | 368 | 115.56
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-361 | 138-673 | 265 | 368 | 115.19
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-364 | 138-673 | 265 | 368 | 115.16
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-362 | 138-673 | 265 | 368 | 115.15
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 138-673 | 265 | 368 | 115.15
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-366 | 81 :ELD BUS2 | 265 | 368 | 114.38
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-366 | 76 :NPT BUS4 | 265 | 368 | 114.32
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-366 | 138-678 | 265 | 368 | 114.32
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-366 | 138-673 | 265 | 368 | 113.98
129315 SYOSSET 138 129351 OAKWOOD 138 1 Max | [5 empty] | 115.62
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | HOLBROOK 138/69 Bank #2 | PILGRIM 138/69 Bank #4 | 215 | 288 | 119.72
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 68 : PIL BUS2 | 215 | 288 | 119.72
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-882 | 68 : PIL BUS2 | 215 | 288 | 119.72
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-882 | PILGRIM 138/69 Bank #4 | 215 | 288 | 119.72
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-881 NEW | 215 | 288 | 117.24
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-882 | 138-881 NEW | 215 | 288 | 117.24
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-881 | 215 | 288 | 114.68
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-882 | 138-881 | 215 | 288 | 114.68
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | PILGRIM 138/69 Bank #4 | 138-882 | 215 | 288 | 110.05
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | PILGRIM 138/69 Bank #4 | 108:HOL BUS2 | 215 | 288 | 110.05
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | PILGRIM 138/69 Bank #4 | HOLBROOK 138/69 Bank #2 | 215 | 288 | 110.05
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | PILGRIM 138/69 Bank #4 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 215 | 288 | 108.88
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 NEW | 138-882 | 215 | 288 | 106.31
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 NEW | 108:HOL BUS2 | 215 | 288 | 106.31
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 NEW | HOLBROOK 138/69 Bank #2 | 215 | 288 | 106.31
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | SHORE RD 345/138 Bank #2 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 215 | 288 | 105.46
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | SHORE RD 345/138 Bank #2 | GEN: OSW Holbrook 1 | 215 | 288 | 105.34
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-362 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 215 | 288 | 105.22
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-364 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 215 | 288 | 105.17
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-362 | GEN: OSW Holbrook 1 | 215 | 288 | 105.11
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 Max | [5 empty] | 119.72
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-875 | 572 | 617 | 105.76
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-882 | 138-875 | 572 | 617 | 105.76
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-882 | 138-883 | 572 | 617 | 104.53
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-883 | 572 | 617 | 104.53
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 108:HOL BUS2 | 572 | 617 | 101.87
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | C.ISLIP 138/69 Bank #3 | HOLBROOK 138/69 Bank #2 | 572 | 617 | 101.87
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 138-882 | 572 | 617 | 101.87
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-882 | C.ISLIP 138/69 Bank #3 | 572 | 617 | 101.46
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-882 | 86 :CISL BUS3 | 572 | 617 | 101.46
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | C.ISLIP 138/69 Bank #3 | 572 | 617 | 101.46
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 86 :CISL BUS3 | 572 | 617 | 101.46
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 572 | 617 | 101.16
129339 KINGS 138 129355 PILGRIM 138 1 Max | [5 empty] | 105.76
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-875 | 577 | 618 | 107.43
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-882 | 138-875 | 577 | 618 | 107.43
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-883 | 577 | 618 | 106.2
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-882 | 138-883 | 577 | 618 | 106.2
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 108:HOL BUS2 | 577 | 618 | 103.55
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 138-882 | 577 | 618 | 103.55
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | HOLBROOK 138/69 Bank #2 | 577 | 618 | 103.55
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-882 | C.ISLIP 138/69 Bank #3 | 577 | 618 | 103.13
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-882 | 86 :CISL BUS3 | 577 | 618 | 103.13
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 86 :CISL BUS3 | 577 | 618 | 103.13
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | C.ISLIP 138/69 Bank #3 | 577 | 618 | 103.13
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 577 | 618 | 102.83
129339 KINGS 138 129428 WEST BUS 138 1 Max | [5 empty] | 107.43
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-362 | Base Case | 517 | 591 | 114.79
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | SHORE RD 345/138 Bank #2 | Base Case | 517 | 591 | 114.77
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-364 | Base Case | 517 | 591 | 114.75
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-361 | Base Case | 517 | 591 | 114.71
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-366 | Base Case | 517 | 591 | 113.64
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | SHORE RD 345/138 Bank #2 | 1102 BAR_138_OSW2 138 129202 BARRETT1 138 1 | 517 | 591 | 113.52
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | SHORE RD 345/138 Bank #2 | GEN: OSW Barret 2 | 517 | 591 | 113.49
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | SHORE RD 345/138 Bank #2 | GEN: OSW Holbrook 2 | 517 | 591 | 113.49
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-362 | 1102 BAR_138_OSW2 138 129202 BARRETT1 138 1 | 517 | 591 | 112.92
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-362 | GEN: OSW Holbrook 2 | 517 | 591 | 112.89
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-362 | GEN: OSW Barret 2 | 517 | 591 | 112.89
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-364 | 1102 BAR_138_OSW2 138 129202 BARRETT1 138 1 | 517 | 591 | 112.82
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-364 | GEN: OSW Barret 2 | 517 | 591 | 112.79
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-364 | GEN: OSW Holbrook 2 | 517 | 591 | 112.79
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-361 | 1102 BAR_138_OSW2 138 129202 BARRETT1 138 1 | 517 | 591 | 112.56
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-361 | GEN: OSW Holbrook 2 | 517 | 591 | 112.53
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-361 | GEN: OSW Barret 2 | 517 | 591 | 112.53
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-366 | 1102 BAR_138_OSW2 138 129202 BARRETT1 138 1 | 517 | 591 | 112.13
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-366 | GEN: OSW Holbrook 2 | 517 | 591 | 112.11
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-366 | GEN: OSW Barret 2 | 517 | 591 | 112.11
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 Max | [5 empty] | 114.79
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | Y49 | 465 | 599 | 160.33
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | Base Case | 465 | 599 | 117.34
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | E.G.C. 345 kV P.A.R. #1 | 465 | 599 | 108.23
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | EGC REA | 465 | 599 | 108.23
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 465 | 599 | 108.23
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 465 | 599 | 108.23
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | 33 :EGC BUS2 | 465 | 599 | 108.23
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 465 | 599 | 108.21
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 465 | 599 | 108.21
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | E.G.C. 345 kV P.A.R. #2 | 465 | 599 | 108.21
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | VLY STRM 138/69 kV Bank #5 | 465 | 599 | 106.92
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | 8 :VST BUS1 | 465 | 599 | 106.79
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | JAMCA - VLLYSTRM 901L&M 138 | 465 | 599 | 106.79
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | 901 L&M | 465 | 599 | 106.79
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | Y50 | VLY STRM 138 kV P.A.R. | 465 | 599 | 106.62
129344 NRTHPT1 138 129343 NRTHPT P 138 1 Max | [5 empty] | 160.33
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-677 | Northport Bus Tie No.1-2 | 179 | 295 | 106.5
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-677 | 78 :NPT BUS1-1 | 179 | 295 | 105.13
129344 NRTHPT1 138 129355 PILGRIM 138 3 Max | [5 empty] | 106.5
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-882 | 138-875 | 577 | 618 | 104.24
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-875 | 577 | 618 | 104.24
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-883 | 577 | 618 | 103
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-882 | 138-883 | 577 | 618 | 103
129421 HOLBROOK 138 129428 WEST BUS 138 1 Max | [5 empty] | 104.24

## NConv_SLL_Base
AnalysisType | Areas | First Level Contingency | Second Level Contingency
N-1-1 | 11 | GEN:CAITH | 11 :BRT BUS1
N-1-1 | 9/11 | GEN:CAITH | P5_BARRETT_138_R
N-1-1 | 11 | 138-291 | 12 :BRT BUS2
N-1-1 | 11 | 138-291 | Barrett Bus Tie
N-1-1 | 9 | 138-291 | 9 :BRT 1380
N-1-1 | 9/11 | 138-459 | P5_VALLEYSTREAM_138_M
N-1-1 | 9 | 69-965 | 370:EH-BUE2C
N-1-1 | 9 | 69-965 | 350:BLL 210
N-1-1 | 9 | 69-965 | 346:BLLBUS1
N-1-1 | 9 | 69-970 | 369:BRH-EH2C
N-1 | 11 | 11 :BRT BUS1
N-1 | 11 | P5_BARRETT_138_R

## N-1_SLL_Alt
Monitored Facility | Areas | Cont Name | Rate Base (MVA) | Rate Cont (MVA) | SCD AC %Loading
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | ALPSBERK393 | 31 | 31 | 135.8
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 31 | 31 | 135.18
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | BS:345:ALPS99K | 31 | 31 | 135.13
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | B:ALPS345 | 31 | 31 | 135.13
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | Base Case | 31 | 31 | 114.09
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 Max |  |  |  |  | 135.8
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 155 | 210 | 121.16
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | 139:EGC-CP2C | 155 | 210 | 104.05
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | 140:CP-ROS2C | 155 | 210 | 103.52
121408 NE_601_NY 138 129343 NRTHPT P 138 1 Max |  |  |  |  | 121.16
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 155 | 210 | 120.8
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | 139:EGC-CP2C | 155 | 210 | 103.74
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | 140:CP-ROS2C | 155 | 210 | 103.21
121409 NE_602_NY 138 129343 NRTHPT P 138 2 Max |  |  |  |  | 120.8
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 155 | 210 | 120.01
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | 139:EGC-CP2C | 155 | 210 | 103.06
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | 140:CP-ROS2C | 155 | 210 | 102.54
121410 NE_603_NY 138 129343 NRTHPT P 138 3 Max |  |  |  |  | 120.01
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | DNWDIE - MOTTHAVEN 345 72 | 823 | 953 | 128.2
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SB:MOTT345_3 | 823 | 953 | 128.17
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SB:MOTT345_7 | 823 | 953 | 128.16
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SB:DUNW345_8 | 823 | 953 | 127.54
126266 DUNWOODIE 345 126600 REAC71 345 BY Max |  |  |  |  | 128.2
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SB:DUNW345_3 | 823 | 953 | 127.4
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | DNWDIE - MOTTHAVEN 345 71 | 823 | 953 | 126.71
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SB:MOTT345_2 | 823 | 953 | 126.67
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SB:MOTT345_BTE | 823 | 953 | 126.67
126266 DUNWOODIE 345 126601 REAC72 345 BY Max |  |  |  |  | 127.4
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 780 | 1028 | 384.61
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Base Case | 780 | 1028 | 340.39
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | SPRNBRK - EGC 345 Y49 | 780 | 1028 | 311.01
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | 780 | 1028 | 311.01
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | B:EGC345 | 780 | 1028 | 311.01
126266 DUNWOODIE 345 128835 SHORE RD 345 1 Max |  |  |  |  | 384.61
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 143 | 178 | 213.73
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | 17 :SRD1370 | 143 | 178 | 171.35
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | 20 :SRD BUS1 | 143 | 178 | 171.32
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | Base Case | 143 | 178 | 126.76
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 Max |  |  |  |  | 213.73
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 139:EGC-CP2C | 1046 | 1194 | 235.66
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 140:CP-ROS2C | 1046 | 1194 | 235.26
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 141:ROS-GL2C | 1046 | 1194 | 235.07
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 17 :SRD1370 | 1046 | 1194 | 218.35
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | Base Case | 1046 | 1194 | 214.95
126298 SPRAINBROOK 345 126299 REACBUS 345 SR Max |  |  |  |  | 235.66
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SB:W49_5 | 887 | 1062 | 116.61
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SB:DUNW345_5 | 887 | 1062 | 115.11
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SB:DUNW345_7 | 887 | 1062 | 115.01
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SB:W49_3 | 887 | 1062 | 114.41
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SB:SPRA345_RNS4 | 887 | 1062 | 114.26
126298 SPRAINBROOK 345 126517 REACM51 345 BY Max |  |  |  |  | 116.61
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SB:DUNW345_5 | 887 | 1062 | 115.11
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SB:DUNW345_7 | 887 | 1062 | 115.01
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SB:W49_BTN | 887 | 1062 | 114.43
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SB:W49_2 | 887 | 1062 | 114.42
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SB:SPRA345_RNS5 | 887 | 1062 | 114.25
126298 SPRAINBROOK 345 126518 REACM52 345 BY Max |  |  |  |  | 115.11
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | Base Case | 770 | 990 | 300.52
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 139:EGC-CP2C | 770 | 990 | 289.72
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 140:CP-ROS2C | 770 | 990 | 289.25
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 141:ROS-GL2C | 770 | 990 | 289.05
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 17 :SRD1370 | 770 | 990 | 269.05
126299 REACBUS 345 147857 DVNPT NK 345 1 Max |  |  |  |  | 300.52
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SB:W49_5 | 887 | 1061 | 128.39
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SB:SPRA345_RNS4 | 887 | 1061 | 127.22
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SB:W49_3 | 887 | 1061 | 126.46
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | 887 | 1061 | 126.24
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SB:SPRA345_RS4 | 887 | 1061 | 126.24
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | Base Case | 887 | 1061 | 110.87
126304 W 49 ST 345 126517 REACM51 345 1 Max |  |  |  |  | 128.39
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SB:SPRA345_RNS5 | 887 | 1061 | 127.28
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SB:W49_BTN | 887 | 1061 | 126.46
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SB:W49_2 | 887 | 1061 | 126.46
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | 887 | 1061 | 126.24
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SB:SPRA345_RS5 | 887 | 1061 | 126.24
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | Base Case | 887 | 1061 | 110.87
126304 W 49 ST 345 126518 REACM52 345 2 Max |  |  |  |  | 127.28
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 165 | 165 | 196.39
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | 17 :SRD1370 | 165 | 165 | 157.52
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | 20 :SRD BUS1 | 165 | 165 | 157.49
126399 TAP X9 138 126437 FGT_X9 138 1 Max |  |  |  |  | 196.39
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | Base Case | 178 | 363 | 185.8
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 178 | 363 | 160.38
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | 17 :SRD1370 | 178 | 363 | 132.61
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | 20 :SRD BUS1 | 178 | 363 | 132.56
126452 HUDAVE E 138 126455 JAMAICA 138 1 Max |  |  |  |  | 185.8
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | Base Case | 178 | 363 | 185.8
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 178 | 363 | 160.38
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | 17 :SRD1370 | 178 | 363 | 132.61
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | 20 :SRD BUS1 | 178 | 363 | 132.56
126452 HUDAVE E 138 126455 JAMAICA 138 2 Max |  |  |  |  | 185.8
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 139:EGC-CP2C | 319 | 375 | 291.9
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 140:CP-ROS2C | 319 | 375 | 291.01
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 141:ROS-GL2C | 319 | 375 | 290.32
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 319 | 375 | 287.11
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Base Case | 319 | 375 | 138.35
126455 JAMAICA 138 129235 V STRM P 138 1 Max |  |  |  |  | 291.9
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 285 | 368 | 163.89
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | SHORE RD 345/138 Bank #1 | 285 | 368 | 144.61
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | SHORE RD 345/138 Bank #2 | 285 | 368 | 139.82
126455 JAMAICA 138 129249 L SUCSPH 138 1 Max |  |  |  |  | 163.89
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | DNWDIE - MOTTHAVEN 345 72 | 822 | 953 | 128.6
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SB:MOTT345_3 | 822 | 953 | 128.56
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SB:MOTT345_7 | 822 | 953 | 128.56
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SB:DUNW345_8 | 822 | 953 | 127.93
126600 REAC71 345 126641 MOTT HAVEN 345 3 Max |  |  |  |  | 128.6
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SB:DUNW345_3 | 822 | 953 | 127.79
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | DNWDIE - MOTTHAVEN 345 71 | 822 | 953 | 127.1
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SB:MOTT345_2 | 822 | 953 | 127.06
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SB:MOTT345_BTE | 822 | 953 | 127.06
126601 REAC72 345 126641 MOTT HAVEN 345 4 Max |  |  |  |  | 127.79
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SB:MOTT345_BTW | 822 | 953 | 140.59
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SB:MOTT345_1 | 822 | 953 | 140.59
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SB:RAIN345_2E | 822 | 953 | 140.49
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | 822 | 953 | 140.44
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SB:RAIN345_1E | 822 | 953 | 118.89
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 Max |  |  |  |  | 140.59
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SB:MOTT345_4 | 822 | 953 | 143.71
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SB:MOTT345_9 | 822 | 953 | 143.67
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | 822 | 953 | 143.52
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SB:RAINEY_7W | 822 | 953 | 143.35
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SB:RAINEY_6W | 822 | 953 | 141.16
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 Max |  |  |  |  | 143.71
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | SB:RAIN345_1E | 775 | 932 | 118.21
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 Max |  |  |  |  | 118.21
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 143 | 177 | 215.12
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | 17 :SRD1370 | 143 | 177 | 172.45
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | 20 :SRD BUS1 | 143 | 177 | 172.42
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | Base Case | 143 | 177 | 126.83
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 Max |  |  |  |  | 215.12
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 143 | 178 | 214.07
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | 17 :SRD1370 | 143 | 178 | 171.61
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | 20 :SRD BUS1 | 143 | 178 | 171.57
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | Base Case | 143 | 178 | 126.92
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 Max |  |  |  |  | 214.07
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Base Case | 770 | 990 | 282.69
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 139:EGC-CP2C | 770 | 990 | 275.65
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 140:CP-ROS2C | 770 | 990 | 275.18
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 141:ROS-GL2C | 770 | 990 | 274.96
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 17 :SRD1370 | 770 | 990 | 255.47
128824 EGC DUM 345 128825 EGC PAR 345 1 Max |  |  |  |  | 282.69
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | Base Case | 770 | 990 | 286.96
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 139:EGC-CP2C | 770 | 990 | 279.95
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 140:CP-ROS2C | 770 | 990 | 279.47
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 141:ROS-GL2C | 770 | 990 | 279.25
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 17 :SRD1370 | 770 | 990 | 259.31
128824 EGC DUM 345 128830 HMP HRBR 345 1 Max |  |  |  |  | 286.96
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | Base Case | 770 | 990 | 294
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 139:EGC-CP2C | 770 | 990 | 285.43
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 140:CP-ROS2C | 770 | 990 | 284.96
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 141:ROS-GL2C | 770 | 990 | 284.74
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 17 :SRD1370 | 770 | 990 | 264.61
128830 HMP HRBR 345 147857 DVNPT NK 345 1 Max |  |  |  |  | 294
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | 450 | 563 | 353.47
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 450 | 563 | 327.82
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | 21 :SRD BUS2 | 450 | 563 | 322.58
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | 18 :SRD1380 | 450 | 563 | 321.17
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | Base Case | 450 | 563 | 289.55
128835 SHORE RD 345 129293 SHORE RD 138 1 Max |  |  |  |  | 353.47
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | 540 | 562 | 349.54
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | 20 :SRD BUS1 | 540 | 562 | 320.16
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | 17 :SRD1370 | 540 | 562 | 318.88
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 540 | 562 | 317.01
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | Base Case | 540 | 562 | 233.58
128835 SHORE RD 345 129294 SHORE RD2 138 2 Max |  |  |  |  | 349.54
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Barrett Bus Tie | 218 | 308 | 414.82
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 12 :BRT BUS2 | 218 | 308 | 412.4
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 9 :BRT 1380 | 218 | 308 | 411.87
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 5 :VST NEW1 | 218 | 308 | 344.6
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-292 | 218 | 308 | 344.6
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Base Case | 218 | 308 | 250.1
129202 BARRETT1 138 129233 VLY STRM 138 1 Max |  |  |  |  | 414.82
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | P5_VALLEYSTREAM_138_M | 195 | 275 | 380.43
129203 BARRETT2 138 129204 BRRT PH 138 1 Max |  |  |  |  | 380.43
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 213 | 305 | 353.6
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 8 :VST BUS1 | 213 | 305 | 335.87
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 213 | 305 | 335.81
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | Base Case | 213 | 305 | 283.25
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 213 | 305 | 233.72
129203 BARRETT2 138 129234 VLY STRM2 138 2 Max |  |  |  |  | 353.6
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | P5_VALLEYSTREAM_138_M | 195 | 275 | 373.17
129204 BRRT PH 138 129276 FREEPORT 138 1 Max |  |  |  |  | 373.17
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 133 | 164 | 134.3
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 Max |  |  |  |  | 134.3
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 139:EGC-CP2C | 320 | 375 | 295.65
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 140:CP-ROS2C | 320 | 375 | 294.83
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 141:ROS-GL2C | 320 | 375 | 294.22
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 320 | 375 | 279.11
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Base Case | 320 | 375 | 142.07
129233 VLY STRM 138 129235 V STRM P 138 1 Max |  |  |  |  | 295.65
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | 194 | 284 | 177.31
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 901 L&M | 194 | 284 | 177.31
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138 kV P.A.R. | 194 | 284 | 177.14
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 194 | 284 | 175.06
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 8 :VST BUS1 | 194 | 284 | 174.74
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | Base Case | 194 | 284 | 149.66
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 Max |  |  |  |  | 177.31
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 139:EGC-CP2C | 260 | 380 | 125.44
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 140:CP-ROS2C | 260 | 380 | 124.86
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 141:ROS-GL2C | 260 | 380 | 124.56
129247 L SUCS 138 129293 SHORE RD 138 1 Max |  |  |  |  | 125.44
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 285 | 368 | 153.37
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | SHORE RD 345/138 Bank #1 | 285 | 368 | 144.48
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | SHORE RD 345/138 Bank #2 | 285 | 368 | 139.78
129248 L SUCS2 138 129249 L SUCSPH 138 1 Max |  |  |  |  | 153.37
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 139:EGC-CP2C | 260 | 380 | 125.61
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 140:CP-ROS2C | 260 | 380 | 125.02
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 141:ROS-GL2C | 260 | 380 | 124.72
129248 L SUCS2 138 129294 SHORE RD2 138 2 Max |  |  |  |  | 125.61
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 320 | 352 | 439.91
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 24 :EGC 1360 | 320 | 352 | 426.7
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 31 :GLN 1350 | 320 | 352 | 423.95
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | 320 | 352 | 423.95
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Base Case | 320 | 352 | 316.85
129265 CARLE PL 138 129270 E.G.C. 138 1 Max |  |  |  |  | 439.91
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 325 | 388 | 396.57
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 24 :EGC 1360 | 325 | 388 | 384.55
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | 325 | 388 | 382.06
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 31 :GLN 1350 | 325 | 388 | 382.06
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Base Case | 325 | 388 | 308.98
129265 CARLE PL 138 129283 GLNWD SO 138 1 Max |  |  |  |  | 396.57
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 450 | 585 | 121.72
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 450 | 585 | 121.72
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 450 | 585 | 121.72
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | 29 :EGC 1450 | 450 | 585 | 121.17
129270 E.G.C. 138 128822 E.G.C.-1 345 1 Max |  |  |  |  | 121.72
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 320 | 352 | 428.96
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | 320 | 352 | 416.39
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 35 :GLNSO BUS | 320 | 352 | 416.39
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 30 :GLN1320 | 320 | 352 | 416.39
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Base Case | 320 | 352 | 308.38
129270 E.G.C. 138 129288 ROSLYN 138 1 Max |  |  |  |  | 428.96
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 129270 E.G.C. 138 129271 E.G.C.-2 138 1 | 194 | 284 | 429.59
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | Base Case | 194 | 284 | 353.72
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | P5_VALLEYSTREAM_138_M | 194 | 284 | 329.4
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 46 :NBR 1400 | 194 | 284 | 328.51
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | NEW_EGC 1390 | 194 | 284 | 322.01
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | 194 | 284 | 321.8
129270 E.G.C. 138 129310 NEWBRGE 138 1 Max |  |  |  |  | 429.59
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 129270 E.G.C. 138 129271 E.G.C.-2 138 1 | 216 | 306 | 384.65
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | Base Case | 216 | 306 | 306.52
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | P5_VALLEYSTREAM_138_M | 216 | 306 | 295.13
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 46 :NBR 1400 | 216 | 306 | 293.83
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | 216 | 306 | 291.34
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 41 :NBR 1350 | 216 | 306 | 290.28
129270 E.G.C. 138 129310 NEWBRGE 138 3 Max |  |  |  |  | 384.65
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | 24 :EGC 1360 | 450 | 585 | 129.28
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | 28 :EGC 1420 | 450 | 585 | 121.66
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 450 | 585 | 121.66
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | 33 :EGC BUS2 | 450 | 585 | 121.66
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 Max |  |  |  |  | 129.28
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | Base Case | 210 | 302 | 316.41
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | P5_VALLEYSTREAM_138_M | 210 | 302 | 303.12
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | 210 | 302 | 296.54
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 41 :NBR 1350 | 210 | 302 | 295.45
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 23 :EGC 1350 | 210 | 302 | 293.14
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-465 | 210 | 302 | 292.9
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 Max |  |  |  |  | 316.41
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | Base Case | 270 | 474 | 181.75
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 46 :NBR 1400 | 270 | 474 | 142.89
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | P5_VALLEYSTREAM_138_M | 270 | 474 | 142.65
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-463 | 270 | 474 | 139.43
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-462 | 270 | 474 | 139.33
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | NEW_EGC 1390 | 270 | 474 | 139.23
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 Max |  |  |  |  | 181.75
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | P5_VALLEYSTREAM_138_M | 229 | 299 | 326.81
129276 FREEPORT 138 129310 NEWBRGE 138 1 Max |  |  |  |  | 326.81
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 351 | 388 | 387.58
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 35 :GLNSO BUS | 351 | 388 | 376.31
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | 351 | 388 | 376.31
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 30 :GLN1320 | 351 | 388 | 376.31
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Base Case | 351 | 388 | 279.59
129281 GLNWD GT 138 129282 GLNWD NO 138 1 Max |  |  |  |  | 387.58
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 351 | 388 | 387.6
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 30 :GLN1320 | 351 | 388 | 376.32
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | 351 | 388 | 376.32
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 35 :GLNSO BUS | 351 | 388 | 376.32
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Base Case | 351 | 388 | 279.6
129281 GLNWD GT 138 129288 ROSLYN 138 1 Max |  |  |  |  | 387.6
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 381 | 446 | 394.5
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 30 :GLN1320 | 381 | 446 | 387.99
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 35 :GLNSO BUS | 381 | 446 | 387.99
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | 381 | 446 | 387.99
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Base Case | 381 | 446 | 298.41
129282 GLNWD NO 138 129293 SHORE RD 138 1 Max |  |  |  |  | 394.5
129282 GLNWD NO 138 129587 GLNWD NO 69.0 1 | 11 | 139:EGC-CP2C | 134 | 164 | 247.72
129282 GLNWD NO 138 129587 GLNWD NO 69.0 1 | 11 | 140:CP-ROS2C | 134 | 164 | 246.93
129282 GLNWD NO 138 129587 GLNWD NO 69.0 1 | 11 | 141:ROS-GL2C | 134 | 164 | 246.61
129282 GLNWD NO 138 129587 GLNWD NO 69.0 1 | 11 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 134 | 164 | 170.18
129282 GLNWD NO 138 129587 GLNWD NO 69.0 1 | 11 | 138-365 | 134 | 164 | 154.56
129282 GLNWD NO 138 129587 GLNWD NO 69.0 1 | 11 | Base Case | 134 | 164 | 111.37
129282 GLNWD NO 138 129587 GLNWD NO 69.0 1 Max |  |  |  |  | 247.72
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 351 | 388 | 458.47
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 33 :GLN 1340 | 351 | 388 | 447.96
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | 351 | 388 | 447.96
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 31 :GLN 1350 | 351 | 388 | 447.96
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Base Case | 351 | 388 | 327.71
129283 GLNWD SO 138 129294 SHORE RD2 138 1 Max |  |  |  |  | 458.47
129283 GLNWD SO 138 129588 GLNWD SO 69.0 1 | 11 | 139:EGC-CP2C | 135 | 164 | 232.93
129283 GLNWD SO 138 129588 GLNWD SO 69.0 1 | 11 | 140:CP-ROS2C | 135 | 164 | 232.11
129283 GLNWD SO 138 129588 GLNWD SO 69.0 1 | 11 | 141:ROS-GL2C | 135 | 164 | 231.84
129283 GLNWD SO 138 129588 GLNWD SO 69.0 1 | 11 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 135 | 164 | 162.07
129283 GLNWD SO 138 129588 GLNWD SO 69.0 1 | 11 | 31 :GLN 1350 | 135 | 164 | 146.92
129283 GLNWD SO 138 129588 GLNWD SO 69.0 1 | 11 | Base Case | 135 | 164 | 104.16
129283 GLNWD SO 138 129588 GLNWD SO 69.0 1 Max |  |  |  |  | 232.93
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | P5_RULANDRD_138_M | 365 | 602 | 130.15
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | Base Case | 365 | 602 | 129.54
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 54 :NBR 1480 | 365 | 602 | 117.29
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 135:RUL-NB2C | 365 | 602 | 114.28
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 143:PIL-NB2C | 365 | 602 | 112.82
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 144:HOL-NB2C | 365 | 602 | 112.5
129305 LCST GRV 138 129310 NEWBRGE 138 1 Max |  |  |  |  | 130.15
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | P5_RULANDRD_138_M | 529 | 591 | 133.87
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 54 :NBR 1480 | 529 | 591 | 120.83
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 135:RUL-NB2C | 529 | 591 | 117.76
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 143:PIL-NB2C | 529 | 591 | 116.27
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 144:HOL-NB2C | 529 | 591 | 115.95
129305 LCST GRV 138 129315 SYOSSET 138 1 Max |  |  |  |  | 133.87
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | P5_RULANDRD_138_M | 577 | 618 | 120.13
129310 NEWBRGE 138 129324 BETHPAGE 138 1 Max |  |  |  |  | 120.13
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 77 :RUL 1310 | 302 | 331 | 209.65
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | 302 | 331 | 207.89
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 51 :NBR 1450 | 302 | 331 | 206.72
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | 302 | 331 | 206.69
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 50 :NBR 1440 | 302 | 331 | 206.68
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | Base Case | 302 | 331 | 173.95
129310 NEWBRGE 138 129361 RULND RD 138 1 Max |  |  |  |  | 209.65
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 54 :NBR 1480 | 302 | 331 | 243.54
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 77 :RUL 1310 | 302 | 331 | 209.64
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | 302 | 331 | 207.89
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | 302 | 331 | 206.68
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 50 :NBR 1440 | 302 | 331 | 206.67
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | Base Case | 302 | 331 | 173.95
129310 NEWBRGE 138 129361 RULND RD 138 2 Max |  |  |  |  | 243.54
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 135:RUL-NB2C | 259 | 388 | 253.1
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 54 :NBR 1480 | 259 | 388 | 204.48
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | Base Case | 259 | 388 | 199.7
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-561 | 259 | 388 | 174.56
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-562 | 259 | 388 | 174.55
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 51 :NBR 1450 | 259 | 388 | 173.57
129310 NEWBRGE 138 129361 RULND RD 138 3 Max |  |  |  |  | 253.1
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 | 11 | 139:EGC-CP2C | 136 | 167 | 143.42
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 | 11 | 140:CP-ROS2C | 136 | 167 | 142.97
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 | 11 | 141:ROS-GL2C | 136 | 167 | 142.75
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 143.42
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-674 | 265 | 368 | 126.03
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | ELWOOD 138/69 kV Bank #3 | 265 | 368 | 124.74
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-675 | 265 | 368 | 124.74
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 80 :ELD BUS1 | 265 | 368 | 124.74
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | P5_RULANDRD_138_M | 265 | 368 | 124.49
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | Base Case | 265 | 368 | 109.51
129315 SYOSSET 138 129333 GRENLAWN 138 1 Max |  |  |  |  | 126.03
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-676 | 265 | 368 | 120.57
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | P5_RULANDRD_138_M | 265 | 368 | 116.91
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 36 :SYT 1340 | 265 | 368 | 116.17
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 76 :NPT BUS4 | 265 | 368 | 115.25
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-678 | 265 | 368 | 115.25
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | Base Case | 265 | 368 | 101.68
129315 SYOSSET 138 129351 OAKWOOD 138 1 Max |  |  |  |  | 120.57
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | P5_RULANDRD_138_M | 418 | 618 | 120.9
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | Base Case | 418 | 618 | 104.62
129321 BAGATELLE 138 129324 BETHPAGE 138 1 Max |  |  |  |  | 120.9
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | P5_RULANDRD_138_M | 572 | 617 | 121.74
129321 BAGATELLE 138 129355 PILGRIM 138 1 Max |  |  |  |  | 121.74
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 351 | 375 | 137.11
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | GEN: OSW Holbrook 1 | 351 | 375 | 137.04
129337 HAUPAGUE 138 129356 PILGRM P 138 1 Max |  |  |  |  | 137.11
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 215 | 288 | 176.86
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | GEN: OSW Holbrook 1 | 215 | 288 | 176.77
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | Base Case | 215 | 288 | 125.73
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 136:HOL-RU2C | 215 | 288 | 116.87
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 215 | 288 | 104.31
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 70 :NPT 1330 | 215 | 288 | 104.24
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 Max |  |  |  |  | 176.86
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 280:HOL 6620 | 572 | 617 | 129.68
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 96 :HOL 1350 | 572 | 617 | 125.33
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 108:HOL BUS2 | 572 | 617 | 125.25
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 572 | 617 | 125.25
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-882 | 572 | 617 | 125.25
129339 KINGS 138 129355 PILGRIM 138 1 Max |  |  |  |  | 129.68
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 280:HOL 6620 | 577 | 618 | 130.86
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 96 :HOL 1350 | 577 | 618 | 126.53
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 108:HOL BUS2 | 577 | 618 | 126.44
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-882 | 577 | 618 | 126.44
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 577 | 618 | 126.44
129339 KINGS 138 129428 WEST BUS 138 1 Max |  |  |  |  | 130.86
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | P5_RULANDRD_138_M | 517 | 591 | 140.22
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 62 : PIL1370 | 517 | 591 | 125.38
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 54 :NBR 1480 | 517 | 591 | 121.12
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 143:PIL-NB2C | 517 | 591 | 120.54
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 144:HOL-NB2C | 517 | 591 | 120.27
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 Max |  |  |  |  | 140.22
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | Northport Bus Tie No.1-1 | 362 | 590 | 101.19
129341 NRTHPRT1 138 129355 PILGRIM 138 1 Max |  |  |  |  | 101.19
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 465 | 599 | 130.99
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | 139:EGC-CP2C | 465 | 599 | 112.98
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | 140:CP-ROS2C | 465 | 599 | 112.44
129344 NRTHPT1 138 129343 NRTHPT P 138 1 Max |  |  |  |  | 130.99
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 300 | 375 | 139.83
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | 300 | 375 | 139.75
129356 PILGRM P 138 129355 PILGRIM 138 1 Max |  |  |  |  | 139.83
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 59 : PIL1320 | 529 | 591 | 104.7
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 NEW | 529 | 591 | 103.77
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 63 : PIL1380 | 529 | 591 | 103.72
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | PILGRIM 138/69 Bank #4 | 529 | 591 | 103.72
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 68 : PIL BUS2 | 529 | 591 | 103.72
129361 RULND RD 138 129421 HOLBROOK 138 1 Max |  |  |  |  | 104.7
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 136:HOL-RU2C | 440 | 591 | 109.14
129393 C.ISLIP 138 129454 RONKONK 138 1 Max |  |  |  |  | 109.14
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 280:HOL 6620 | 577 | 618 | 123.66
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 96 :HOL 1350 | 577 | 618 | 121.17
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-882 | 577 | 618 | 120.96
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 577 | 618 | 120.96
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 108:HOL BUS2 | 577 | 618 | 120.96
129421 HOLBROOK 138 129428 WEST BUS 138 1 Max |  |  |  |  | 123.66
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 136:HOL-RU2C | 572 | 617 | 105.81
129421 HOLBROOK 138 129454 RONKONK 138 1 Max |  |  |  |  | 105.81
129501 BARRETT 69.0 129572 BALDWIN1 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 126 | 168 | 115.26
129501 BARRETT 69.0 129572 BALDWIN1 69.0 1 Max |  |  |  |  | 115.26
129507 CORONA 69.0 129528 VLYSTRM2 69.0 1 | 11 | 139:EGC-CP2C | 139 | 154 | 102.49
129507 CORONA 69.0 129528 VLYSTRM2 69.0 1 | 11 | 140:CP-ROS2C | 139 | 154 | 102.24
129507 CORONA 69.0 129528 VLYSTRM2 69.0 1 | 11 | 141:ROS-GL2C | 139 | 154 | 102.07
129507 CORONA 69.0 129528 VLYSTRM2 69.0 1 Max |  |  |  |  | 102.49
129507 CORONA 69.0 129565 WHITESDE 69.0 1 | 11 | 139:EGC-CP2C | 101 | 112 | 136.59
129507 CORONA 69.0 129565 WHITESDE 69.0 1 | 11 | 140:CP-ROS2C | 101 | 112 | 136.26
129507 CORONA 69.0 129565 WHITESDE 69.0 1 | 11 | 141:ROS-GL2C | 101 | 112 | 136.02
129507 CORONA 69.0 129565 WHITESDE 69.0 1 Max |  |  |  |  | 136.59
129527 VLYSTRM1 69.0 129565 WHITESDE 69.0 1 | 11 | 139:EGC-CP2C | 101 | 112 | 131.86
129527 VLYSTRM1 69.0 129565 WHITESDE 69.0 1 | 11 | 140:CP-ROS2C | 101 | 112 | 131.54
129527 VLYSTRM1 69.0 129565 WHITESDE 69.0 1 | 11 | 141:ROS-GL2C | 101 | 112 | 131.31
129527 VLYSTRM1 69.0 129565 WHITESDE 69.0 1 | 11 | 69-265 | 101 | 112 | 102.08
129527 VLYSTRM1 69.0 129565 WHITESDE 69.0 1 Max |  |  |  |  | 131.86
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | 139:EGC-CP2C | 101 | 112 | 341.3
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | 140:CP-ROS2C | 101 | 112 | 339.74
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | 141:ROS-GL2C | 101 | 112 | 339.18
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 101 | 112 | 220.7
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | Base Case | 101 | 112 | 172.43
129540 HERRICK 69.0 129558 SPERRY 69.0 1 Max |  |  |  |  | 341.3
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | 139:EGC-CP2C | 118 | 139 | 279.16
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | 140:CP-ROS2C | 118 | 139 | 277.92
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | 141:ROS-GL2C | 118 | 139 | 277.44
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 118 | 139 | 182.03
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | Base Case | 118 | 139 | 152.61
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 Max |  |  |  |  | 279.16
129543 LKE SCSS 69.0 129247 L SUCS 138 1 | 11 | 139:EGC-CP2C | 272 | 335 | 127.37
129543 LKE SCSS 69.0 129247 L SUCS 138 1 | 11 | 140:CP-ROS2C | 272 | 335 | 126.98
129543 LKE SCSS 69.0 129247 L SUCS 138 1 | 11 | 141:ROS-GL2C | 272 | 335 | 126.83
129543 LKE SCSS 69.0 129247 L SUCS 138 1 Max |  |  |  |  | 127.37
129543 LKE SCSS 69.0 129248 L SUCS2 138 2 | 11 | 139:EGC-CP2C | 272 | 335 | 116.5
129543 LKE SCSS 69.0 129248 L SUCS2 138 2 | 11 | 140:CP-ROS2C | 272 | 335 | 116.15
129543 LKE SCSS 69.0 129248 L SUCS2 138 2 | 11 | 141:ROS-GL2C | 272 | 335 | 116.01
129543 LKE SCSS 69.0 129248 L SUCS2 138 2 Max |  |  |  |  | 116.5
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | 139:EGC-CP2C | 127 | 145 | 287.15
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | 140:CP-ROS2C | 127 | 145 | 285.87
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | 141:ROS-GL2C | 127 | 145 | 285.4
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 127 | 145 | 214.23
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 127 | 145 | 212.79
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | Base Case | 127 | 145 | 162.28
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 Max |  |  |  |  | 287.15
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 139:EGC-CP2C | 93 | 106 | 268.73
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 140:CP-ROS2C | 93 | 106 | 268.05
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 141:ROS-GL2C | 93 | 106 | 267.58
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 93 | 106 | 171.27
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | Base Case | 93 | 106 | 135.37
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 Max |  |  |  |  | 268.73
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 139:EGC-CP2C | 93 | 106 | 269.39
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 140:CP-ROS2C | 93 | 106 | 268.71
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 141:ROS-GL2C | 93 | 106 | 268.24
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 93 | 106 | 171.93
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | Base Case | 93 | 106 | 136.06
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 Max |  |  |  |  | 269.39
129572 BALDWIN1 69.0 129617 BELMR 1 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 126 | 168 | 111.21
129572 BALDWIN1 69.0 129617 BELMR 1 69.0 1 Max |  |  |  |  | 111.21
129580 E.G.C.1 69.0 129270 E.G.C. 138 1 | 11 | 139:EGC-CP2C | 272 | 335 | 105.09
129580 E.G.C.1 69.0 129270 E.G.C. 138 1 | 11 | 140:CP-ROS2C | 272 | 335 | 104.14
129580 E.G.C.1 69.0 129270 E.G.C. 138 1 | 11 | 141:ROS-GL2C | 272 | 335 | 104.04
129580 E.G.C.1 69.0 129270 E.G.C. 138 1 Max |  |  |  |  | 105.09
129584 GLEN HD 69.0 129598 ORCHARD 69.0 1 | 11 | 139:EGC-CP2C | 101 | 112 | 114.79
129584 GLEN HD 69.0 129598 ORCHARD 69.0 1 | 11 | 140:CP-ROS2C | 101 | 112 | 114.43
129584 GLEN HD 69.0 129598 ORCHARD 69.0 1 | 11 | 141:ROS-GL2C | 101 | 112 | 114.27
129584 GLEN HD 69.0 129598 ORCHARD 69.0 1 | 11 | 186:GLN6090 | 101 | 112 | 106.11
129584 GLEN HD 69.0 129598 ORCHARD 69.0 1 | 11 | 69-530 | 101 | 112 | 106.02
129584 GLEN HD 69.0 129598 ORCHARD 69.0 1 Max |  |  |  |  | 114.79
129587 GLNWD NO 69.0 129590 GLNWD#3A 69.0 1 | 11 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 149 | 183 | 153.6
129587 GLNWD NO 69.0 129590 GLNWD#3A 69.0 1 | 11 | 21 :SRD BUS2 | 149 | 183 | 139.53
129587 GLNWD NO 69.0 129590 GLNWD#3A 69.0 1 | 11 | 35 :GLNSO BUS | 149 | 183 | 125.65
129587 GLNWD NO 69.0 129590 GLNWD#3A 69.0 1 | 11 | 30 :GLN1320 | 149 | 183 | 125.65
129587 GLNWD NO 69.0 129590 GLNWD#3A 69.0 1 | 11 | 138-365 | 149 | 183 | 125.65
129587 GLNWD NO 69.0 129590 GLNWD#3A 69.0 1 Max |  |  |  |  | 153.6
129588 GLNWD SO 69.0 129589 GLNWD#3 69.0 1 | 11 | 129585 GLWND TAP 69.0 129588 GLNWD SO 69.0 1 | 139 | 154 | 119.08
129588 GLNWD SO 69.0 129589 GLNWD#3 69.0 1 | 11 | 190:GH 650 | 139 | 154 | 117.71
129588 GLNWD SO 69.0 129589 GLNWD#3 69.0 1 | 11 | 69-489 | 139 | 154 | 117.08
129588 GLNWD SO 69.0 129589 GLNWD#3 69.0 1 Max |  |  |  |  | 119.08
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 | 11 | 139:EGC-CP2C | 149 | 183 | 217.82
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 | 11 | 140:CP-ROS2C | 149 | 183 | 216.97
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 | 11 | 141:ROS-GL2C | 149 | 183 | 216.61
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 149 | 183 | 136.19
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 | 11 | Base Case | 149 | 183 | 114.43
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 Max |  |  |  |  | 217.82
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | 139:EGC-CP2C | 149 | 183 | 205.22
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | 140:CP-ROS2C | 149 | 183 | 204.44
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | 141:ROS-GL2C | 149 | 183 | 204.1
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | 128824 EGC DUM 345 128830 HMP HRBR 345 1 | 149 | 183 | 120.76
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | Base Case | 149 | 183 | 105.14
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 205.22
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | 139:EGC-CP2C | 66 | 73 | 135.01
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | 140:CP-ROS2C | 66 | 73 | 133.85
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | 141:ROS-GL2C | 66 | 73 | 133.59
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | 69-372 | 66 | 73 | 116.43
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | 178:HKS 650 | 66 | 73 | 116.22
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 Max |  |  |  |  | 135.01
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 | 11 | 139:EGC-CP2C | 101 | 112 | 225.73
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 | 11 | 140:CP-ROS2C | 101 | 112 | 225.01
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 | 11 | 141:ROS-GL2C | 101 | 112 | 224.71
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 | 11 | NEWBUS2 | 101 | 112 | 156.31
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 | 11 | 53 :NBR 1470 | 101 | 112 | 153.19
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 | 11 | Base Case | 101 | 112 | 131.42
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 Max |  |  |  |  | 225.73
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 | 11 | 139:EGC-CP2C | 101 | 112 | 239.76
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 | 11 | 140:CP-ROS2C | 101 | 112 | 239.36
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 | 11 | 141:ROS-GL2C | 101 | 112 | 239.08
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 101 | 112 | 219.23
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 | 11 | 48 :NBR 1420 | 101 | 112 | 167.02
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 | 11 | Base Case | 101 | 112 | 149.65
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 Max |  |  |  |  | 239.76
129619 BELMR 2 69.0 129631 MASPEQUA 69.0 1 | 11 | 152:NB-LEVIT2C | 139 | 154 | 111.36
129619 BELMR 2 69.0 129631 MASPEQUA 69.0 1 | 11 | 135:RUL-NB2C | 139 | 154 | 109.8
129619 BELMR 2 69.0 129631 MASPEQUA 69.0 1 | 11 | 201:LV 610 | 139 | 154 | 104.22
129619 BELMR 2 69.0 129631 MASPEQUA 69.0 1 | 11 | LV BUS1 | 139 | 154 | 104.22
129619 BELMR 2 69.0 129631 MASPEQUA 69.0 1 | 11 | NEWBUS1 | 139 | 154 | 101.93
129619 BELMR 2 69.0 129631 MASPEQUA 69.0 1 Max |  |  |  |  | 111.36
129619 BELMR 2 69.0 129639 NEWBRGE1 69.0 1 | 11 | 129630 MASPEQUA2 69.0 129631 MASPEQUA 69.0 1 | 110 | 135 | 113.11
129619 BELMR 2 69.0 129639 NEWBRGE1 69.0 1 | 11 | MS BUS3 | 110 | 135 | 111.94
129619 BELMR 2 69.0 129639 NEWBRGE1 69.0 1 | 11 | 69-566 | 110 | 135 | 111.94
129619 BELMR 2 69.0 129639 NEWBRGE1 69.0 1 | 11 | 139:EGC-CP2C | 110 | 135 | 106.35
129619 BELMR 2 69.0 129639 NEWBRGE1 69.0 1 | 11 | 140:CP-ROS2C | 110 | 135 | 105.87
129619 BELMR 2 69.0 129639 NEWBRGE1 69.0 1 Max |  |  |  |  | 113.11
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 | 11 | 139:EGC-CP2C | 127 | 145 | 148.57
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 | 11 | 140:CP-ROS2C | 127 | 145 | 148.01
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 | 11 | 141:ROS-GL2C | 127 | 145 | 147.75
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 | 11 | 129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 | 127 | 145 | 111.8
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 | 11 | 69-477 478 | 127 | 145 | 111.7
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 148.57
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | 139:EGC-CP2C | 101 | 112 | 228.6
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | 140:CP-ROS2C | 101 | 112 | 227.9
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | 141:ROS-GL2C | 101 | 112 | 227.57
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | NEWBUS2 | 101 | 112 | 158.93
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | 53 :NBR 1470 | 101 | 112 | 155.82
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | Base Case | 101 | 112 | 134.34
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 Max |  |  |  |  | 228.6
129630 MASPEQUA2 69.0 129765 STERLING 69.0 1 | 11 | 135:RUL-NB2C | 176 | 194 | 111.62
129630 MASPEQUA2 69.0 129765 STERLING 69.0 1 | 11 | 243:RUL6500 | 176 | 194 | 101.55
129630 MASPEQUA2 69.0 129765 STERLING 69.0 1 Max |  |  |  |  | 111.62
129633 MEDBROOK 69.0 129640 NEWBRGE2 69.0 1 | 11 | 139:EGC-CP2C | 73 | 83 | 116.78
129633 MEDBROOK 69.0 129640 NEWBRGE2 69.0 1 | 11 | 140:CP-ROS2C | 73 | 83 | 115.81
129633 MEDBROOK 69.0 129640 NEWBRGE2 69.0 1 | 11 | 141:ROS-GL2C | 73 | 83 | 115.54
129633 MEDBROOK 69.0 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 116.78
129635 N.BELLMR 69.0 129640 NEWBRGE2 69.0 1 | 11 | 139:EGC-CP2C | 139 | 154 | 170.91
129635 N.BELLMR 69.0 129640 NEWBRGE2 69.0 1 | 11 | 140:CP-ROS2C | 139 | 154 | 170.63
129635 N.BELLMR 69.0 129640 NEWBRGE2 69.0 1 | 11 | 141:ROS-GL2C | 139 | 154 | 170.43
129635 N.BELLMR 69.0 129640 NEWBRGE2 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 139 | 154 | 156.1
129635 N.BELLMR 69.0 129640 NEWBRGE2 69.0 1 | 11 | 48 :NBR 1420 | 139 | 154 | 118.48
129635 N.BELLMR 69.0 129640 NEWBRGE2 69.0 1 | 11 | Base Case | 139 | 154 | 105.3
129635 N.BELLMR 69.0 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 170.91
129642 OYSTRBAY 69.0 129650 SYOSSET 69.0 1 | 11 | 139:EGC-CP2C | 173 | 185 | 140.74
129642 OYSTRBAY 69.0 129650 SYOSSET 69.0 1 | 11 | 140:CP-ROS2C | 173 | 185 | 140.33
129642 OYSTRBAY 69.0 129650 SYOSSET 69.0 1 | 11 | 141:ROS-GL2C | 173 | 185 | 140.15
129642 OYSTRBAY 69.0 129650 SYOSSET 69.0 1 Max |  |  |  |  | 140.74
129644 PLN TAP 69.0 129648 PLNVIEW 69.0 1 | 11 | SS BUS1 | 85 | 104 | 111.5
129644 PLN TAP 69.0 129648 PLNVIEW 69.0 1 | 11 | 213:SS 630 | 85 | 104 | 111.5
129644 PLN TAP 69.0 129648 PLNVIEW 69.0 1 | 11 | 135:RUL-NB2C | 85 | 104 | 105.21
129644 PLN TAP 69.0 129648 PLNVIEW 69.0 1 Max |  |  |  |  | 111.5
129668 DEPOSIT 69.0 129680 INDIANHD 69.0 1 | 11 | 136:HOL-RU2C | 139 | 154 | 127.31
129668 DEPOSIT 69.0 129680 INDIANHD 69.0 1 Max |  |  |  |  | 127.31
129668 DEPOSIT 69.0 129689 PULASKI 69.0 1 | 11 | 136:HOL-RU2C | 139 | 154 | 135.01
129668 DEPOSIT 69.0 129689 PULASKI 69.0 1 Max |  |  |  |  | 135.01
129671 ELWOOD 69.0 129676 GRENLAWN2 69.0 1 | 11 | 136:HOL-RU2C | 101 | 112 | 116.51
129671 ELWOOD 69.0 129676 GRENLAWN2 69.0 1 | 11 | P5_RULANDRD_138_M | 101 | 112 | 115.38
129671 ELWOOD 69.0 129676 GRENLAWN2 69.0 1 Max |  |  |  |  | 116.51
129671 ELWOOD 69.0 129689 PULASKI 69.0 1 | 11 | 136:HOL-RU2C | 139 | 154 | 132.15
129671 ELWOOD 69.0 129689 PULASKI 69.0 1 Max |  |  |  |  | 132.15
129680 INDIANHD 69.0 129695 SMITHTWN 69.0 1 | 11 | 136:HOL-RU2C | 173 | 185 | 108.09
129680 INDIANHD 69.0 129695 SMITHTWN 69.0 1 Max |  |  |  |  | 108.09
129714 BABYLON 69.0 129723 BRGHTWTR 69.0 1 | 11 | P5_RULANDRD_138_M | 173 | 185 | 132.71
129714 BABYLON 69.0 129723 BRGHTWTR 69.0 1 | 11 | 136:HOL-RU2C | 173 | 185 | 131.85
129714 BABYLON 69.0 129723 BRGHTWTR 69.0 1 | 11 | 143:PIL-NB2C | 173 | 185 | 112.16
129714 BABYLON 69.0 129723 BRGHTWTR 69.0 1 | 11 | 144:HOL-NB2C | 173 | 185 | 112.02
129714 BABYLON 69.0 129723 BRGHTWTR 69.0 1 | 11 | 80 :RUL 1410 | 173 | 185 | 101.78
129714 BABYLON 69.0 129723 BRGHTWTR 69.0 1 Max |  |  |  |  | 132.71
129714 BABYLON 69.0 129771 W.BABYLN 69.0 1 | 11 | P5_RULANDRD_138_M | 149 | 162 | 147.95
129714 BABYLON 69.0 129771 W.BABYLN 69.0 1 | 11 | 136:HOL-RU2C | 149 | 162 | 146.99
129714 BABYLON 69.0 129771 W.BABYLN 69.0 1 | 11 | 143:PIL-NB2C | 149 | 162 | 124.56
129714 BABYLON 69.0 129771 W.BABYLN 69.0 1 | 11 | 144:HOL-NB2C | 149 | 162 | 124.4
129714 BABYLON 69.0 129771 W.BABYLN 69.0 1 Max |  |  |  |  | 147.95
129717 BAYPORT 69.0 129737 GRT RVER 69.0 1 | 11 | 136:HOL-RU2C | 101 | 112 | 113.03
129717 BAYPORT 69.0 129737 GRT RVER 69.0 1 Max |  |  |  |  | 113.03
129723 BRGHTWTR 69.0 129777 WATSON 69.0 1 | 11 | 136:HOL-RU2C | 101 | 112 | 138.62
129723 BRGHTWTR 69.0 129777 WATSON 69.0 1 | 11 | 69-783 | 101 | 112 | 101.27
129723 BRGHTWTR 69.0 129777 WATSON 69.0 1 | 11 | P5_RULANDRD_138_M | 101 | 112 | 101.19
129723 BRGHTWTR 69.0 129777 WATSON 69.0 1 Max |  |  |  |  | 138.62
129726 BRNTWD3 69.0 129755 PINES 69.0 1 | 11 | 136:HOL-RU2C | 139 | 154 | 140.35
129726 BRNTWD3 69.0 129755 PINES 69.0 1 Max |  |  |  |  | 140.35
129731 C.ISLIP 69.0 129755 PINES 69.0 1 | 11 | 136:HOL-RU2C | 173 | 185 | 118.26
129731 C.ISLIP 69.0 129755 PINES 69.0 1 Max |  |  |  |  | 118.26
129737 GRT RVER 69.0 129777 WATSON 69.0 1 | 11 | 136:HOL-RU2C | 101 | 112 | 109.19
129737 GRT RVER 69.0 129777 WATSON 69.0 1 Max |  |  |  |  | 109.19
129860 BHMPTMID 69.0 129866 DEERFILD 69.0 1 | 11 | 356:220 | 121 | 121 | 101.79
129860 BHMPTMID 69.0 129866 DEERFILD 69.0 1 | 11 | 355:EHPBUS2 | 121 | 121 | 101.76
129860 BHMPTMID 69.0 129866 DEERFILD 69.0 1 Max |  |  |  |  | 101.79
129860 BHMPTMID 69.0 129868 EHAMP 69.0 1 | 11 | 356:220 | 121 | 121 | 101.81
129860 BHMPTMID 69.0 129868 EHAMP 69.0 1 | 11 | 355:EHPBUS2 | 121 | 121 | 101.77
129860 BHMPTMID 69.0 129868 EHAMP 69.0 1 Max |  |  |  |  | 101.81
129862 BUELL 69.0 129868 EHAMP 69.0 1 | 11 | 369:BRH-EH2C | 121 | 121 | 101.79
129862 BUELL 69.0 129868 EHAMP 69.0 1 | 11 | 342:DRFD650 | 121 | 121 | 101.72
129862 BUELL 69.0 129868 EHAMP 69.0 1 | 11 | 361:BHMPTMID | 121 | 121 | 101.72
129862 BUELL 69.0 129868 EHAMP 69.0 1 | 11 | BHMPTMID | 121 | 121 | 101.72
129862 BUELL 69.0 129868 EHAMP 69.0 1 | 11 | 341:DRFD640 | 121 | 121 | 101.72
129862 BUELL 69.0 129868 EHAMP 69.0 1 Max |  |  |  |  | 101.79
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 | 11 | P5_VALLEYSTREAM_138_M | 87 | 96 | 119.42
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 Max |  |  |  |  | 119.42
130718 Q535_POI 138 130675 RIVHEAD_PSU 138 1 | 11 | 129488 EDWRDSAV 138 130718 Q535_POI 138 1 | 25 | 25 | 165.18
130718 Q535_POI 138 130675 RIVHEAD_PSU 138 1 Max |  |  |  |  | 165.18
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 | 11 | Base Case | 40 | 40 | 107.35
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 | 11 | 350:BLL 210 | 40 | 40 | 105.32
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 | 11 | 98 :HOL 1370 | 40 | 40 | 105.23
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 | 11 | 279:HOL 6610 | 40 | 40 | 105.01
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 | 11 | 138-888 | 40 | 40 | 104.96
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 | 11 | 107:HOL BUS1 | 40 | 40 | 104.96
130718 Q535_POI 138 130717 Q535_PSU 34.5 1 Max |  |  |  |  | 107.35

## N-1-1_SLL_Alt
Monitored Facility | Areas | First Level Scenario | Cont Name | Rate Base (MVA) | Rate Cont (MVA) | SCD AC %Loading
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | NNC-B | NNC-C | 155 | 210 | 343.07
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | NNC-C | NNC-B | 155 | 210 | 343.04
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | NNC-B | Y50 | 155 | 210 | 329.2
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | NNC-C | Y50 | 155 | 210 | 328.13
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | NNC-B | Base Case | 155 | 210 | 245.49
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | NNC-C | Base Case | 155 | 210 | 244.7
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 155 | 210 | 236.48
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 155 | 210 | 234.67
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | SHORE RD 345/138 Bank #2 | Y50 | 155 | 210 | 228.52
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | 69-533 | Y50 | 155 | 210 | 228.13
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | NNC-B | 20 :SRD BUS1 | 155 | 210 | 228.04
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | 69-531 | Y50 | 155 | 210 | 227.99
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | 69-532 | Y50 | 155 | 210 | 227.95
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | BELMR 69/34.5 kV BK#5 | Y50 | 155 | 210 | 227.67
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | SHORE RD 345/138 Bank #2 | SHORE RD 345/138 Bank #1 | 155 | 210 | 227.58
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | GLNWD NO 138/69 Bank #5 | Y50 | 155 | 210 | 227.35
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | 138-564 | Y50 | 155 | 210 | 227.31
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | NNC-C | 20 :SRD BUS1 | 155 | 210 | 227.3
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | SHORE RD 345/138 Bank #1 | Y50 | 155 | 210 | 227.25
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | NNC-B | 21 :SRD BUS2 | 155 | 210 | 226.73
121408 NE_601_NY 138 129343 NRTHPT P 138 1 Max | [5 empty] | 343.07
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | NNC-C | NNC-1C | 155 | 210 | 342.95
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | NNC-C | NNC-A | 155 | 210 | 342.95
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | NNC-1C | NNC-C | 155 | 210 | 342.84
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | NNC-A | NNC-C | 155 | 210 | 342.84
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | NNC-1C | Y50 | 155 | 210 | 327.94
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | NNC-A | Y50 | 155 | 210 | 327.94
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | NNC-C | Y50 | 155 | 210 | 327.13
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | NNC-A | Base Case | 155 | 210 | 245.01
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | NNC-1C | Base Case | 155 | 210 | 245.01
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | NNC-C | Base Case | 155 | 210 | 243.96
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 155 | 210 | 235.76
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 155 | 210 | 233.96
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | SHORE RD 345/138 Bank #2 | Y50 | 155 | 210 | 227.83
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | NNC-A | 20 :SRD BUS1 | 155 | 210 | 227.54
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | NNC-1C | 20 :SRD BUS1 | 155 | 210 | 227.54
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | 69-533 | Y50 | 155 | 210 | 227.44
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | 69-531 | Y50 | 155 | 210 | 227.3
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | 69-532 | Y50 | 155 | 210 | 227.25
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | BELMR 69/34.5 kV BK#5 | Y50 | 155 | 210 | 226.98
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | SHORE RD 345/138 Bank #2 | SHORE RD 345/138 Bank #1 | 155 | 210 | 226.89
121409 NE_602_NY 138 129343 NRTHPT P 138 2 Max | [5 empty] | 342.95
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-B | NNC-A | 155 | 210 | 342.76
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-B | NNC-1C | 155 | 210 | 342.76
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-1C | NNC-B | 155 | 210 | 342.62
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-A | NNC-B | 155 | 210 | 342.62
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-B | Y50 | 155 | 210 | 326
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-A | Y50 | 155 | 210 | 325.75
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-1C | Y50 | 155 | 210 | 325.75
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-A | Base Case | 155 | 210 | 243.4
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-1C | Base Case | 155 | 210 | 243.4
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-B | Base Case | 155 | 210 | 243.14
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 155 | 210 | 234.19
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 155 | 210 | 232.4
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | SHORE RD 345/138 Bank #2 | Y50 | 155 | 210 | 226.31
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-1C | 20 :SRD BUS1 | 155 | 210 | 226.03
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-A | 20 :SRD BUS1 | 155 | 210 | 226.03
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | 69-533 | Y50 | 155 | 210 | 225.93
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | NNC-B | 20 :SRD BUS1 | 155 | 210 | 225.84
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | 69-531 | Y50 | 155 | 210 | 225.79
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | 69-532 | Y50 | 155 | 210 | 225.74
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | BELMR 69/34.5 kV BK#5 | Y50 | 155 | 210 | 225.47
121410 NE_603_NY 138 129343 NRTHPT P 138 3 Max | [5 empty] | 342.76
126262 BUCHANAN N 345 126267 E VIEW 2N 345 1 | 8/9 | MILLWOOD - SPRNBRK W99/W64 345 | T:W82&W85 | 1918 | 2121 | 107.95
126262 BUCHANAN N 345 126267 E VIEW 2N 345 1 Max | [5 empty] | 107.95
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | RAMAPO - BUCHN 345 Y94 | T:F30&F31_UC21 | 1793 | 1994 | 132.16
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | BUCH - SPRNBRK W93/W79 345 | T:F30&F31_UC21 | 1793 | 1994 | 126.32
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | RAMAPO - BUCHN 345 Y94 | T:F38&F39_UC02 | 1793 | 1994 | 124.29
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | BUCH - SPRNBRK W93/W79 345 | T:F38&F39_UC02 | 1793 | 1994 | 119.79
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | EFISHKILL - PLSNTVLLE F39/Y87 345 | T:F30&F31_UC21 | 1793 | 1994 | 118.83
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | DUNWOODIE-PLEASANTVILLE W90/W74 | T:F30&F31_UC21 | 1793 | 1994 | 118.63
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | DUNWOODIE-PLEASANTVILLE W89/W73 | T:F30&F31_UC21 | 1793 | 1994 | 118.27
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | EFISHKILL - PLSNTVLLE F38/Y86 345 | T:F30&F31_UC21 | 1793 | 1994 | 116.23
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | RAMAPO - BUCHN 345 Y94 | SB:FISH345_5 | 1793 | 1994 | 104.78
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | RAMAPO - BUCHN 345 Y94 | SB:FISH345_3 | 1793 | 1994 | 102.89
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | RAMAPO - BUCHN 345 Y94 | SB:MILL345_11 | 1793 | 1994 | 102.56
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | RAMAPO - BUCHN 345 Y94 | SB:MILL345_6 | 1793 | 1994 | 102.55
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | RAMAPO - BUCHN 345 Y94 | SB:MILL345_4 | 1793 | 1994 | 102.17
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | RAMAPO - BUCHN 345 Y94 | PV - MILLWOOD 345 F30/W80 | 1793 | 1994 | 102
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | RAMAPO - BUCHN 345 Y94 | PV - MILLWOOD F31/W81 345 | 1793 | 1994 | 101.98
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | PV - MILLWOOD 345 F30/W80 | T:F38&F39_UC02 | 1793 | 1994 | 101.87
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | PV - MILLWOOD F31/W81 345 | T:F38&F39_UC02 | 1793 | 1994 | 101.79
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 | 8/7 | RAMAPO - BUCHN 345 Y94 | OE:MILLW_W80 | 1793 | 1994 | 101.46
126263 BUCHANAN S 345 146874 LOVETT345 ST 345 1 Max | [5 empty] | 132.16
126266 DUNWOODIE 345 126292 PL VILLE 345 1 | 9 | DUNWOODIE-PLEASANTVILLE W90/W74 | T:F30&F31_UC21 | 2213 | 2402 | 102.68
126266 DUNWOODIE 345 126292 PL VILLE 345 1 | 9 | EFISHKILL - PLSNTVLLE F39/Y87 345 | T:F30&F31_UC21 | 2213 | 2402 | 101
126266 DUNWOODIE 345 126292 PL VILLE 345 1 Max | [5 empty] | 102.68
126266 DUNWOODIE 345 126293 PL VILLW 345 1 | 9 | DUNWOODIE-PLEASANTVILLE W89/W73 | T:F30&F31_UC21 | 2213 | 2402 | 105.04
126266 DUNWOODIE 345 126293 PL VILLW 345 1 | 9 | EFISHKILL - PLSNTVLLE F38/Y86 345 | T:F30&F31_UC21 | 2213 | 2402 | 101.41
126266 DUNWOODIE 345 126293 PL VILLW 345 1 Max | [5 empty] | 105.04
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_8 | 823 | 953 | 153.88
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_8 | 823 | 953 | 153.58
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M51 | DNWDIE - MOTTHAVEN 345 72 | 823 | 953 | 151.85
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_3 | 823 | 953 | 151.76
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_7 | 823 | 953 | 151.76
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M52 | DNWDIE - MOTTHAVEN 345 72 | 823 | 953 | 151.5
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_7 | 823 | 953 | 151.42
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_3 | 823 | 953 | 151.42
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | DNWDIE - MOTTHAVEN 345 72 | Y50 | 823 | 953 | 148.3
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | DNWDIE - MOTTHAVEN 345 72 | SB:DUNW345_4 | 823 | 953 | 148.15
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | DNWDIE - MOTTHAVEN 345 72 | SB:DUNW345_6 | 823 | 953 | 147.65
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RNS4 | 823 | 953 | 143.84
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RNS5 | 823 | 953 | 143.56
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:W49_5 | 823 | 953 | 141.54
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:W49_3 | 823 | 953 | 140.56
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RS4 | 823 | 953 | 140.52
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SPRNBRK - W49ST 345 M52 | 823 | 953 | 140.52
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:W49_2 | 823 | 953 | 140.03
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:W49_BTN | 823 | 953 | 140.03
126266 DUNWOODIE 345 126600 REAC71 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SPRNBRK - W49ST 345 M51 | 823 | 953 | 139.98
126266 DUNWOODIE 345 126600 REAC71 345 BY Max | [5 empty] | 153.88
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_3 | 823 | 953 | 155.33
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_3 | 823 | 953 | 154.87
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_2 | 823 | 953 | 150.4
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_BTE | 823 | 953 | 150.36
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M51 | DNWDIE - MOTTHAVEN 345 71 | 823 | 953 | 150.26
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M52 | DNWDIE - MOTTHAVEN 345 71 | 823 | 953 | 149.93
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_2 | 823 | 953 | 149.88
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_BTE | 823 | 953 | 149.85
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | DNWDIE - MOTTHAVEN 345 71 | Y50 | 823 | 953 | 146.35
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | DNWDIE - MOTTHAVEN 345 71 | SB:DUNW345_4 | 823 | 953 | 146.24
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | DNWDIE - MOTTHAVEN 345 71 | SB:DUNW345_6 | 823 | 953 | 146.15
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RNS4 | 823 | 953 | 140.32
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RNS5 | 823 | 953 | 140.05
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:W49_5 | 823 | 953 | 138.08
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:W49_3 | 823 | 953 | 137.12
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RS4 | 823 | 953 | 137.09
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SPRNBRK - W49ST 345 M52 | 823 | 953 | 137.08
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:W49_BTN | 823 | 953 | 136.6
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:W49_2 | 823 | 953 | 136.6
126266 DUNWOODIE 345 126601 REAC72 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RS5 | 823 | 953 | 136.55
126266 DUNWOODIE 345 126601 REAC72 345 BY Max | [5 empty] | 155.33
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | Base Case | 780 | 1028 | 409.33
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | 8 :VST BUS1 | 780 | 1028 | 375.28
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | VLY STRM 138/69 kV Bank #5 | 780 | 1028 | 375.14
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | JAMCA - VLLYSTRM 901L&M 138 | 780 | 1028 | 375.09
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | 901 L&M | 780 | 1028 | 375.09
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | VLY STRM 138 kV P.A.R. | 780 | 1028 | 373.77
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | E.G.C. 345 kV P.A.R. #1 | Base Case | 780 | 1028 | 344.39
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | EGC REA | Base Case | 780 | 1028 | 344.38
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | E.G.C. 345 kV P.A.R. #2 | Base Case | 780 | 1028 | 344.25
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | Northport-Norwalk NNC-3C | 780 | 1028 | 337.21
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | NNC-3C | 780 | 1028 | 337.21
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | 67 :NPT 1300 | 780 | 1028 | 337.16
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | 72 :NPT BUS1-2 | 780 | 1028 | 337.16
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | 74 :NPT 1410 | 780 | 1028 | 337.08
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | SPRNBRK - TREMONT X28 345 | Base Case | 780 | 1028 | 330.17
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | NNC-3C | SB:SPRA345_RNS2 | 780 | 1028 | 329.92
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Northport-Norwalk NNC-3C | SB:SPRA345_RNS2 | 780 | 1028 | 329.92
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | GOWANUS 345/138 2TR | Base Case | 780 | 1028 | 329.12
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | SPRNBRK - ACDMY 345 M29 | Base Case | 780 | 1028 | 328.71
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | ASTORIA 345/138 PS | Base Case | 780 | 1028 | 328.22
126266 DUNWOODIE 345 128835 SHORE RD 345 1 Max | [5 empty] | 409.33
126267 E VIEW 2N 345 126298 SPRAINBROOK 345 1 | 9 | MILLWOOD - SPRNBRK W99/W64 345 | T:W82&W85 | 2079 | 2512 | 102.74
126267 E VIEW 2N 345 126298 SPRAINBROOK 345 1 Max | [5 empty] | 102.74
126268 E VIEW 1N 345 126291 MILLWOOD 345 1 | 9/8 | RAMAPO - BUCHN 345 Y94 | T:W82&W85 | 2558 | 2971 | 109.22
126268 E VIEW 1N 345 126291 MILLWOOD 345 1 | 9/8 | BUCH - SPRNBRK W93/W79 345 | T:W82&W85 | 2558 | 2971 | 108.17
126268 E VIEW 1N 345 126291 MILLWOOD 345 1 | 9/8 | DUNWOODIE-PLEASANTVILLE W90/W74 | T:W82&W85 | 2558 | 2971 | 102.56
126268 E VIEW 1N 345 126291 MILLWOOD 345 1 | 9/8 | EFISHKILL - PLSNTVLLE F39/Y87 345 | T:W82&W85 | 2558 | 2971 | 102.18
126268 E VIEW 1N 345 126291 MILLWOOD 345 1 | 9/8 | DUNWOODIE-PLEASANTVILLE W89/W73 | T:W82&W85 | 2558 | 2971 | 102.04
126268 E VIEW 1N 345 126291 MILLWOOD 345 1 Max | [5 empty] | 109.22
126268 E VIEW 1N 345 126298 SPRAINBROOK 345 1 | 9 | BUCH - SPRNBRK W93/W79 345 | T:W82&W85 | 2558 | 2971 | 117.84
126268 E VIEW 1N 345 126298 SPRAINBROOK 345 1 | 9 | RAMAPO - BUCHN 345 Y94 | T:W82&W85 | 2558 | 2971 | 107.87
126268 E VIEW 1N 345 126298 SPRAINBROOK 345 1 | 9 | DUNWOODIE-PLEASANTVILLE W90/W74 | T:W82&W85 | 2558 | 2971 | 104.59
126268 E VIEW 1N 345 126298 SPRAINBROOK 345 1 | 9 | EFISHKILL - PLSNTVLLE F39/Y87 345 | T:W82&W85 | 2558 | 2971 | 104.25
126268 E VIEW 1N 345 126298 SPRAINBROOK 345 1 | 9 | DUNWOODIE-PLEASANTVILLE W89/W73 | T:W82&W85 | 2558 | 2971 | 104.16
126268 E VIEW 1N 345 126298 SPRAINBROOK 345 1 | 9 | EFISHKILL - PLSNTVLLE F38/Y86 345 | T:W82&W85 | 2558 | 2971 | 101.81
126268 E VIEW 1N 345 126298 SPRAINBROOK 345 1 Max | [5 empty] | 117.84
126269 E VIEW 2S 345 126291 MILLWOOD 345 1 | 9/8 | MILLWOOD - SPRNBRK W85/W78 345 | T:W99&W93 | 2558 | 2971 | 104.49
126269 E VIEW 2S 345 126291 MILLWOOD 345 1 Max | [5 empty] | 104.49
126269 E VIEW 2S 345 126298 SPRAINBROOK 345 2 | 9 | MILLWOOD - SPRNBRK W85/W78 345 | T:W99&W93 | 2079 | 2512 | 134.95
126269 E VIEW 2S 345 126298 SPRAINBROOK 345 2 Max | [5 empty] | 134.95
126270 E VIEW 1S 345 126291 MILLWOOD 345 1 | 9/8 | MILLWOOD - SPRNBRK W82/W65 345 | T:W99&W93 | 2558 | 2971 | 104.49
126270 E VIEW 1S 345 126291 MILLWOOD 345 1 Max | [5 empty] | 104.49
126270 E VIEW 1S 345 126298 SPRAINBROOK 345 1 | 9 | MILLWOOD - SPRNBRK W82/W65 345 | T:W99&W93 | 2558 | 2971 | 114.1
126270 E VIEW 1S 345 126298 SPRAINBROOK 345 1 Max | [5 empty] | 114.1
126272 E13ST 45 345 126304 W 49 ST 345 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | T:F38&F39_UC02 | 857 | 1121 | 116.5
126272 E13ST 45 345 126304 W 49 ST 345 1 Max | [5 empty] | 116.5
126272 E13ST 45 345 126645 FARRAGUT EAS 345 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | T:F38&F39_UC02 | 859 | 1049 | 136.04
126272 E13ST 45 345 126645 FARRAGUT EAS 345 1 Max | [5 empty] | 136.04
126273 E13ST 46 345 126304 W 49 ST 345 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | T:F38&F39_UC02 | 857 | 1121 | 118.97
126273 E13ST 46 345 126304 W 49 ST 345 1 Max | [5 empty] | 118.97
126273 E13ST 46 345 126644 FARRAGUT WES 345 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | T:F38&F39_UC02 | 873 | 1060 | 134.68
126273 E13ST 46 345 126644 FARRAGUT WES 345 1 Max | [5 empty] | 134.68
126277 FARRAGUT 345 126643 RAINEY EAST 345 3 | 10 | RAINEYW - FARRAGUTE 345 61 | SB:RAIN345_6E | 776 | 933 | 110.15
126277 FARRAGUT 345 126643 RAINEY EAST 345 3 | 10 | RAINEYE - FARRAGUT WEST 345 62 | SB:RAIN345_3W | 776 | 933 | 106.04
126277 FARRAGUT 345 126643 RAINEY EAST 345 3 | 10 | RAINEYE - FARRAGUT WEST 345 62 | SB:RAIN345_2W | 776 | 933 | 105.01
126277 FARRAGUT 345 126643 RAINEY EAST 345 3 | 10 | RAINEYE - FARRAGUT WEST 345 62 | SB:FARR345_2E | 776 | 933 | 104.92
126277 FARRAGUT 345 126643 RAINEY EAST 345 3 | 10 | RAINEYE - FARRAGUT WEST 345 62 | SB:FARR345_3E | 776 | 933 | 104.83
126277 FARRAGUT 345 126643 RAINEY EAST 345 3 | 10 | RAINEYE - FARRAGUT WEST 345 62 | RAINEYW - FARRAGUTE 345 61 | 776 | 933 | 104.72
126277 FARRAGUT 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M51 | SB:W49_5 | 776 | 933 | 103.82
126277 FARRAGUT 345 126643 RAINEY EAST 345 3 | 10 | RAINEYW - FARRAGUTE 345 61 | SB:FARR345_4W | 776 | 933 | 103.03
126277 FARRAGUT 345 126643 RAINEY EAST 345 3 | 10 | RAINEYW - FARRAGUTE 345 61 | RAINEYE - FARRAGUT WEST 345 62 | 776 | 933 | 102.96
126277 FARRAGUT 345 126643 RAINEY EAST 345 3 | 10 | RAINEYW - FARRAGUTE 345 61 | SB:FARR345_5W | 776 | 933 | 102.42
126277 FARRAGUT 345 126643 RAINEY EAST 345 3 | 10 | RAINEYW - FARRAGUTE 345 61 | SB:RAIN345_7E | 776 | 933 | 101.48
126277 FARRAGUT 345 126643 RAINEY EAST 345 3 Max | [5 empty] | 110.15
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | SIN:340-Hellgate#1-Astoria E | Y50 | 143 | 178 | 189.51
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | SIN:350 Hellgate#4-Astoria E | Y50 | 143 | 178 | 189.43
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | NNC-1C | Y50 | 143 | 178 | 188.49
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | NNC-A | Y50 | 143 | 178 | 188.49
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | 138-677 | Y50 | 143 | 178 | 188.37
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | 69-863 | Y50 | 143 | 178 | 188.33
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | 138-368 | Y50 | 143 | 178 | 188.21
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | 138-367 | Y50 | 143 | 178 | 188.21
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | 138-881 NEW | Y50 | 143 | 178 | 187.57
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | LKE SCSS 138/69 Bank #5 | Y50 | 143 | 178 | 187.43
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | SIN:340-Hellgate#1-Astoria E | SB:DUNW345_4 | 143 | 178 | 187.3
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | 138-881 | Y50 | 143 | 178 | 187.3
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | S:E13TH_M55 | Y50 | 143 | 178 | 187.25
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | S:E13TH_46 | Y50 | 143 | 178 | 187.24
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | SIN:350 Hellgate#4-Astoria E | SB:DUNW345_4 | 143 | 178 | 187.08
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | S:E13TH_45 | Y50 | 143 | 178 | 186.9
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | S:E13TH_M54 | Y50 | 143 | 178 | 186.89
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | FARRAGUTW 345/138 4TR | Y50 | 143 | 178 | 186.49
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | FARRAGUTE 345/138 5TR | Y50 | 143 | 178 | 186.44
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | MILLWOOD 345/138 TA2 | Y50 | 143 | 178 | 186.41
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 Max | [5 empty] | 189.51
126290 LADENTWN 345 126297 RAMAPO 345 1 | 7 | RAMAPO - BUCHN 345 Y94 | T:F30&F31_UC21 | 1918 | 2121 | 107.39
126290 LADENTWN 345 126297 RAMAPO 345 1 | 7 | BUCH - SPRNBRK W93/W79 345 | T:F30&F31_UC21 | 1918 | 2121 | 102.13
126290 LADENTWN 345 126297 RAMAPO 345 1 Max | [5 empty] | 107.39
126290 LADENTWN 345 146874 LOVETT345 ST 345 1 | 7 | RAMAPO - BUCHN 345 Y94 | T:F30&F31_UC21 | 1793 | 1994 | 119.12
126290 LADENTWN 345 146874 LOVETT345 ST 345 1 | 7 | BUCH - SPRNBRK W93/W79 345 | T:F30&F31_UC21 | 1793 | 1994 | 113.66
126290 LADENTWN 345 146874 LOVETT345 ST 345 1 | 7 | RAMAPO - BUCHN 345 Y94 | T:F38&F39_UC02 | 1793 | 1994 | 111.71
126290 LADENTWN 345 146874 LOVETT345 ST 345 1 | 7 | BUCH - SPRNBRK W93/W79 345 | T:F38&F39_UC02 | 1793 | 1994 | 107.51
126290 LADENTWN 345 146874 LOVETT345 ST 345 1 | 7 | EFISHKILL - PLSNTVLLE F39/Y87 345 | T:F30&F31_UC21 | 1793 | 1994 | 106.48
126290 LADENTWN 345 146874 LOVETT345 ST 345 1 | 7 | DUNWOODIE-PLEASANTVILLE W90/W74 | T:F30&F31_UC21 | 1793 | 1994 | 106.32
126290 LADENTWN 345 146874 LOVETT345 ST 345 1 | 7 | DUNWOODIE-PLEASANTVILLE W89/W73 | T:F30&F31_UC21 | 1793 | 1994 | 105.97
126290 LADENTWN 345 146874 LOVETT345 ST 345 1 | 7 | EFISHKILL - PLSNTVLLE F38/Y86 345 | T:F30&F31_UC21 | 1793 | 1994 | 104.11
126290 LADENTWN 345 146874 LOVETT345 ST 345 1 Max | [5 empty] | 119.12
126291 MILLWOOD 345 126306 WOOD B 345 1 | 8 | PV - MILLWOOD F31/W81 345 | T:F38&F39_UC02 | 2079 | 2512 | 103.82
126291 MILLWOOD 345 126306 WOOD B 345 1 Max | [5 empty] | 103.82
126291 MILLWOOD 345 126319 WOOD C 345 1 | 8 | PV - MILLWOOD 345 F30/W80 | T:F38&F39_UC02 | 2080 | 2510 | 103.72
126291 MILLWOOD 345 126319 WOOD C 345 1 Max | [5 empty] | 103.72
126293 PL VILLW 345 126305 WOOD A 345 1 | 9/8 | DUNWOODIE-PLEASANTVILLE W89/W73 | T:F30&F31_UC21 | 2213 | 2402 | 102.58
126293 PL VILLW 345 126305 WOOD A 345 1 Max | [5 empty] | 102.58
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | SHORE RD 345/138 Bank #2 | 17 :SRD1370 | 1046 | 1194 | 262.48
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 1046 | 1194 | 262.11
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | SHORE RD 345/138 Bank #1 | 18 :SRD1380 | 1046 | 1194 | 260.43
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 1046 | 1194 | 260.09
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | SIN:350 Hellgate#4-Astoria E | Y50 | 1046 | 1194 | 259.05
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | SIN:340-Hellgate#1-Astoria E | Y50 | 1046 | 1194 | 259.01
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 138-368 | Y50 | 1046 | 1194 | 258.82
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 138-367 | Y50 | 1046 | 1194 | 258.76
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | LKE SCSS 138/69 Bank #5 | Y50 | 1046 | 1194 | 258.66
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | SIN:340-Hellgate#1-Astoria E | SB:DUNW345_4 | 1046 | 1194 | 258.55
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | SIN:350 Hellgate#4-Astoria E | SB:DUNW345_4 | 1046 | 1194 | 258.5
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | LKE SCSS 138/69 Bank #5 | SB:DUNW345_6 | 1046 | 1194 | 258.47
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 138-367 | SB:DUNW345_6 | 1046 | 1194 | 257.76
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | DNWDIE - MOTTHAVEN 345 71 | SB:DUNW345_6 | 1046 | 1194 | 257.75
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 138-368 | SB:DUNW345_6 | 1046 | 1194 | 257.75
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 138-368 | SB:DUNW345_4 | 1046 | 1194 | 257.71
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | 138-367 | SB:DUNW345_4 | 1046 | 1194 | 257.64
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | LKE SCSS 138/69 Bank #5 | SB:DUNW345_4 | 1046 | 1194 | 257.62
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | NNC-B | Y50 | 1046 | 1194 | 257.06
126298 SPRAINBROOK 345 126299 REACBUS 345 SR | 9 | NNC-C | Y50 | 1046 | 1194 | 257.05
126298 SPRAINBROOK 345 126299 REACBUS 345 SR Max | [5 empty] | 262.48
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | T:F38&F39_UC02 | 887 | 1062 | 174.92
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_5 | 887 | 1062 | 160.34
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_3 | 887 | 1062 | 159.88
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SPRNBRK - W49ST 345 M52 | 887 | 1062 | 159.8
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:SPRA345_RS4 | 887 | 1062 | 158.04
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_5 | 887 | 1062 | 157.13
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_7 | 887 | 1062 | 156.89
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:SPRA345_RNS4 | 887 | 1062 | 155.22
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RS3 | 887 | 1062 | 154.27
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1062 | 152.06
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RNS3 | 887 | 1062 | 147.56
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:SPRA345_RS3 | 887 | 1062 | 128.2
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1062 | 128.13
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:DUNW345_5 | 887 | 1062 | 128.12
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:DUNW345_7 | 887 | 1062 | 128.12
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | Y49 | SB:DUNW345_5 | 887 | 1062 | 126.9
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | Y49 | SB:DUNW345_7 | 887 | 1062 | 126.85
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | Y49 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1062 | 125.73
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:DUNW345_8 | 887 | 1062 | 125.12
126298 SPRAINBROOK 345 126517 REACM51 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | DUNWOODIE-PLEASANTVILLE W90/W74 | 887 | 1062 | 125.04
126298 SPRAINBROOK 345 126517 REACM51 345 BY Max | [5 empty] | 174.92
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | T:F38&F39_UC02 | 887 | 1062 | 174.92
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_BTN | 887 | 1062 | 159.88
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_2 | 887 | 1062 | 159.88
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SPRNBRK - W49ST 345 M51 | 887 | 1062 | 159.8
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:SPRA345_RS5 | 887 | 1062 | 158.04
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_5 | 887 | 1062 | 157.73
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_7 | 887 | 1062 | 157.49
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RS3 | 887 | 1062 | 154.95
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:SPRA345_RNS5 | 887 | 1062 | 154.91
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1062 | 152.47
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RNS3 | 887 | 1062 | 147.99
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:SPRA345_RS3 | 887 | 1062 | 128.2
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1062 | 128.13
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:DUNW345_5 | 887 | 1062 | 128.12
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:DUNW345_7 | 887 | 1062 | 128.12
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | Y49 | SB:DUNW345_5 | 887 | 1062 | 126.9
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | Y49 | SB:DUNW345_7 | 887 | 1062 | 126.85
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | Y49 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1062 | 125.73
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - DUNWDIE 345 W75 | SB:DUNW345_8 | 887 | 1062 | 125.12
126298 SPRAINBROOK 345 126518 REACM52 345 BY | 9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_3 | 887 | 1062 | 125.05
126298 SPRAINBROOK 345 126518 REACM52 345 BY Max | [5 empty] | 174.92
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | SHORE RD 345/138 Bank #2 | 17 :SRD1370 | 770 | 990 | 321.29
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 770 | 990 | 320.83
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | SHORE RD 345/138 Bank #1 | 18 :SRD1380 | 770 | 990 | 318.84
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 770 | 990 | 318.44
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 138-362 | Base Case | 770 | 990 | 317.81
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | NNC-3C | Base Case | 770 | 990 | 317.57
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | Northport-Norwalk NNC-3C | Base Case | 770 | 990 | 317.57
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | SIN:350 Hellgate#4-Astoria E | Y50 | 770 | 990 | 317.33
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | SIN:340-Hellgate#1-Astoria E | Y50 | 770 | 990 | 317.28
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 138-368 | Y50 | 770 | 990 | 316.89
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | SIN:340-Hellgate#1-Astoria E | SB:DUNW345_4 | 770 | 990 | 316.86
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 138-367 | Y50 | 770 | 990 | 316.82
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | SIN:350 Hellgate#4-Astoria E | SB:DUNW345_4 | 770 | 990 | 316.79
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | LKE SCSS 138/69 Bank #5 | Y50 | 770 | 990 | 316.7
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | LKE SCSS 138/69 Bank #5 | SB:DUNW345_6 | 770 | 990 | 316.64
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | DNWDIE - MOTTHAVEN 345 71 | SB:DUNW345_6 | 770 | 990 | 315.96
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 138-367 | SB:DUNW345_6 | 770 | 990 | 315.77
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 138-368 | SB:DUNW345_6 | 770 | 990 | 315.75
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 138-368 | SB:DUNW345_4 | 770 | 990 | 315.71
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 138-367 | SB:DUNW345_4 | 770 | 990 | 315.63
126299 REACBUS 345 147857 DVNPT NK 345 1 Max | [5 empty] | 321.29
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | T:F38&F39_UC02 | 887 | 1061 | 187.93
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_5 | 887 | 1061 | 176.51
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_3 | 887 | 1061 | 176.07
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SPRNBRK - W49ST 345 M52 | 887 | 1061 | 176.01
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:SPRA345_RS4 | 887 | 1061 | 174.77
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_5 | 887 | 1061 | 174.44
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_7 | 887 | 1061 | 174.2
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:SPRA345_RNS4 | 887 | 1061 | 173.03
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RS3 | 887 | 1061 | 171.74
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1061 | 169.42
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RNS3 | 887 | 1061 | 166.26
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_3 | 887 | 1061 | 145.53
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_8 | 887 | 1061 | 144.19
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:DUNW345_5 | 887 | 1061 | 141.95
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:DUNW345_7 | 887 | 1061 | 141.95
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:SPRA345_RS3 | 887 | 1061 | 141.89
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1061 | 141.86
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | DUNWOODIE-PLEASANTVILLE W90/W74 | 887 | 1061 | 140.6
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:DUNW345_8 | 887 | 1061 | 140.57
126304 W 49 ST 345 126517 REACM51 345 1 | 10/9 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_2 | 887 | 1061 | 140.46
126304 W 49 ST 345 126517 REACM51 345 1 Max | [5 empty] | 187.93
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | T:F38&F39_UC02 | 887 | 1061 | 187.93
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_2 | 887 | 1061 | 176.07
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:W49_BTN | 887 | 1061 | 176.06
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SPRNBRK - W49ST 345 M51 | 887 | 1061 | 176.01
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_5 | 887 | 1061 | 175.17
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_7 | 887 | 1061 | 174.93
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:SPRA345_RS5 | 887 | 1061 | 174.77
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - DUNWDIE 345 W75 | SB:SPRA345_RNS5 | 887 | 1061 | 172.85
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RS3 | 887 | 1061 | 172.59
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1061 | 169.95
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RNS3 | 887 | 1061 | 166.79
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_3 | 887 | 1061 | 145.78
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_8 | 887 | 1061 | 144.5
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:DUNW345_5 | 887 | 1061 | 141.95
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:DUNW345_7 | 887 | 1061 | 141.95
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:SPRA345_RS3 | 887 | 1061 | 141.89
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | DUNWOODIE-PLEASANTVILLE W90/W74 | SPRNBRK - DUNWDIE 345 W75 | 887 | 1061 | 141.86
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_2 | 887 | 1061 | 140.86
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_BTE | 887 | 1061 | 140.84
126304 W 49 ST 345 126518 REACM52 345 2 | 10/9 | SPRNBRK - W49ST 345 M51 | DNWDIE - MOTTHAVEN 345 71 | 887 | 1061 | 140.69
126304 W 49 ST 345 126518 REACM52 345 2 Max | [5 empty] | 187.93
126317 38M72 TAP 138 126551 ASTOR T5 TAP 138 1 | 10 | GEN: OSW W49 Street 5 | Base Case | 210 | 297 | 121.2
126317 38M72 TAP 138 126551 ASTOR T5 TAP 138 1 Max | [5 empty] | 121.2
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 217 | 348 | 362.13
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 217 | 348 | 362.07
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | EFISHKILL - PLSNTVLLE F39/Y87 345 | Base Case | 217 | 348 | 322.36
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SIN:340-Hellgate#1-Astoria E | 217 | 348 | 315.37
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SIN:340-Hellgate#1-Astoria E | 217 | 348 | 315.36
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | DUNWOODIE-PLEASANTVILLE W89/W73 | Base Case | 217 | 348 | 305.86
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | Base Case | 217 | 348 | 293.98
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 217 | 348 | 289.14
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | EFISHKILL - PLSNTVLLE F39/Y87 345 | SIN:340-Hellgate#1-Astoria E | 217 | 348 | 278.43
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | DUNWOODIE-PLEASANTVILLE W89/W73 | SIN:340-Hellgate#1-Astoria E | 217 | 348 | 264.27
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | SIN:340-Hellgate#1-Astoria E | 217 | 348 | 252.98
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | SIN:340-Hellgate#1-Astoria E | 217 | 348 | 248.34
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | 20 :SRD BUS1 | 217 | 348 | 236.75
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | 20 :SRD BUS1 | 217 | 348 | 236.75
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | 21 :SRD BUS2 | 217 | 348 | 236.14
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | 21 :SRD BUS2 | 217 | 348 | 236.14
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | DUNWOODIE-PLEASANTVILLE W90/W74 | Base Case | 217 | 348 | 235.98
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SHORE RD 345/138 Bank #1 | 217 | 348 | 235.98
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SHORE RD 345/138 Bank #1 | 217 | 348 | 235.97
126334 ASTE-ERG 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Y49 | 217 | 348 | 235.4
126334 ASTE-ERG 138 126445 HG 4 138 1 Max | [5 empty] | 362.13
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 217 | 348 | 361.16
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 217 | 348 | 361.11
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | EFISHKILL - PLSNTVLLE F39/Y87 345 | Base Case | 217 | 348 | 321.49
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SIN:350 Hellgate#4-Astoria E | 217 | 348 | 314.97
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SIN:350 Hellgate#4-Astoria E | 217 | 348 | 314.96
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | DUNWOODIE-PLEASANTVILLE W89/W73 | Base Case | 217 | 348 | 304.82
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | Base Case | 217 | 348 | 293.01
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 217 | 348 | 288.38
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | EFISHKILL - PLSNTVLLE F39/Y87 345 | SIN:350 Hellgate#4-Astoria E | 217 | 348 | 278.07
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | DUNWOODIE-PLEASANTVILLE W89/W73 | SIN:350 Hellgate#4-Astoria E | 217 | 348 | 263.85
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | SIN:350 Hellgate#4-Astoria E | 217 | 348 | 252.59
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | SIN:350 Hellgate#4-Astoria E | 217 | 348 | 248.02
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M51 | 20 :SRD BUS1 | 217 | 348 | 236.11
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M52 | 20 :SRD BUS1 | 217 | 348 | 236.11
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M52 | 21 :SRD BUS2 | 217 | 348 | 235.51
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M51 | 21 :SRD BUS2 | 217 | 348 | 235.51
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SHORE RD 345/138 Bank #1 | 217 | 348 | 235.35
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SHORE RD 345/138 Bank #1 | 217 | 348 | 235.35
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | DUNWOODIE-PLEASANTVILLE W90/W74 | Base Case | 217 | 348 | 235.05
126352 ASTE-WRG 138 126442 HG 1 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Y49 | 217 | 348 | 234.77
126352 ASTE-WRG 138 126442 HG 1 138 1 Max | [5 empty] | 361.16
126352 ASTE-WRG 138 128244 ANNEX TIE 138 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | SIN:350 Hellgate#4-Astoria E | 319 | 353 | 101.48
126352 ASTE-WRG 138 128244 ANNEX TIE 138 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | SIN:340-Hellgate#1-Astoria E | 319 | 353 | 101.47
126352 ASTE-WRG 138 128244 ANNEX TIE 138 1 Max | [5 empty] | 101.48
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | Y49 | GEN: OSW Astoria 2 | 345 | 413 | 114.47
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | Y49 | 20 :SRD BUS1 | 345 | 413 | 110.89
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | PV - EFISHKILL 345 F36 | Y50 | 345 | 413 | 110.64
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | PV - EFISHKILL 345 F37 | Y50 | 345 | 413 | 110.64
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | Y49 | 21 :SRD BUS2 | 345 | 413 | 109.53
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | 138-366 | Y50 | 345 | 413 | 108.18
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 345 | 413 | 108.07
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | 138-365 | Y50 | 345 | 413 | 107.98
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | SHORE RD 345/138 Bank #2 | Y50 | 345 | 413 | 106.95
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | SHORE RD 345/138 Bank #2 | SHORE RD 345/138 Bank #1 | 345 | 413 | 106.56
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 345 | 413 | 106.31
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | Northport-Norwalk NNC-3C | GEN: OSW Astoria 2 | 345 | 413 | 106.07
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | NNC-3C | GEN: OSW Astoria 2 | 345 | 413 | 106.07
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | SHORE RD 345/138 Bank #1 | Y50 | 345 | 413 | 105.47
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | SHORE RD 345/138 Bank #1 | SHORE RD 345/138 Bank #2 | 345 | 413 | 105.03
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | MILLWOOD - SPRNBRK W85/W78 345 | GEN: OSW Astoria 2 | 345 | 413 | 103.35
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | MILLWOOD - SPRNBRK W82/W65 345 | GEN: OSW Astoria 2 | 345 | 413 | 103.34
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | 138-361 | Y50 | 345 | 413 | 102.86
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | 138-363 | Y50 | 345 | 413 | 102.71
126363 CORONA-S 138 126364 CORONA1R 138 1 | 10 | Y49 | SHORE RD 345/138 Bank #1 | 345 | 413 | 102.67
126363 CORONA-S 138 126364 CORONA1R 138 1 Max | [5 empty] | 114.47
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | Y49 | GEN: OSW Astoria 2 | 186 | 250 | 190.57
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | Y49 | 20 :SRD BUS1 | 186 | 250 | 183.03
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | PV - EFISHKILL 345 F37 | Y50 | 186 | 250 | 181.66
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | PV - EFISHKILL 345 F36 | Y50 | 186 | 250 | 181.66
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | Y49 | 21 :SRD BUS2 | 186 | 250 | 180.39
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | 138-366 | Y50 | 186 | 250 | 178.64
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | 138-365 | Y50 | 186 | 250 | 178.54
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 186 | 250 | 177.51
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | SHORE RD 345/138 Bank #2 | Y50 | 186 | 250 | 175.41
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | SHORE RD 345/138 Bank #2 | SHORE RD 345/138 Bank #1 | 186 | 250 | 174.74
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 186 | 250 | 174.68
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | NNC-3C | GEN: OSW Astoria 2 | 186 | 250 | 174.61
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | Northport-Norwalk NNC-3C | GEN: OSW Astoria 2 | 186 | 250 | 174.61
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | SHORE RD 345/138 Bank #1 | Y50 | 186 | 250 | 173.06
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | SHORE RD 345/138 Bank #1 | SHORE RD 345/138 Bank #2 | 186 | 250 | 172.3
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | MILLWOOD - SPRNBRK W85/W78 345 | GEN: OSW Astoria 2 | 186 | 250 | 170.22
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | MILLWOOD - SPRNBRK W82/W65 345 | GEN: OSW Astoria 2 | 186 | 250 | 170.21
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | 138-361 | Y50 | 186 | 250 | 169.1
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | 138-363 | Y50 | 186 | 250 | 168.86
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | Y49 | SHORE RD 345/138 Bank #1 | 186 | 250 | 168.11
126364 CORONA1R 138 126455 JAMAICA 138 1 Max | [5 empty] | 190.57
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | Y49 | GEN: OSW Astoria 2 | 186 | 250 | 200.12
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | 138-366 | Y50 | 186 | 250 | 194.43
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | 138-365 | Y50 | 186 | 250 | 194.36
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | Y49 | 20 :SRD BUS1 | 186 | 250 | 193.1
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | Y49 | 21 :SRD BUS2 | 186 | 250 | 189.98
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 186 | 250 | 189.34
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 186 | 250 | 188.4
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | PV - EFISHKILL 345 F36 | Y50 | 186 | 250 | 187.86
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | PV - EFISHKILL 345 F37 | Y50 | 186 | 250 | 187.86
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | SHORE RD 345/138 Bank #2 | Y50 | 186 | 250 | 186.92
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | SHORE RD 345/138 Bank #1 | Y50 | 186 | 250 | 186.53
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | SHORE RD 345/138 Bank #2 | SHORE RD 345/138 Bank #1 | 186 | 250 | 186.16
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | SHORE RD 345/138 Bank #1 | SHORE RD 345/138 Bank #2 | 186 | 250 | 185.69
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | 138-361 | Y50 | 186 | 250 | 185.33
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | 138-363 | Y50 | 186 | 250 | 185.14
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | 138-364 | Y50 | 186 | 250 | 183.86
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | DNWDIE - MOTTHAVEN 345 72 | Y50 | 186 | 250 | 180.44
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | DNWDIE - MOTTHAVEN 345 71 | Y50 | 186 | 250 | 180.42
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | RAINEYW - RAINEYMID TIE 345 | Y50 | 186 | 250 | 179.52
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | GLNWD SO 138/69 kV Bank #6 | Y50 | 186 | 250 | 179.4
126365 CORONA2R 138 126455 JAMAICA 138 1 Max | [5 empty] | 200.12
126370 DUN NO1R 138 126483 S CREEK W 138 1 | 9/10 | GEN: OSW Farragut 3 | Base Case | 170 | 279 | 105.62
126370 DUN NO1R 138 126483 S CREEK W 138 1 Max | [5 empty] | 105.62
126374 DUN SO1R 138 126385 E179 ST W 138 1 | 9/10 | SPRNBRK - W49ST 345 M51 | Base Case | 268 | 510 | 156.56
126374 DUN SO1R 138 126385 E179 ST W 138 1 | 9/10 | SPRNBRK - W49ST 345 M52 | Base Case | 268 | 510 | 156.46
126374 DUN SO1R 138 126385 E179 ST W 138 1 | 9/10 | DUNWOODIE-PLEASANTVILLE W89/W73 | Base Case | 268 | 510 | 147.64
126374 DUN SO1R 138 126385 E179 ST W 138 1 Max | [5 empty] | 156.56
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 208 | 342 | 377.77
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 208 | 342 | 377.71
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | EFISHKILL - PLSNTVLLE F39/Y87 345 | Base Case | 208 | 342 | 336.29
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SIN:340-Hellgate#1-Astoria E | 208 | 342 | 320.87
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SIN:340-Hellgate#1-Astoria E | 208 | 342 | 320.87
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | DUNWOODIE-PLEASANTVILLE W89/W73 | Base Case | 208 | 342 | 319.08
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | Base Case | 208 | 342 | 306.68
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 208 | 342 | 301.63
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | EFISHKILL - PLSNTVLLE F39/Y87 345 | SIN:340-Hellgate#1-Astoria E | 208 | 342 | 283.28
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | DUNWOODIE-PLEASANTVILLE W89/W73 | SIN:340-Hellgate#1-Astoria E | 208 | 342 | 268.89
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | SIN:340-Hellgate#1-Astoria E | 208 | 342 | 257.4
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | SIN:340-Hellgate#1-Astoria E | 208 | 342 | 252.68
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | DUNWOODIE-PLEASANTVILLE W90/W74 | Base Case | 208 | 342 | 246.17
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | 20 :SRD BUS1 | 208 | 342 | 240.89
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | 20 :SRD BUS1 | 208 | 342 | 240.88
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | 21 :SRD BUS2 | 208 | 342 | 240.28
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | 21 :SRD BUS2 | 208 | 342 | 240.27
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SHORE RD 345/138 Bank #1 | 208 | 342 | 240.1
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SHORE RD 345/138 Bank #1 | 208 | 342 | 240.1
126385 E179 ST W 138 126445 HG 4 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Y49 | 208 | 342 | 239.51
126385 E179 ST W 138 126445 HG 4 138 1 Max | [5 empty] | 377.77
126385 E179 ST W 138 126483 S CREEK W 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 204 | 336 | 130.06
126385 E179 ST W 138 126483 S CREEK W 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 204 | 336 | 129.23
126385 E179 ST W 138 126483 S CREEK W 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SPRNBRK - TREMONT X28 345 | 204 | 336 | 112.8
126385 E179 ST W 138 126483 S CREEK W 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SPRNBRK - TREMONT X28 345 | 204 | 336 | 112.51
126385 E179 ST W 138 126483 S CREEK W 138 1 | 10 | SPRNBRK - TREMONT X28 345 | Base Case | 204 | 336 | 106.6
126385 E179 ST W 138 126483 S CREEK W 138 1 | 10 | RAINEY-CORONA PAR 2 | Base Case | 204 | 336 | 102.21
126385 E179 ST W 138 126483 S CREEK W 138 1 Max | [5 empty] | 130.06
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | SIN:340-Hellgate#1-Astoria E | Y50 | 165 | 165 | 194.67
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | SIN:350 Hellgate#4-Astoria E | Y50 | 165 | 165 | 194.61
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | S:E13TH_46 | Y50 | 165 | 165 | 191.14
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | S:E13TH_M55 | Y50 | 165 | 165 | 191.12
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | S:E13TH_M54 | Y50 | 165 | 165 | 190.94
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | NNC-1C | Y50 | 165 | 165 | 190.88
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | NNC-A | Y50 | 165 | 165 | 190.88
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | 138-677 | Y50 | 165 | 165 | 190.76
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | 69-863 | Y50 | 165 | 165 | 190.72
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | S:E13TH_45 | Y50 | 165 | 165 | 190.69
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | 138-368 | Y50 | 165 | 165 | 190.62
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | 138-367 | Y50 | 165 | 165 | 190.62
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | MILLWOOD 345/138 TA2 | Y50 | 165 | 165 | 190.33
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | FARRAGUTW 345/138 4TR | Y50 | 165 | 165 | 190.33
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | FARRAGUTE 345/138 5TR | Y50 | 165 | 165 | 190.25
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | RAMAPO - SMAHWAH 69/J3410 345 | Y50 | 165 | 165 | 190.24
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | RAMAPO - SMAHWAH 70/K3411 345 | Y50 | 165 | 165 | 190.24
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | 69-858 | Y50 | 165 | 165 | 190.21
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | FARRAGUTE 345/138 3TR | Y50 | 165 | 165 | 190.19
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | PILGRIM 138/69 Bank #4 | Y50 | 165 | 165 | 190.18
126399 TAP X9 138 126437 FGT_X9 138 1 Max | [5 empty] | 194.67
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | Y49 | GEN: OSW Astoria 2 | 293 | 355 | 139.84
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | 138-366 | Y50 | 293 | 355 | 136.97
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | 138-365 | Y50 | 293 | 355 | 136.74
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | Y49 | 20 :SRD BUS1 | 293 | 355 | 135.92
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 293 | 355 | 134.05
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | Y49 | 21 :SRD BUS2 | 293 | 355 | 134
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 293 | 355 | 133.37
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | PV - EFISHKILL 345 F37 | Y50 | 293 | 355 | 133
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | PV - EFISHKILL 345 F36 | Y50 | 293 | 355 | 133
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | SHORE RD 345/138 Bank #2 | Y50 | 293 | 355 | 132.53
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | SHORE RD 345/138 Bank #1 | Y50 | 293 | 355 | 132.22
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | SHORE RD 345/138 Bank #2 | SHORE RD 345/138 Bank #1 | 293 | 355 | 132.01
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | SHORE RD 345/138 Bank #1 | SHORE RD 345/138 Bank #2 | 293 | 355 | 131.65
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | 138-361 | Y50 | 293 | 355 | 131.16
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | 138-363 | Y50 | 293 | 355 | 131.02
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | 138-364 | Y50 | 293 | 355 | 130.11
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | DNWDIE - MOTTHAVEN 345 72 | Y50 | 293 | 355 | 127.48
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | DNWDIE - MOTTHAVEN 345 71 | Y50 | 293 | 355 | 127.47
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | RAINEYW - RAINEYMID TIE 345 | Y50 | 293 | 355 | 126.83
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | GLNWD SO 138/69 kV Bank #6 | Y50 | 293 | 355 | 126.71
126415 CORONA-N 138 126365 CORONA2R 138 1 Max | [5 empty] | 139.84
126416 FOX HILLS 138 126434 GRENWOOD N 138 1 | 10 | GOWANUS 345/138 2TR | Base Case | 217 | 348 | 139.36
126416 FOX HILLS 138 126434 GRENWOOD N 138 1 | 10 | 138-261 | Base Case | 217 | 348 | 101.78
126416 FOX HILLS 138 126434 GRENWOOD N 138 1 Max | [5 empty] | 139.36
126416 FOX HILLS 138 126646 GRENWOOD S 138 1 | 10 | GOWANUS 345/138 2TR | Base Case | 217 | 348 | 138.9
126416 FOX HILLS 138 126646 GRENWOOD S 138 1 | 10 | 138-261 | Base Case | 217 | 348 | 101.39
126416 FOX HILLS 138 126646 GRENWOOD S 138 1 Max | [5 empty] | 138.9
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | RAINEYW - FARRAGUTE 345 61 | Base Case | 217 | 310 | 133.32
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 217 | 310 | 132.46
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 217 | 310 | 132.43
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | RAINEYW 345/138 8WTR | Base Case | 217 | 310 | 129.17
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | RAINEYE - FARRAGUTTIE 345 63 | Base Case | 217 | 310 | 121.04
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | RAINEYE - FARRAGUT WEST 345 62 | Base Case | 217 | 310 | 120.42
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | PV - MILLWOOD 345 F30/W80 | Base Case | 217 | 310 | 118.8
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | PV - MILLWOOD F31/W81 345 | Base Case | 217 | 310 | 118.8
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | MILLWOOD - SPRNBRK W99/W64 345 | Base Case | 217 | 310 | 118.8
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | RAMAPO - BUCHN 345 Y94 | Base Case | 217 | 310 | 118.71
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | Northport-Norwalk NNC-3C | Base Case | 217 | 310 | 118.66
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | BUCH - SPRNBRK W93/W79 345 | Base Case | 217 | 310 | 118.66
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | NNC-3C | Base Case | 217 | 310 | 118.66
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | 138-362 | Base Case | 217 | 310 | 118.6
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | MILLWOOD - SPRNBRK W85/W78 345 | Base Case | 217 | 310 | 118.57
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | MILLWOOD - SPRNBRK W82/W65 345 | Base Case | 217 | 310 | 118.57
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | Y49 | Base Case | 217 | 310 | 118.5
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | RAINEYW - FARRAGUTE 345 61 | GEN: OSW Astoria 2 | 217 | 310 | 101.79
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | SPRNBRK - W49ST 345 M51 | GEN: OSW Astoria 2 | 217 | 310 | 101.75
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | SPRNBRK - W49ST 345 M52 | GEN: OSW Astoria 2 | 217 | 310 | 101.72
126434 GRENWOOD N 138 126454 KENTTAP 138 1 Max | [5 empty] | 133.32
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 208 | 342 | 376.78
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 208 | 342 | 376.72
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | EFISHKILL - PLSNTVLLE F39/Y87 345 | Base Case | 208 | 342 | 335.39
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SIN:350 Hellgate#4-Astoria E | 208 | 342 | 320.47
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SIN:350 Hellgate#4-Astoria E | 208 | 342 | 320.47
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | DUNWOODIE-PLEASANTVILLE W89/W73 | Base Case | 208 | 342 | 318
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | Base Case | 208 | 342 | 305.68
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 208 | 342 | 300.85
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | EFISHKILL - PLSNTVLLE F39/Y87 345 | SIN:350 Hellgate#4-Astoria E | 208 | 342 | 282.92
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | DUNWOODIE-PLEASANTVILLE W89/W73 | SIN:350 Hellgate#4-Astoria E | 208 | 342 | 268.47
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | SIN:350 Hellgate#4-Astoria E | 208 | 342 | 257.01
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | SIN:350 Hellgate#4-Astoria E | 208 | 342 | 252.36
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | DUNWOODIE-PLEASANTVILLE W90/W74 | Base Case | 208 | 342 | 245.21
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M51 | 20 :SRD BUS1 | 208 | 342 | 240.25
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M52 | 20 :SRD BUS1 | 208 | 342 | 240.24
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M52 | 21 :SRD BUS2 | 208 | 342 | 239.64
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M51 | 21 :SRD BUS2 | 208 | 342 | 239.63
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M52 | SHORE RD 345/138 Bank #1 | 208 | 342 | 239.47
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M51 | SHORE RD 345/138 Bank #1 | 208 | 342 | 239.47
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Y49 | 208 | 342 | 238.88
126442 HG 1 138 126647 E179 ST E 138 1 Max | [5 empty] | 376.78
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | Y49 | Base Case | 178 | 363 | 164.66
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | SIN:340-Hellgate#1-Astoria E | Y50 | 178 | 363 | 160.84
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | SIN:350 Hellgate#4-Astoria E | Y50 | 178 | 363 | 160.8
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | S:E13TH_M54 | Y50 | 178 | 363 | 158.49
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | S:E13TH_46 | Y50 | 178 | 363 | 158.38
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | S:E13TH_M55 | Y50 | 178 | 363 | 158.36
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | S:E13TH_45 | Y50 | 178 | 363 | 158.33
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | 138-367 | Y50 | 178 | 363 | 158.24
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | 138-368 | Y50 | 178 | 363 | 158.24
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | NNC-B | Y50 | 178 | 363 | 158.15
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | NNC-C | Y50 | 178 | 363 | 158.14
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | MILLWOOD 345/138 TA2 | Y50 | 178 | 363 | 157.94
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | RAMAPO - SMAHWAH 69/J3410 345 | Y50 | 178 | 363 | 157.88
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | RAMAPO - SMAHWAH 70/K3411 345 | Y50 | 178 | 363 | 157.88
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | 69-858 | Y50 | 178 | 363 | 157.87
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | MILLWOOD 345/138 TA1 | Y50 | 178 | 363 | 157.84
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | PILGRIM 138/69 Bank #4 | Y50 | 178 | 363 | 157.84
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | RAINEYW 345/138 8ETR | Y50 | 178 | 363 | 157.83
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | NNC-A | Y50 | 178 | 363 | 157.75
126452 HUDAVE E 138 126455 JAMAICA 138 1 | 10 | NNC-1C | Y50 | 178 | 363 | 157.75
126452 HUDAVE E 138 126455 JAMAICA 138 1 Max | [5 empty] | 164.66
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | Y49 | Base Case | 178 | 363 | 164.66
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | SIN:340-Hellgate#1-Astoria E | Y50 | 178 | 363 | 160.84
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | SIN:350 Hellgate#4-Astoria E | Y50 | 178 | 363 | 160.8
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | S:E13TH_M54 | Y50 | 178 | 363 | 158.49
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | S:E13TH_46 | Y50 | 178 | 363 | 158.38
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | S:E13TH_M55 | Y50 | 178 | 363 | 158.36
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | S:E13TH_45 | Y50 | 178 | 363 | 158.33
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | 138-367 | Y50 | 178 | 363 | 158.24
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | 138-368 | Y50 | 178 | 363 | 158.24
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | NNC-B | Y50 | 178 | 363 | 158.15
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | NNC-C | Y50 | 178 | 363 | 158.14
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | MILLWOOD 345/138 TA2 | Y50 | 178 | 363 | 157.94
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | RAMAPO - SMAHWAH 69/J3410 345 | Y50 | 178 | 363 | 157.88
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | RAMAPO - SMAHWAH 70/K3411 345 | Y50 | 178 | 363 | 157.88
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | 69-858 | Y50 | 178 | 363 | 157.87
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | MILLWOOD 345/138 TA1 | Y50 | 178 | 363 | 157.84
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | PILGRIM 138/69 Bank #4 | Y50 | 178 | 363 | 157.84
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | RAINEYW 345/138 8ETR | Y50 | 178 | 363 | 157.83
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | NNC-A | Y50 | 178 | 363 | 157.75
126452 HUDAVE E 138 126455 JAMAICA 138 2 | 10 | NNC-1C | Y50 | 178 | 363 | 157.75
126452 HUDAVE E 138 126455 JAMAICA 138 2 Max | [5 empty] | 164.66
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | RAINEYW - FARRAGUTE 345 61 | Base Case | 217 | 310 | 131.89
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 217 | 310 | 130.97
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 217 | 310 | 130.94
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | RAINEYW 345/138 8WTR | Base Case | 217 | 310 | 127.27
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | RAINEYE - FARRAGUTTIE 345 63 | Base Case | 217 | 310 | 119.45
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | RAINEYE - FARRAGUT WEST 345 62 | Base Case | 217 | 310 | 118.73
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | MILLWOOD - SPRNBRK W99/W64 345 | Base Case | 217 | 310 | 117.11
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | PV - MILLWOOD 345 F30/W80 | Base Case | 217 | 310 | 117.11
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | PV - MILLWOOD F31/W81 345 | Base Case | 217 | 310 | 117.11
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | RAMAPO - BUCHN 345 Y94 | Base Case | 217 | 310 | 117.1
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | NNC-3C | Base Case | 217 | 310 | 117.05
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | Northport-Norwalk NNC-3C | Base Case | 217 | 310 | 117.05
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | 138-362 | Base Case | 217 | 310 | 116.96
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | BUCH - SPRNBRK W93/W79 345 | Base Case | 217 | 310 | 116.96
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | MILLWOOD - SPRNBRK W85/W78 345 | Base Case | 217 | 310 | 116.96
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | MILLWOOD - SPRNBRK W82/W65 345 | Base Case | 217 | 310 | 116.96
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | SPRNBRK - ACDMY 345 M29 | Base Case | 217 | 310 | 116.82
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | Y49 | Base Case | 217 | 310 | 116.8
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | ASTORIA 345/138 PS | Base Case | 217 | 310 | 116.62
126454 KENTTAP 138 126507 VERNON-W 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 217 | 310 | 107.5
126454 KENTTAP 138 126507 VERNON-W 138 1 Max | [5 empty] | 131.89
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 20 :SRD BUS1 | 319 | 375 | 389.59
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 21 :SRD BUS2 | 319 | 375 | 387.12
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 138-362 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 319 | 375 | 368.28
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 138-362 | 138-361 | 319 | 375 | 352.76
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 138-362 | 138-363 | 319 | 375 | 350.98
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 35 :GLNSO BUS | 319 | 375 | 329.01
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 138-365 | 319 | 375 | 329.01
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 36 :GLNNO BUS | 319 | 375 | 326.8
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 138-366 | 319 | 375 | 326.8
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 319 | 375 | 325.05
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 319 | 375 | 322.96
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 319 | 375 | 320.89
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 138-361 | 319 | 375 | 320.32
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 138-363 | 319 | 375 | 319.63
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | SHORE RD 345/138 Bank #1 | 319 | 375 | 318.35
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 319 | 375 | 318.25
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 138-362 | 319 | 375 | 317.4
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 138-364 | 319 | 375 | 316.95
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 37 :GLNGT BUS | 319 | 375 | 316.95
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 319 | 375 | 316.94
126455 JAMAICA 138 129235 V STRM P 138 1 Max | [5 empty] | 389.59
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | RAINEYW - FARRAGUTE 345 61 | Y50 | 285 | 368 | 313.42
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | NNC-B | Y50 | 285 | 368 | 313.25
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | NNC-C | Y50 | 285 | 368 | 313.23
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | NNC-1C | Y50 | 285 | 368 | 312.73
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | NNC-A | Y50 | 285 | 368 | 312.73
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | SIN:350 Hellgate#4-Astoria E | Y50 | 285 | 368 | 312.57
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | SIN:340-Hellgate#1-Astoria E | Y50 | 285 | 368 | 312.57
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 69-863 | Y50 | 285 | 368 | 312.34
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | DNWDIE - MOTTHAVEN 345 71 | Y50 | 285 | 368 | 312.23
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 69-858 | Y50 | 285 | 368 | 312.17
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | S:E13TH_M54 | Y50 | 285 | 368 | 312.07
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-677 | Y50 | 285 | 368 | 311.92
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | RAINEYE - FARRAGUT WEST 345 62 | Y50 | 285 | 368 | 311.81
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | S:E13TH_46 | Y50 | 285 | 368 | 311.72
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | PILGRIM 138/69 Bank #4 | Y50 | 285 | 368 | 311.7
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | S:E13TH_M55 | Y50 | 285 | 368 | 311.7
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | MOTTHAVEN - RAINEY Q12 345 | Y50 | 285 | 368 | 311.66
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | S:E13TH_45 | Y50 | 285 | 368 | 311.62
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-292 | Y50 | 285 | 368 | 311.6
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | DNWDIE - MOTTHAVEN 345 72 | Y50 | 285 | 368 | 311.59
126455 JAMAICA 138 129249 L SUCSPH 138 1 Max | [5 empty] | 313.42
126506 VERNON-E 138 126646 GRENWOOD S 138 1 | 10 | RAINEYW - FARRAGUTE 345 61 | Base Case | 217 | 310 | 112.61
126506 VERNON-E 138 126646 GRENWOOD S 138 1 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 217 | 310 | 111.85
126506 VERNON-E 138 126646 GRENWOOD S 138 1 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 217 | 310 | 111.83
126506 VERNON-E 138 126646 GRENWOOD S 138 1 | 10 | GEN: OSW W49 Street 5 | Base Case | 217 | 310 | 108.11
126506 VERNON-E 138 126646 GRENWOOD S 138 1 | 10 | S:E13TH_46 | Base Case | 217 | 310 | 103.62
126506 VERNON-E 138 126646 GRENWOOD S 138 1 | 10 | S:E13TH_45 | Base Case | 217 | 310 | 102.3
126506 VERNON-E 138 126646 GRENWOOD S 138 1 | 10 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 217 | 310 | 101.26
126506 VERNON-E 138 126646 GRENWOOD S 138 1 Max | [5 empty] | 112.61
126581 HG TAP 138 126730 15055 SR 138 1 | 10 | DNWDIE - MOTTHAVEN 345 72 | Base Case | 269 | 400 | 110.36
126581 HG TAP 138 126730 15055 SR 138 1 | 10 | DNWDIE - MOTTHAVEN 345 71 | Base Case | 269 | 400 | 109.57
126581 HG TAP 138 126730 15055 SR 138 1 | 10 | MOTTHAVEN - RAINEY Q12 345 | Base Case | 269 | 400 | 109.55
126581 HG TAP 138 126730 15055 SR 138 1 | 10 | MOTTHAVEN - RAINEY Q11 345 | Base Case | 269 | 400 | 109.17
126581 HG TAP 138 126730 15055 SR 138 1 | 10 | PV - EFISHKILL 345 F36 | Base Case | 269 | 400 | 102.75
126581 HG TAP 138 126730 15055 SR 138 1 | 10 | PV - EFISHKILL 345 F37 | Base Case | 269 | 400 | 102.75
126581 HG TAP 138 126730 15055 SR 138 1 Max | [5 empty] | 110.36
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_8 | 822 | 953 | 154.34
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_8 | 822 | 953 | 154.05
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M51 | DNWDIE - MOTTHAVEN 345 72 | 822 | 953 | 152.31
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_3 | 822 | 953 | 152.22
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_7 | 822 | 953 | 152.22
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M52 | DNWDIE - MOTTHAVEN 345 72 | 822 | 953 | 151.97
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_7 | 822 | 953 | 151.88
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_3 | 822 | 953 | 151.88
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | DNWDIE - MOTTHAVEN 345 72 | Y50 | 822 | 953 | 148.75
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | DNWDIE - MOTTHAVEN 345 72 | SB:DUNW345_4 | 822 | 953 | 148.6
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | DNWDIE - MOTTHAVEN 345 72 | SB:DUNW345_6 | 822 | 953 | 148.1
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RNS4 | 822 | 953 | 144.28
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RNS5 | 822 | 953 | 144
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:W49_5 | 822 | 953 | 141.98
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:W49_3 | 822 | 953 | 140.99
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RS4 | 822 | 953 | 140.96
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M51 | SPRNBRK - W49ST 345 M52 | 822 | 953 | 140.95
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:W49_2 | 822 | 953 | 140.46
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:W49_BTN | 822 | 953 | 140.46
126600 REAC71 345 126641 MOTT HAVEN 345 3 | 9/10 | SPRNBRK - W49ST 345 M52 | SPRNBRK - W49ST 345 M51 | 822 | 953 | 140.41
126600 REAC71 345 126641 MOTT HAVEN 345 3 Max | [5 empty] | 154.34
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:DUNW345_3 | 822 | 953 | 155.8
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:DUNW345_3 | 822 | 953 | 155.34
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_2 | 822 | 953 | 150.85
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_BTE | 822 | 953 | 150.82
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M51 | DNWDIE - MOTTHAVEN 345 71 | 822 | 953 | 150.71
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M52 | DNWDIE - MOTTHAVEN 345 71 | 822 | 953 | 150.39
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_2 | 822 | 953 | 150.34
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_BTE | 822 | 953 | 150.3
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | DNWDIE - MOTTHAVEN 345 71 | Y50 | 822 | 953 | 146.79
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | DNWDIE - MOTTHAVEN 345 71 | SB:DUNW345_4 | 822 | 953 | 146.69
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | DNWDIE - MOTTHAVEN 345 71 | SB:DUNW345_6 | 822 | 953 | 146.59
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RNS4 | 822 | 953 | 140.75
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:SPRA345_RNS5 | 822 | 953 | 140.48
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:W49_5 | 822 | 953 | 138.51
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:W49_3 | 822 | 953 | 137.54
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M51 | SB:SPRA345_RS4 | 822 | 953 | 137.51
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M51 | SPRNBRK - W49ST 345 M52 | 822 | 953 | 137.5
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:W49_BTN | 822 | 953 | 137.02
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M52 | SB:W49_2 | 822 | 953 | 137.02
126601 REAC72 345 126641 MOTT HAVEN 345 4 | 9/10 | SPRNBRK - W49ST 345 M52 | SPRNBRK - W49ST 345 M51 | 822 | 953 | 136.97
126601 REAC72 345 126641 MOTT HAVEN 345 4 Max | [5 empty] | 155.8
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | Y50 | 822 | 953 | 168.46
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:DUNW345_4 | 822 | 953 | 166.26
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:DUNW345_6 | 822 | 953 | 165.34
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | T:W89&W90_UC20 | 822 | 953 | 161.01
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M51 | SB:RAIN345_2E | 822 | 953 | 154.78
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M51 | MOTTHAVEN - RAINEY Q11 345 | 822 | 953 | 154.76
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_BTW | 822 | 953 | 154.37
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_1 | 822 | 953 | 154.37
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_BTW | 822 | 953 | 154.36
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_1 | 822 | 953 | 154.36
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M52 | SB:RAIN345_2E | 822 | 953 | 154.32
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | SPRNBRK - W49ST 345 M52 | MOTTHAVEN - RAINEY Q11 345 | 822 | 953 | 154.17
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | Y49 | SB:MOTT345_1 | 822 | 953 | 146.48
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | Y49 | SB:MOTT345_BTW | 822 | 953 | 146.48
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | Y49 | SB:RAIN345_2E | 822 | 953 | 146.41
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | Y49 | MOTTHAVEN - RAINEY Q11 345 | 822 | 953 | 146.4
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:SPRA345_RNS5 | 822 | 953 | 145.46
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:SPRA345_RNS4 | 822 | 953 | 145.37
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:W49_BTN | 822 | 953 | 144.36
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 | 10 | MOTTHAVEN - RAINEY Q11 345 | SB:W49_2 | 822 | 953 | 144.36
126641 MOTT HAVEN 345 126642 RAINEY WEST 345 4 Max | [5 empty] | 168.46
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | Y50 | 822 | 953 | 171.79
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SB:DUNW345_4 | 822 | 953 | 169.53
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SB:DUNW345_6 | 822 | 953 | 168.57
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | T:W89&W90_UC20 | 822 | 953 | 164.4
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M51 | SB:RAINEY_6W | 822 | 953 | 157.83
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M52 | SB:RAINEY_6W | 822 | 953 | 157.8
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M51 | SB:RAINEY_7W | 822 | 953 | 157.47
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_9 | 822 | 953 | 157.36
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M51 | SB:MOTT345_4 | 822 | 953 | 157.33
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_9 | 822 | 953 | 157.28
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M52 | SB:MOTT345_4 | 822 | 953 | 157.25
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M51 | MOTTHAVEN - RAINEY Q12 345 | 822 | 953 | 157.13
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M52 | MOTTHAVEN - RAINEY Q12 345 | 822 | 953 | 157.06
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | SPRNBRK - W49ST 345 M52 | SB:RAINEY_7W | 822 | 953 | 156.91
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | Y49 | SB:MOTT345_9 | 822 | 953 | 149.58
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | Y49 | SB:MOTT345_4 | 822 | 953 | 149.55
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | Y49 | MOTTHAVEN - RAINEY Q12 345 | 822 | 953 | 149.5
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | Y49 | SB:RAINEY_7W | 822 | 953 | 149.45
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SB:SPRA345_RNS5 | 822 | 953 | 147.42
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 | 10 | MOTTHAVEN - RAINEY Q12 345 | SB:SPRA345_RNS4 | 822 | 953 | 147.32
126641 MOTT HAVEN 345 126643 RAINEY EAST 345 3 Max | [5 empty] | 171.79
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | SPRNBRK - W49ST 345 M51 | SB:RAIN345_1E | 775 | 932 | 141.64
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | SPRNBRK - W49ST 345 M52 | SB:RAIN345_1E | 775 | 932 | 141.44
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | DUNWOODIE-PLEASANTVILLE W89/W73 | SB:RAIN345_1E | 775 | 932 | 124.1
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | RAINEY-CORONA PAR 2 | SB:RAIN345_1E | 775 | 932 | 122.02
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | S:E13TH_45 | SB:RAIN345_1E | 775 | 932 | 120.05
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | S:E13TH_46 | SB:RAIN345_1E | 775 | 932 | 119.98
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | EFISHKILL - PLSNTVLLE F39/Y87 345 | SB:RAIN345_1E | 775 | 932 | 118.75
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | S:E13TH_M55 | SB:RAIN345_1E | 775 | 932 | 118.72
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | SB:RAIN345_1E | 775 | 932 | 118.63
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | SPRNBRK - TREMONT X28 345 | SB:RAIN345_1E | 775 | 932 | 118.6
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | SPRNBRK - ACDMY 345 M29 | SB:RAIN345_1E | 775 | 932 | 117.72
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | DUNWOODIE-PLEASANTVILLE W90/W74 | SB:RAIN345_1E | 775 | 932 | 117.38
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | S:E13TH_M54 | SB:RAIN345_1E | 775 | 932 | 117.08
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | NNC-3C | SB:RAIN345_1E | 775 | 932 | 116.95
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | Northport-Norwalk NNC-3C | SB:RAIN345_1E | 775 | 932 | 116.95
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | GOWANUS 345/138 2TR | SB:RAIN345_1E | 775 | 932 | 116.67
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | GEN: OSW Holbrook 2 | SB:RAIN345_1E | 775 | 932 | 116.62
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | GEN: OSW Barret 2 | SB:RAIN345_1E | 775 | 932 | 116.62
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | MILLWOOD - SPRNBRK W85/W78 345 | SB:RAIN345_1E | 775 | 932 | 114.75
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 | 10 | MILLWOOD - SPRNBRK W82/W65 345 | SB:RAIN345_1E | 775 | 932 | 114.73
126642 RAINEY WEST 345 126645 FARRAGUT EAS 345 1 Max | [5 empty] | 141.64
126643 RAINEY EAST 345 126644 FARRAGUT WES 345 2 | 10 | RAINEYE - FARRAGUTTIE 345 63 | SB:RAIN345_3W | 821 | 948 | 101.02
126643 RAINEY EAST 345 126644 FARRAGUT WES 345 2 Max | [5 empty] | 101.02
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | SIN:340-Hellgate#1-Astoria E | Y50 | 143 | 177 | 190.64
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | SIN:350 Hellgate#4-Astoria E | Y50 | 143 | 177 | 190.56
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | 138-367 | Y50 | 143 | 177 | 189.34
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | 138-368 | Y50 | 143 | 177 | 189.34
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | LKE SCSS 138/69 Bank #5 | Y50 | 143 | 177 | 188.56
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | SIN:340-Hellgate#1-Astoria E | SB:DUNW345_4 | 143 | 177 | 188.41
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | S:E13TH_M54 | Y50 | 143 | 177 | 188.28
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | S:E13TH_45 | Y50 | 143 | 177 | 188.23
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | SIN:350 Hellgate#4-Astoria E | SB:DUNW345_4 | 143 | 177 | 188.19
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | S:E13TH_46 | Y50 | 143 | 177 | 188.11
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | S:E13TH_M55 | Y50 | 143 | 177 | 188.06
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | FARRAGUTW 345/138 4TR | Y50 | 143 | 177 | 187.59
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | LKE SCSS 138/69 Bank #5 | SB:DUNW345_6 | 143 | 177 | 187.53
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | MILLWOOD 345/138 TA2 | Y50 | 143 | 177 | 187.52
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | FARRAGUTE 345/138 5TR | Y50 | 143 | 177 | 187.51
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | RAMAPO - SMAHWAH 69/J3410 345 | Y50 | 143 | 177 | 187.51
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | RAMAPO - SMAHWAH 70/K3411 345 | Y50 | 143 | 177 | 187.51
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | FARRAGUTE 345/138 3TR | Y50 | 143 | 177 | 187.48
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | 69-858 | Y50 | 143 | 177 | 187.48
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 | 10 | PILGRIM 138/69 Bank #4 | Y50 | 143 | 177 | 187.45
126644 FARRAGUT WES 345 126436 FGT_X10 138 1 Max | [5 empty] | 190.64
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | NNC-B | Y50 | 143 | 178 | 190.13
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | NNC-C | Y50 | 143 | 178 | 190.12
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | SIN:340-Hellgate#1-Astoria E | Y50 | 143 | 178 | 189.71
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | SIN:350 Hellgate#4-Astoria E | Y50 | 143 | 178 | 189.63
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | NNC-1C | Y50 | 143 | 178 | 188.68
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | NNC-A | Y50 | 143 | 178 | 188.68
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | 138-677 | Y50 | 143 | 178 | 188.55
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | 69-863 | Y50 | 143 | 178 | 188.52
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | 138-367 | Y50 | 143 | 178 | 188.41
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | 138-368 | Y50 | 143 | 178 | 188.41
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | 138-881 NEW | Y50 | 143 | 178 | 187.75
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | LKE SCSS 138/69 Bank #5 | Y50 | 143 | 178 | 187.64
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | SIN:340-Hellgate#1-Astoria E | SB:DUNW345_4 | 143 | 178 | 187.49
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | 138-881 | Y50 | 143 | 178 | 187.47
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | NNC-B | SB:DUNW345_6 | 143 | 178 | 187.42
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | NNC-C | SB:DUNW345_6 | 143 | 178 | 187.41
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | S:E13TH_M54 | Y50 | 143 | 178 | 187.37
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | S:E13TH_45 | Y50 | 143 | 178 | 187.31
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | SIN:350 Hellgate#4-Astoria E | SB:DUNW345_4 | 143 | 178 | 187.27
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | S:E13TH_46 | Y50 | 143 | 178 | 187.19
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 Max | [5 empty] | 190.13
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | SPRNBRK - W49ST 345 M51 | Base Case | 204 | 336 | 133.15
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | SPRNBRK - W49ST 345 M52 | Base Case | 204 | 336 | 132.34
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | SPRNBRK - W49ST 345 M51 | SPRNBRK - TREMONT X28 345 | 204 | 336 | 114.61
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | SPRNBRK - W49ST 345 M52 | SPRNBRK - TREMONT X28 345 | 204 | 336 | 114.32
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | SPRNBRK - TREMONT X28 345 | Base Case | 204 | 336 | 109.25
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | RAINEY-CORONA PAR 2 | Base Case | 204 | 336 | 103.5
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | DUNWOODIE-PLEASANTVILLE W89/W73 | Base Case | 204 | 336 | 103.2
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | BUCH - SPRNBRK W93/W79 345 | Base Case | 204 | 336 | 103.1
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | 138-362 | Base Case | 204 | 336 | 103.1
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | MILLWOOD - SPRNBRK W99/W64 345 | Base Case | 204 | 336 | 103.09
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | NNC-3C | Base Case | 204 | 336 | 103.08
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | Northport-Norwalk NNC-3C | Base Case | 204 | 336 | 103.08
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | RAMAPO - BUCHN 345 Y94 | Base Case | 204 | 336 | 102.99
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | PV - MILLWOOD 345 F30/W80 | Base Case | 204 | 336 | 102.98
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | PV - MILLWOOD F31/W81 345 | Base Case | 204 | 336 | 102.98
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | MILLWOOD - SPRNBRK W82/W65 345 | Base Case | 204 | 336 | 102.97
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | MILLWOOD - SPRNBRK W85/W78 345 | Base Case | 204 | 336 | 102.97
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | ASTORIA 345/138 PS | Base Case | 204 | 336 | 102.88
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | DUNWOODIE-PLEASANTVILLE W90/W74 | Base Case | 204 | 336 | 102.78
126647 E179 ST E 138 126648 S CREEK E 138 2 | 10 | GOWANUS 345/138 2TR | Base Case | 204 | 336 | 102.72
126647 E179 ST E 138 126648 S CREEK E 138 2 Max | [5 empty] | 133.15
126647 E179 ST E 138 126730 15055 SR 138 SR | 10 | DNWDIE - MOTTHAVEN 345 72 | Base Case | 268 | 400 | 110.77
126647 E179 ST E 138 126730 15055 SR 138 SR | 10 | DNWDIE - MOTTHAVEN 345 71 | Base Case | 268 | 400 | 109.98
126647 E179 ST E 138 126730 15055 SR 138 SR | 10 | MOTTHAVEN - RAINEY Q12 345 | Base Case | 268 | 400 | 109.96
126647 E179 ST E 138 126730 15055 SR 138 SR | 10 | MOTTHAVEN - RAINEY Q11 345 | Base Case | 268 | 400 | 109.58
126647 E179 ST E 138 126730 15055 SR 138 SR | 10 | PV - EFISHKILL 345 F36 | Base Case | 268 | 400 | 103.14
126647 E179 ST E 138 126730 15055 SR 138 SR | 10 | PV - EFISHKILL 345 F37 | Base Case | 268 | 400 | 103.14
126647 E179 ST E 138 126730 15055 SR 138 SR Max | [5 empty] | 110.77
128248 ANNTRHIGH 345 147829 ASTOR345 345 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | SIN:350 Hellgate#4-Astoria E | 319 | 353 | 101.44
128248 ANNTRHIGH 345 147829 ASTOR345 345 1 | 10 | EFISHKILL - PLSNTVLLE F38/Y86 345 | SIN:340-Hellgate#1-Astoria E | 319 | 353 | 101.44
128248 ANNTRHIGH 345 147829 ASTOR345 345 1 Max | [5 empty] | 101.44
128248 ANNTRHIGH 345 999942 TR1 138 1 | 10 | GEN: OSW Astoria 2 | Base Case | 320 | 390 | 101.81
128248 ANNTRHIGH 345 999942 TR1 138 1 Max | [5 empty] | 101.81
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | Base Case | 450 | 855 | 175.64
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN: OSW EGC 5 | Base Case | 450 | 855 | 146.5
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 1105 EGC_345_OSW5 345 128825 EGC PAR 345 1 | 450 | 855 | 119.2
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | GEN: OSW EGC 5 | 450 | 855 | 119.16
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN: OSW EGC 5 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 450 | 855 | 119.01
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN: OSW EGC 5 | E.G.C. 345 kV P.A.R. #2 | 450 | 855 | 119.01
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN: OSW EGC 5 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 450 | 855 | 119.01
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | SHORE RD 345/138 Bank #2 | Base Case | 450 | 855 | 103.1
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | SHORE RD 345/138 Bank #1 | Base Case | 450 | 855 | 102.92
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN: OSW Astoria 2 | Base Case | 450 | 855 | 102.34
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | 138-365 | Base Case | 450 | 855 | 102.34
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | 138-366 | Base Case | 450 | 855 | 102.18
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | 138-362 | Base Case | 450 | 855 | 102.09
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | GEN: OSW Gowanus 1 | Base Case | 450 | 855 | 102.09
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | 138-361 | Base Case | 450 | 855 | 101.69
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | VLY STRM 138 kV P.A.R. | Base Case | 450 | 855 | 101.67
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | 901 L&M | Base Case | 450 | 855 | 101.67
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Base Case | 450 | 855 | 101.67
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | 138-363 | Base Case | 450 | 855 | 101.67
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | VLY STRM 138/69 kV Bank #5 | Base Case | 450 | 855 | 101.48
128822 E.G.C.-1 345 128825 EGC PAR 345 1 Max | [5 empty] | 175.64
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | Base Case | 450 | 855 | 175.53
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | EGC REA | Base Case | 450 | 855 | 175.53
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | GEN: OSW EGC 5 | Base Case | 450 | 855 | 149.79
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | GEN: OSW EGC 5 | E.G.C. 345 kV P.A.R. #1 | 450 | 855 | 119.1
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | GEN: OSW EGC 5 | 33 :EGC BUS2 | 450 | 855 | 119.1
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | GEN: OSW EGC 5 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 450 | 855 | 119.1
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | GEN: OSW EGC 5 | EGC REA | 450 | 855 | 119.1
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | GEN: OSW EGC 5 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 450 | 855 | 119.1
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | EGC REA | 1105 EGC_345_OSW5 345 128825 EGC PAR 345 1 | 450 | 855 | 119.03
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | 1105 EGC_345_OSW5 345 128825 EGC PAR 345 1 | 450 | 855 | 119.03
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | EGC REA | GEN: OSW EGC 5 | 450 | 855 | 118.99
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | GEN: OSW EGC 5 | 450 | 855 | 118.99
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | SHORE RD 345/138 Bank #1 | Base Case | 450 | 855 | 103.11
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | SHORE RD 345/138 Bank #2 | Base Case | 450 | 855 | 103
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | 138-364 | Base Case | 450 | 855 | 102.4
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | 138-362 | Base Case | 450 | 855 | 102.26
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | GEN: OSW Astoria 2 | Base Case | 450 | 855 | 102.19
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | 138-365 | Base Case | 450 | 855 | 102.1
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | GEN: OSW Gowanus 1 | Base Case | 450 | 855 | 101.95
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | 138-366 | Base Case | 450 | 855 | 101.95
128823 E.G.C.-2 345 128825 EGC PAR 345 1 Max | [5 empty] | 175.53
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 770 | 990 | 307.07
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 770 | 990 | 304.71
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | SIN:350 Hellgate#4-Astoria E | Y50 | 770 | 990 | 303.33
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | SIN:340-Hellgate#1-Astoria E | Y50 | 770 | 990 | 303.28
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 138-368 | Y50 | 770 | 990 | 303.22
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 138-367 | Y50 | 770 | 990 | 303.15
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | LKE SCSS 138/69 Bank #5 | Y50 | 770 | 990 | 303.03
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | NNC-B | Y50 | 770 | 990 | 301.16
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | NNC-C | Y50 | 770 | 990 | 301.14
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | S:E13TH_M54 | Y50 | 770 | 990 | 300.78
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | NNC-A | Y50 | 770 | 990 | 300.69
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | NNC-1C | Y50 | 770 | 990 | 300.69
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 69-858 | Y50 | 770 | 990 | 300.65
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 69-863 | Y50 | 770 | 990 | 300.64
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | S:E13TH_M55 | Y50 | 770 | 990 | 300.51
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | S:E13TH_46 | Y50 | 770 | 990 | 300.51
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | S:E13TH_45 | Y50 | 770 | 990 | 300.44
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | DNWDIE - MOTTHAVEN 345 71 | Y50 | 770 | 990 | 300.44
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | PILGRIM 138/69 Bank #4 | Y50 | 770 | 990 | 300.39
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | MOTTHAVEN - RAINEY Q12 345 | Y50 | 770 | 990 | 300.33
128824 EGC DUM 345 128825 EGC PAR 345 1 Max | [5 empty] | 307.07
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | SHORE RD 345/138 Bank #2 | 17 :SRD1370 | 770 | 990 | 312.17
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 770 | 990 | 311.73
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | SHORE RD 345/138 Bank #1 | 18 :SRD1380 | 770 | 990 | 309.73
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 770 | 990 | 309.33
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | SIN:350 Hellgate#4-Astoria E | Y50 | 770 | 990 | 308.03
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | SIN:340-Hellgate#1-Astoria E | Y50 | 770 | 990 | 307.99
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 138-368 | Y50 | 770 | 990 | 307.81
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 138-367 | Y50 | 770 | 990 | 307.74
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | LKE SCSS 138/69 Bank #5 | Y50 | 770 | 990 | 307.62
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | SIN:340-Hellgate#1-Astoria E | SB:DUNW345_4 | 770 | 990 | 307.36
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | LKE SCSS 138/69 Bank #5 | SB:DUNW345_6 | 770 | 990 | 307.35
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | SIN:350 Hellgate#4-Astoria E | SB:DUNW345_4 | 770 | 990 | 307.3
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 138-367 | SB:DUNW345_6 | 770 | 990 | 306.52
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 138-368 | SB:DUNW345_6 | 770 | 990 | 306.5
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 138-368 | SB:DUNW345_4 | 770 | 990 | 306.44
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | DNWDIE - MOTTHAVEN 345 71 | SB:DUNW345_6 | 770 | 990 | 306.38
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 138-367 | SB:DUNW345_4 | 770 | 990 | 306.36
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | LKE SCSS 138/69 Bank #5 | SB:DUNW345_4 | 770 | 990 | 306.33
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | NNC-B | Y50 | 770 | 990 | 305.71
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | NNC-C | Y50 | 770 | 990 | 305.7
128824 EGC DUM 345 128830 HMP HRBR 345 1 Max | [5 empty] | 312.17
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | SHORE RD 345/138 Bank #2 | 17 :SRD1370 | 770 | 990 | 317.52
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 770 | 990 | 317.07
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | SHORE RD 345/138 Bank #1 | 18 :SRD1380 | 770 | 990 | 315.06
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 770 | 990 | 314.65
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | SIN:350 Hellgate#4-Astoria E | Y50 | 770 | 990 | 313.47
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | SIN:340-Hellgate#1-Astoria E | Y50 | 770 | 990 | 313.42
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 138-368 | Y50 | 770 | 990 | 313.12
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 138-367 | Y50 | 770 | 990 | 313.05
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | LKE SCSS 138/69 Bank #5 | Y50 | 770 | 990 | 312.93
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | SIN:340-Hellgate#1-Astoria E | SB:DUNW345_4 | 770 | 990 | 312.91
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | SIN:350 Hellgate#4-Astoria E | SB:DUNW345_4 | 770 | 990 | 312.84
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | LKE SCSS 138/69 Bank #5 | SB:DUNW345_6 | 770 | 990 | 312.78
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | DNWDIE - MOTTHAVEN 345 71 | SB:DUNW345_6 | 770 | 990 | 311.97
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 138-367 | SB:DUNW345_6 | 770 | 990 | 311.91
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 138-368 | SB:DUNW345_6 | 770 | 990 | 311.89
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 138-368 | SB:DUNW345_4 | 770 | 990 | 311.85
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 138-367 | SB:DUNW345_4 | 770 | 990 | 311.77
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | LKE SCSS 138/69 Bank #5 | SB:DUNW345_4 | 770 | 990 | 311.75
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 138-362 | Base Case | 770 | 990 | 311.65
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | Northport-Norwalk NNC-3C | Base Case | 770 | 990 | 311.48
128830 HMP HRBR 345 147857 DVNPT NK 345 1 Max | [5 empty] | 317.52
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | Y49 | SHORE RD 345/138 Bank #2 | 450 | 563 | 434.72
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | Y49 | 21 :SRD BUS2 | 450 | 563 | 405.15
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | Y49 | 450 | 563 | 383.35
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | Base Case | 450 | 563 | 379.7
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | Northport-Norwalk NNC-3C | SHORE RD 345/138 Bank #2 | 450 | 563 | 370.61
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | NNC-3C | SHORE RD 345/138 Bank #2 | 450 | 563 | 370.61
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | E.G.C. 345 kV P.A.R. #1 | SHORE RD 345/138 Bank #2 | 450 | 563 | 362.54
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | EGC REA | SHORE RD 345/138 Bank #2 | 450 | 563 | 362.54
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | E.G.C. 345 kV P.A.R. #2 | SHORE RD 345/138 Bank #2 | 450 | 563 | 362.38
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SPRNBRK - DUNWDIE 345 W75 | SHORE RD 345/138 Bank #2 | 450 | 563 | 349.93
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SPRNBRK - TREMONT X28 345 | SHORE RD 345/138 Bank #2 | 450 | 563 | 347.15
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | 901 L&M | SHORE RD 345/138 Bank #2 | 450 | 563 | 346.79
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | SHORE RD 345/138 Bank #2 | 450 | 563 | 346.79
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | SHORE RD 345/138 Bank #2 | 450 | 563 | 346.31
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | VLY STRM 138 kV P.A.R. | SHORE RD 345/138 Bank #2 | 450 | 563 | 346.26
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | GOWANUS 345/138 2TR | SHORE RD 345/138 Bank #2 | 450 | 563 | 346.06
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | ASTORIA 345/138 PS | SHORE RD 345/138 Bank #2 | 450 | 563 | 345.97
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | GEN: OSW Astoria 2 | SHORE RD 345/138 Bank #2 | 450 | 563 | 345.65
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | GEN: OSW Gowanus 1 | SHORE RD 345/138 Bank #2 | 450 | 563 | 345.38
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | Y49 | Base Case | 450 | 563 | 344.08
128835 SHORE RD 345 129293 SHORE RD 138 1 Max | [5 empty] | 434.72
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | Y49 | SHORE RD 345/138 Bank #1 | 540 | 562 | 430.95
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | Y49 | 20 :SRD BUS1 | 540 | 562 | 403.45
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | Y49 | 540 | 562 | 384.24
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | E.G.C. 345 kV P.A.R. #1 | SHORE RD 345/138 Bank #1 | 540 | 562 | 358.85
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | EGC REA | SHORE RD 345/138 Bank #1 | 540 | 562 | 358.85
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | E.G.C. 345 kV P.A.R. #2 | SHORE RD 345/138 Bank #1 | 540 | 562 | 358.69
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SPRNBRK - DUNWDIE 345 W75 | SHORE RD 345/138 Bank #1 | 540 | 562 | 346.34
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | JAMCA - VLLYSTRM 901L&M 138 | SHORE RD 345/138 Bank #1 | 540 | 562 | 344.24
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | 901 L&M | SHORE RD 345/138 Bank #1 | 540 | 562 | 344.24
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | SHORE RD 345/138 Bank #1 | 540 | 562 | 343.81
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | VLY STRM 138 kV P.A.R. | SHORE RD 345/138 Bank #1 | 540 | 562 | 343.69
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SPRNBRK - TREMONT X28 345 | SHORE RD 345/138 Bank #1 | 540 | 562 | 343.69
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | GOWANUS 345/138 2TR | SHORE RD 345/138 Bank #1 | 540 | 562 | 342.58
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | ASTORIA 345/138 PS | SHORE RD 345/138 Bank #1 | 540 | 562 | 342.5
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | GEN: OSW Astoria 2 | SHORE RD 345/138 Bank #1 | 540 | 562 | 342.28
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | GEN: OSW Gowanus 1 | SHORE RD 345/138 Bank #1 | 540 | 562 | 341.97
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | 901 L&M | 540 | 562 | 340.88
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | JAMCA - VLLYSTRM 901L&M 138 | 540 | 562 | 340.88
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | VLY STRM 138 kV P.A.R. | 540 | 562 | 340.33
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | VLY STRM 138/69 kV Bank #5 | 540 | 562 | 340.25
128835 SHORE RD 345 129294 SHORE RD2 138 2 Max | [5 empty] | 430.95
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-292 | Base Case | 218 | 308 | 494.41
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GEN: OSW Ruland 3 | Barrett Bus Tie | 218 | 308 | 437.65
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Barrett G1-8* | Barrett Bus Tie | 218 | 308 | 435.67
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GEN: OSW Northport 4 | Barrett Bus Tie | 218 | 308 | 434.24
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Barrett G1-8* | 12 :BRT BUS2 | 218 | 308 | 433.52
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GEN: OSW Ruland 3 | 12 :BRT BUS2 | 218 | 308 | 432.78
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GEN: OSW Holbrook 1 | Barrett Bus Tie | 218 | 308 | 431.68
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GEN: OSW Northport 4 | 12 :BRT BUS2 | 218 | 308 | 429.07
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-574 | Barrett Bus Tie | 218 | 308 | 426.74
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-576 | Barrett Bus Tie | 218 | 308 | 426.44
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GEN: OSW Holbrook 1 | 12 :BRT BUS2 | 218 | 308 | 426.32
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-559 | Barrett Bus Tie | 218 | 308 | 424.56
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-359 | Barrett Bus Tie | 218 | 308 | 424.25
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-558 | Barrett Bus Tie | 218 | 308 | 423.9
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | BELMR 69/34.5 kV BK#5 | Barrett Bus Tie | 218 | 308 | 423.78
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-574 | 12 :BRT BUS2 | 218 | 308 | 423.24
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-576 | 12 :BRT BUS2 | 218 | 308 | 422.91
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-459 | Barrett Bus Tie | 218 | 308 | 422.71
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-564 | Barrett Bus Tie | 218 | 308 | 422.27
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-562 | Barrett Bus Tie | 218 | 308 | 421.88
129202 BARRETT1 138 129233 VLY STRM 138 1 Max | [5 empty] | 494.41
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-291 | 138-292 | 195 | 275 | 381.32
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | 138-291 | 195 | 275 | 379.88
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | 8 :VST BUS1 | 195 | 275 | 379.18
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 379.18
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 195 | 275 | 376.41
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | Valley Stream Bus Tie | 195 | 275 | 167.94
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-261 | 138-262 | 195 | 275 | 145.33
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-262 | 138-261 | 195 | 275 | 144.37
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW W49 Street 5 | Base Case | 195 | 275 | 126.82
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW W49 Street 5 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 122.13
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW W49 Street 5 | 8 :VST BUS1 | 195 | 275 | 122.07
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | PV - EFISHKILL 345 F37 | Base Case | 195 | 275 | 120.48
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | PV - EFISHKILL 345 F36 | Base Case | 195 | 275 | 120.48
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-262 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 118.37
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-262 | 8 :VST BUS1 | 195 | 275 | 118.25
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | PV - EFISHKILL 345 F37 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 117.63
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | PV - EFISHKILL 345 F36 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 117.63
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | PV - EFISHKILL 345 F36 | 8 :VST BUS1 | 195 | 275 | 117.57
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | PV - EFISHKILL 345 F37 | 8 :VST BUS1 | 195 | 275 | 117.57
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW W49 Street 5 | 1103 RUL_138_OSW3 138 129361 RULND RD 138 1 | 195 | 275 | 117.41
129203 BARRETT2 138 129204 BRRT PH 138 1 Max | [5 empty] | 381.32
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | Base Case | 213 | 305 | 507.26
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | Base Case | 213 | 305 | 491.24
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | 138-291 | 213 | 305 | 413.41
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | 138-291 | 213 | 305 | 413.27
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | BARRETT 138 kV P.A.R. | 213 | 305 | 412.93
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 138-459 | 213 | 305 | 412.63
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 129204 BRRT PH 138 129276 FREEPORT 138 1 | 213 | 305 | 412.63
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | 8 :VST BUS1 | 213 | 305 | 401.75
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | VLY STRM 138/69 kV Bank #5 | 213 | 305 | 401.72
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | 8 :VST BUS1 | 213 | 305 | 401.62
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | VLY STRM 138/69 kV Bank #5 | 213 | 305 | 401.59
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | BARRETT 138 kV P.A.R. | 213 | 305 | 401.45
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 138-459 | 213 | 305 | 401.34
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 129204 BRRT PH 138 129276 FREEPORT 138 1 | 213 | 305 | 401.34
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-461 | 138-291 | 213 | 305 | 398.52
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 138-461 | 213 | 305 | 397.69
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | Y50 | 213 | 305 | 388.7
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | Y49 | 138-291 | 213 | 305 | 387.15
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-461 | 8 :VST BUS1 | 213 | 305 | 387.1
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-461 | VLY STRM 138/69 kV Bank #5 | 213 | 305 | 387.08
129203 BARRETT2 138 129234 VLY STRM2 138 2 Max | [5 empty] | 507.26
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-291 | 138-292 | 195 | 275 | 373.97
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | 138-291 | 195 | 275 | 372.56
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | 8 :VST BUS1 | 195 | 275 | 371.89
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 371.89
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 195 | 275 | 369.17
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | Valley Stream Bus Tie | 195 | 275 | 163.05
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-261 | 138-262 | 195 | 275 | 141.24
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-262 | 138-261 | 195 | 275 | 140.33
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW W49 Street 5 | Base Case | 195 | 275 | 123.51
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW W49 Street 5 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 119.61
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW W49 Street 5 | 8 :VST BUS1 | 195 | 275 | 119.55
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | PV - EFISHKILL 345 F37 | Base Case | 195 | 275 | 117.37
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | PV - EFISHKILL 345 F36 | Base Case | 195 | 275 | 117.37
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-262 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 116.03
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-262 | 8 :VST BUS1 | 195 | 275 | 115.91
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | PV - EFISHKILL 345 F37 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 115.21
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | PV - EFISHKILL 345 F36 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 115.21
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | PV - EFISHKILL 345 F37 | 8 :VST BUS1 | 195 | 275 | 115.15
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | PV - EFISHKILL 345 F36 | 8 :VST BUS1 | 195 | 275 | 115.15
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | SPRNBRK - DUNWDIE 345 W75 | VLY STRM 138/69 kV Bank #5 | 195 | 275 | 113.19
129204 BRRT PH 138 129276 FREEPORT 138 1 Max | [5 empty] | 373.97
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 20 :SRD BUS1 | 320 | 375 | 371
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 21 :SRD BUS2 | 320 | 375 | 368.95
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 138-362 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 320 | 375 | 355.82
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 138-362 | 138-361 | 320 | 375 | 344.18
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 138-362 | 138-363 | 320 | 375 | 342.84
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 138-365 | 320 | 375 | 324.76
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 35 :GLNSO BUS | 320 | 375 | 324.76
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 36 :GLNNO BUS | 320 | 375 | 322.93
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 138-366 | 320 | 375 | 322.93
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 320 | 375 | 321.37
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 320 | 375 | 319.6
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 320 | 375 | 318.88
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 138-361 | 320 | 375 | 317.46
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 138-363 | 320 | 375 | 316.89
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 320 | 375 | 316.36
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 138-362 | 320 | 375 | 314.99
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 37 :GLNGT BUS | 320 | 375 | 314.64
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 138-364 | 320 | 375 | 314.64
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 320 | 375 | 314.63
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | SHORE RD 345/138 Bank #1 | 320 | 375 | 312.84
129233 VLY STRM 138 129235 V STRM P 138 1 Max | [5 empty] | 371
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | GEN: OSW Ruland 3 | Base Case | 194 | 284 | 280.91
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-261 | 194 | 284 | 278.32
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | GEN: OSW Ruland 3 | 138-261 | 194 | 284 | 276.69
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Base Case | 194 | 284 | 270.5
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | VLY STRM 138/69 kV Bank #5 | 194 | 284 | 267.58
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 8 :VST BUS1 | 194 | 284 | 267.15
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | JAMCA - VLLYSTRM 901L&M 138 | 194 | 284 | 265.71
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 901 L&M | 194 | 284 | 265.71
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | VLY STRM 138 kV P.A.R. | 194 | 284 | 265.69
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | GEN: OSW Northport 4 | Base Case | 194 | 284 | 262.39
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138 kV P.A.R. | 138-261 | 194 | 284 | 260.6
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 901 L&M | 138-261 | 194 | 284 | 260.52
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | 138-261 | 194 | 284 | 260.52
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | GEN: OSW Northport 4 | 138-261 | 194 | 284 | 258.61
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138 kV P.A.R. | Base Case | 194 | 284 | 255.78
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 901 L&M | Base Case | 194 | 284 | 255.71
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Base Case | 194 | 284 | 255.71
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | GEN: OSW Holbrook 1 | Base Case | 194 | 284 | 253.64
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | Base Case | 194 | 284 | 252.4
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 1103 RUL_138_OSW3 138 129361 RULND RD 138 1 | 194 | 284 | 250.27
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 Max | [5 empty] | 280.91
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 138-262 | 280 | 442 | 160.13
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | VLY STRM 138/69 kV Bank #5 | 280 | 442 | 154.68
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 8 :VST BUS1 | 280 | 442 | 154.43
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 901 L&M | 280 | 442 | 152.16
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | JAMCA - VLLYSTRM 901L&M 138 | 280 | 442 | 152.16
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | VLY STRM 138 kV P.A.R. | 280 | 442 | 152.11
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | Base Case | 280 | 442 | 152.08
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | GEN: OSW Ruland 3 | 138-262 | 280 | 442 | 151.37
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | VLY STRM 138 kV P.A.R. | 138-262 | 280 | 442 | 148.47
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | JAMCA - VLLYSTRM 901L&M 138 | 138-262 | 280 | 442 | 148.44
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 901 L&M | 138-262 | 280 | 442 | 148.44
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | GEN: OSW Northport 4 | 138-262 | 280 | 442 | 141.35
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 1103 RUL_138_OSW3 138 129361 RULND RD 138 1 | 280 | 442 | 137.03
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | GEN: OSW Ruland 3 | 280 | 442 | 136.98
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | GEN: OSW Holbrook 1 | 138-262 | 280 | 442 | 136.68
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | BARRETT 138 kV P.A.R. | 138-262 | 280 | 442 | 131.82
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 74 :NPT BUS2 | 280 | 442 | 131.25
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 1104 NRT_138_OSW4 138 129341 NRTHPRT1 138 1 | 280 | 442 | 131.2
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | GEN: OSW Northport 4 | 280 | 442 | 131.15
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-459 | 138-262 | 280 | 442 | 131.06
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 Max | [5 empty] | 160.13
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-366 | 21 :SRD BUS2 | 260 | 380 | 240.87
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-368 | Y50 | 260 | 380 | 225.45
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-366 | Shore Road Bus Tie | 260 | 380 | 181.77
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-362 | Shore Road Bus Tie | 260 | 380 | 166.29
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-364 | 21 :SRD BUS2 | 260 | 380 | 162.94
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-365 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 260 | 380 | 156.36
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-366 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 260 | 380 | 156.35
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-366 | 35 :GLNSO BUS | 260 | 380 | 154.49
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-366 | 138-365 | 260 | 380 | 154.49
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-365 | 36 :GLNNO BUS | 260 | 380 | 154.48
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-365 | 138-366 | 260 | 380 | 154.48
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 260 | 380 | 151.23
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | Shore Road Bus Tie | 260 | 380 | 144.71
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-362 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 260 | 380 | 142.3
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #1 | Shore Road Bus Tie | 260 | 380 | 141.45
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-364 | Shore Road Bus Tie | 260 | 380 | 138.17
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | LKE SCSS 138/69 Bank #6 | Y50 | 260 | 380 | 130.4
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 69-481 | Y50 | 260 | 380 | 129.6
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 69-372 | Y50 | 260 | 380 | 127.61
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 69-371 | Y50 | 260 | 380 | 127.29
129247 L SUCS 138 129293 SHORE RD 138 1 Max | [5 empty] | 240.87
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | RAINEYE - FARRAGUT WEST 345 62 | Y50 | 285 | 368 | 290.97
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | RAINEYW - FARRAGUTE 345 61 | Y50 | 285 | 368 | 290.49
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | RAINEYE - FARRAGUTTIE 345 63 | Y50 | 285 | 368 | 290.31
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | NNC-B | Y50 | 285 | 368 | 290.11
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | NNC-C | Y50 | 285 | 368 | 290.1
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | NNC-A | Y50 | 285 | 368 | 290.05
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | NNC-1C | Y50 | 285 | 368 | 290.05
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 69-863 | Y50 | 285 | 368 | 289.74
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-677 | Y50 | 285 | 368 | 289.47
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | DNWDIE - MOTTHAVEN 345 71 | Y50 | 285 | 368 | 289.34
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 69-858 | Y50 | 285 | 368 | 289.25
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 69-371 | Y50 | 285 | 368 | 289.09
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 69-475 | Y50 | 285 | 368 | 289.02
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 69-372 | Y50 | 285 | 368 | 289
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 69-366 364 | Y50 | 285 | 368 | 288.98
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 69-481 | Y50 | 285 | 368 | 288.98
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | MOTTHAVEN - RAINEY Q12 345 | Y50 | 285 | 368 | 288.96
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | S:E13TH_M54 | Y50 | 285 | 368 | 288.96
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 69-552 | Y50 | 285 | 368 | 288.95
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 69-466 | Y50 | 285 | 368 | 288.94
129248 L SUCS2 138 129249 L SUCSPH 138 1 Max | [5 empty] | 290.97
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | LKE SCSS 138/69 Bank #5 | Y50 | 260 | 380 | 248.49
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-365 | 20 :SRD BUS1 | 260 | 380 | 237.81
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-367 | Y50 | 260 | 380 | 225.73
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-365 | Shore Road Bus Tie | 260 | 380 | 176.6
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-361 | 20 :SRD BUS1 | 260 | 380 | 163.19
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-363 | 20 :SRD BUS1 | 260 | 380 | 161.97
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-365 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 260 | 380 | 156.42
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-366 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 260 | 380 | 156.41
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 260 | 380 | 155.69
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-366 | 138-365 | 260 | 380 | 154.56
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-366 | 35 :GLNSO BUS | 260 | 380 | 154.56
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-365 | 36 :GLNNO BUS | 260 | 380 | 154.55
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-365 | 138-366 | 260 | 380 | 154.55
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #2 | Shore Road Bus Tie | 260 | 380 | 144.73
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-362 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 260 | 380 | 142.94
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | Shore Road Bus Tie | 260 | 380 | 140.76
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-361 | Shore Road Bus Tie | 260 | 380 | 136.21
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-363 | Shore Road Bus Tie | 260 | 380 | 134.76
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | LKE SCSS 138/69 Bank #6 | Y50 | 260 | 380 | 131.93
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 69-481 | Y50 | 260 | 380 | 131.02
129248 L SUCS2 138 129294 SHORE RD2 138 2 Max | [5 empty] | 248.49
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | VLY STRM 138/69 kV Bank #5 | 320 | 352 | 553.7
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | 8 :VST BUS1 | 320 | 352 | 552.53
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | 901 L&M | 320 | 352 | 540.74
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | JAMCA - VLLYSTRM 901L&M 138 | 320 | 352 | 540.74
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | VLY STRM 138 kV P.A.R. | 320 | 352 | 539.12
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 36 :GLNNO BUS | 320 | 352 | 520.42
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 138-366 | 320 | 352 | 520.42
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | Y49 | 320 | 352 | 514.5
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 320 | 352 | 510.56
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 138-362 | 320 | 352 | 500.74
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 138-364 | 320 | 352 | 499.89
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 37 :GLNGT BUS | 320 | 352 | 499.89
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 320 | 352 | 499.88
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 20 :SRD BUS1 | 320 | 352 | 470.43
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | NNC-3C | 320 | 352 | 469.52
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | Northport-Norwalk NNC-3C | 320 | 352 | 469.52
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | 72 :NPT BUS1-2 | 320 | 352 | 469.48
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 8 :VST BUS1 | 320 | 352 | 465.15
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | VLY STRM 138/69 kV Bank #5 | 320 | 352 | 464.88
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | Y49 | 320 | 352 | 463.99
129265 CARLE PL 138 129270 E.G.C. 138 1 Max | [5 empty] | 553.7
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | VLY STRM 138/69 kV Bank #5 | 325 | 388 | 499.46
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | 8 :VST BUS1 | 325 | 388 | 498.39
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | JAMCA - VLLYSTRM 901L&M 138 | 325 | 388 | 487.75
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | 901 L&M | 325 | 388 | 487.75
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | VLY STRM 138 kV P.A.R. | 325 | 388 | 486.3
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 138-366 | 325 | 388 | 469.51
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 36 :GLNNO BUS | 325 | 388 | 469.51
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | Y49 | 325 | 388 | 463.99
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 325 | 388 | 460.56
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 138-362 | 325 | 388 | 451.67
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 37 :GLNGT BUS | 325 | 388 | 450.9
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 325 | 388 | 450.9
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 138-364 | 325 | 388 | 450.9
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | Base Case | 325 | 388 | 441.21
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 20 :SRD BUS1 | 325 | 388 | 424.14
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | NNC-3C | 325 | 388 | 423.28
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | Northport-Norwalk NNC-3C | 325 | 388 | 423.28
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | 72 :NPT BUS1-2 | 325 | 388 | 423.24
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 8 :VST BUS1 | 325 | 388 | 419.05
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | VLY STRM 138/69 kV Bank #5 | 325 | 388 | 418.73
129265 CARLE PL 138 129283 GLNWD SO 138 1 Max | [5 empty] | 499.46
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 1105 EGC_345_OSW5 345 128825 EGC PAR 345 1 | 450 | 585 | 172.56
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | GEN: OSW EGC 5 | 450 | 585 | 172.5
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | GEN: OSW EGC 5 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 450 | 585 | 171.31
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | GEN: OSW EGC 5 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 450 | 585 | 171.31
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | GEN: OSW EGC 5 | E.G.C. 345 kV P.A.R. #2 | 450 | 585 | 171.31
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | Base Case | 450 | 585 | 161.05
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | GEN: OSW EGC 5 | Base Case | 450 | 585 | 152.39
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 20 :SRD BUS1 | 450 | 585 | 143.43
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 21 :SRD BUS2 | 450 | 585 | 142.95
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | SHORE RD 345/138 Bank #1 | 450 | 585 | 136.19
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | SHORE RD 345/138 Bank #2 | 450 | 585 | 135.21
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 35 :GLNSO BUS | 450 | 585 | 133.83
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 138-365 | 450 | 585 | 133.83
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | GEN: OSW EGC 5 | 20 :SRD BUS1 | 450 | 585 | 133.81
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 138-366 | 450 | 585 | 133.57
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 36 :GLNNO BUS | 450 | 585 | 133.57
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | GEN: OSW EGC 5 | 21 :SRD BUS2 | 450 | 585 | 133.34
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 450 | 585 | 133.19
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 450 | 585 | 132.91
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | 138-361 | 450 | 585 | 132.91
129270 E.G.C. 138 128822 E.G.C.-1 345 1 Max | [5 empty] | 172.56
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 35 :GLNSO BUS | 320 | 352 | 512.12
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-365 | 320 | 352 | 512.12
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 320 | 352 | 502.26
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-361 | 320 | 352 | 494.58
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-363 | 320 | 352 | 493.12
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 21 :SRD BUS2 | 320 | 352 | 467.67
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | Northport-Norwalk NNC-3C | 320 | 352 | 463.09
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | NNC-3C | 320 | 352 | 463.09
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | 72 :NPT BUS1-2 | 320 | 352 | 463.06
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | Y49 | 320 | 352 | 456.47
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 8 :VST BUS1 | 320 | 352 | 453.49
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | VLY STRM 138/69 kV Bank #5 | 320 | 352 | 453.2
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 901 L&M | 320 | 352 | 447.62
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | JAMCA - VLLYSTRM 901L&M 138 | 320 | 352 | 447.62
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | VLY STRM 138 kV P.A.R. | 320 | 352 | 446.25
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | NNC-3C | 35 :GLNSO BUS | 320 | 352 | 445.98
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Northport-Norwalk NNC-3C | 138-365 | 320 | 352 | 445.98
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | NNC-3C | 138-365 | 320 | 352 | 445.98
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Northport-Norwalk NNC-3C | 35 :GLNSO BUS | 320 | 352 | 445.98
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-361 | Northport-Norwalk NNC-3C | 320 | 352 | 443.27
129270 E.G.C. 138 129288 ROSLYN 138 1 Max | [5 empty] | 512.12
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-463 | 138-465 | 194 | 284 | 412.97
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | 138-463 | 194 | 284 | 412.68
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | Base Case | 194 | 284 | 404.4
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-463 | Base Case | 194 | 284 | 403.19
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW EGC 5 | Base Case | 194 | 284 | 398.24
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | Northport-Norwalk NNC-3C | Base Case | 194 | 284 | 391.9
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | NNC-3C | Base Case | 194 | 284 | 391.9
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | GOWANUS 345/138 2TR | Base Case | 194 | 284 | 380.08
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | ASTORIA 345/138 PS | Base Case | 194 | 284 | 379.64
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | SPRNBRK - TREMONT X28 345 | Base Case | 194 | 284 | 378.74
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 194 | 284 | 378.38
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | SPRNBRK - ACDMY 345 M29 | Base Case | 194 | 284 | 376.86
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | MILLWOOD - SPRNBRK W82/W65 345 | Base Case | 194 | 284 | 372.85
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | MILLWOOD - SPRNBRK W85/W78 345 | Base Case | 194 | 284 | 372.84
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | MILLWOOD - SPRNBRK W99/W64 345 | Base Case | 194 | 284 | 372.52
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | SPRNBRK - W49ST 345 M52 | Base Case | 194 | 284 | 372.51
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | SPRNBRK - W49ST 345 M51 | Base Case | 194 | 284 | 372.45
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | RAMAPO - BUCHN 345 Y94 | Base Case | 194 | 284 | 372.2
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | BUCH - SPRNBRK W93/W79 345 | Base Case | 194 | 284 | 372.18
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | PV - MILLWOOD 345 F30/W80 | Base Case | 194 | 284 | 370.81
129270 E.G.C. 138 129310 NEWBRGE 138 1 Max | [5 empty] | 412.97
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | 138-463 | 216 | 306 | 372.06
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-463 | 138-462 | 216 | 306 | 371.83
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | Base Case | 216 | 306 | 354.52
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-463 | Base Case | 216 | 306 | 348.88
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | GEN: OSW EGC 5 | Base Case | 216 | 306 | 345.22
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | NNC-3C | Base Case | 216 | 306 | 339.57
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | Northport-Norwalk NNC-3C | Base Case | 216 | 306 | 339.57
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | 138-467 | 216 | 306 | 329.56
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | GOWANUS 345/138 2TR | Base Case | 216 | 306 | 329.29
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | ASTORIA 345/138 PS | Base Case | 216 | 306 | 328.89
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | SPRNBRK - TREMONT X28 345 | Base Case | 216 | 306 | 328.15
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-467 | 138-462 | 216 | 306 | 328.08
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | GEN: OSW EGC 5 | 138-462 | 216 | 306 | 328.08
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 216 | 306 | 327.83
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | Northport-Norwalk NNC-3C | 216 | 306 | 327.73
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | NNC-3C | 216 | 306 | 327.73
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | 72 :NPT BUS1-2 | 216 | 306 | 327.6
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | SPRNBRK - ACDMY 345 M29 | Base Case | 216 | 306 | 326.53
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-463 | 138-467 | 216 | 306 | 326.3
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-467 | 138-463 | 216 | 306 | 325.02
129270 E.G.C. 138 129310 NEWBRGE 138 3 Max | [5 empty] | 372.06
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | 1105 EGC_345_OSW5 345 128825 EGC PAR 345 1 | 450 | 585 | 172.3
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | 1105 EGC_345_OSW5 345 128825 EGC PAR 345 1 | 450 | 585 | 172.3
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | GEN: OSW EGC 5 | 450 | 585 | 172.24
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | GEN: OSW EGC 5 | 450 | 585 | 172.24
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW EGC 5 | E.G.C. 345 kV P.A.R. #1 | 450 | 585 | 172.23
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW EGC 5 | 33 :EGC BUS2 | 450 | 585 | 172.23
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW EGC 5 | EGC REA | 450 | 585 | 172.23
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW EGC 5 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 450 | 585 | 172.23
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW EGC 5 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 450 | 585 | 172.23
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | Base Case | 450 | 585 | 160.94
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | Base Case | 450 | 585 | 160.94
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW EGC 5 | Base Case | 450 | 585 | 155.84
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | 20 :SRD BUS1 | 450 | 585 | 143.31
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | 20 :SRD BUS1 | 450 | 585 | 143.31
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | 21 :SRD BUS2 | 450 | 585 | 142.84
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | 21 :SRD BUS2 | 450 | 585 | 142.84
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | SHORE RD 345/138 Bank #1 | 450 | 585 | 136.08
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | SHORE RD 345/138 Bank #1 | 450 | 585 | 136.08
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW EGC 5 | 20 :SRD BUS1 | 450 | 585 | 135.65
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW EGC 5 | 21 :SRD BUS2 | 450 | 585 | 135.19
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 Max | [5 empty] | 172.3
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | 138-465 | 210 | 302 | 385.31
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-465 | 138-462 | 210 | 302 | 384.79
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | Base Case | 210 | 302 | 366.57
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-465 | Base Case | 210 | 302 | 361.75
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GEN: OSW EGC 5 | Base Case | 210 | 302 | 358.76
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | NNC-3C | Base Case | 210 | 302 | 352.49
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | Northport-Norwalk NNC-3C | Base Case | 210 | 302 | 352.49
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GOWANUS 345/138 2TR | Base Case | 210 | 302 | 341.64
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | ASTORIA 345/138 PS | Base Case | 210 | 302 | 341.28
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | SPRNBRK - TREMONT X28 345 | Base Case | 210 | 302 | 340.32
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 210 | 302 | 340.16
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | 138-467 | 210 | 302 | 339.8
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | SPRNBRK - ACDMY 345 M29 | Base Case | 210 | 302 | 338.76
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-467 | 138-462 | 210 | 302 | 338.21
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GEN: OSW EGC 5 | 138-462 | 210 | 302 | 335.57
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | MILLWOOD - SPRNBRK W82/W65 345 | Base Case | 210 | 302 | 335.13
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | MILLWOOD - SPRNBRK W85/W78 345 | Base Case | 210 | 302 | 335.12
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | MILLWOOD - SPRNBRK W99/W64 345 | Base Case | 210 | 302 | 334.83
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | SPRNBRK - W49ST 345 M52 | Base Case | 210 | 302 | 334.79
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | SPRNBRK - W49ST 345 M51 | Base Case | 210 | 302 | 334.75
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 Max | [5 empty] | 385.31
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-463 | Base Case | 270 | 474 | 210.27
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-462 | Base Case | 270 | 474 | 210.19
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-465 | Base Case | 270 | 474 | 207.76
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | GEN: OSW EGC 5 | Base Case | 270 | 474 | 206.11
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | NNC-3C | Base Case | 270 | 474 | 202.41
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | Northport-Norwalk NNC-3C | Base Case | 270 | 474 | 202.41
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | GOWANUS 345/138 2TR | Base Case | 270 | 474 | 196.17
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | ASTORIA 345/138 PS | Base Case | 270 | 474 | 195.95
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | SPRNBRK - TREMONT X28 345 | Base Case | 270 | 474 | 195.42
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 270 | 474 | 195.32
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | SPRNBRK - ACDMY 345 M29 | Base Case | 270 | 474 | 194.54
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-462 | 138-465 | 270 | 474 | 180.99
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-462 | 138-463 | 270 | 474 | 180.82
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-465 | 138-462 | 270 | 474 | 180.74
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-463 | 138-462 | 270 | 474 | 180.71
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-463 | 138-465 | 270 | 474 | 179.53
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-465 | 138-463 | 270 | 474 | 179.4
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | GEN: OSW EGC 5 | 138-463 | 270 | 474 | 158.11
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | GEN: OSW EGC 5 | 138-462 | 270 | 474 | 157.71
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-463 | NNC-3C | 270 | 474 | 157.25
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 Max | [5 empty] | 210.27
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-291 | 138-292 | 229 | 299 | 327.77
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 138-291 | 229 | 299 | 326.47
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 229 | 299 | 325.78
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 8 :VST BUS1 | 229 | 299 | 325.78
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 229 | 299 | 323.28
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | Valley Stream Bus Tie | 229 | 299 | 133.85
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-261 | 138-262 | 229 | 299 | 113.78
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-262 | 138-261 | 229 | 299 | 112.94
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW Barret 2 | Base Case | 229 | 299 | 105.67
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW Holbrook 2 | Base Case | 229 | 299 | 105.67
129276 FREEPORT 138 129310 NEWBRGE 138 1 Max | [5 empty] | 327.77
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 35 :GLNSO BUS | 351 | 388 | 463.04
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 138-365 | 351 | 388 | 463.04
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 351 | 388 | 454.11
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 138-361 | 351 | 388 | 447.14
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 138-363 | 351 | 388 | 445.83
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 21 :SRD BUS2 | 351 | 388 | 422.5
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | NNC-3C | 351 | 388 | 418.59
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | Northport-Norwalk NNC-3C | 351 | 388 | 418.59
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | 72 :NPT BUS1-2 | 351 | 388 | 418.56
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | Y49 | 351 | 388 | 412.65
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 8 :VST BUS1 | 351 | 388 | 409.52
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | VLY STRM 138/69 kV Bank #5 | 351 | 388 | 409.2
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | JAMCA - VLLYSTRM 901L&M 138 | 351 | 388 | 404.25
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 901 L&M | 351 | 388 | 404.25
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | NNC-3C | 35 :GLNSO BUS | 351 | 388 | 403.06
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | NNC-3C | 138-365 | 351 | 388 | 403.06
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Northport-Norwalk NNC-3C | 35 :GLNSO BUS | 351 | 388 | 403.06
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Northport-Norwalk NNC-3C | 138-365 | 351 | 388 | 403.06
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | VLY STRM 138 kV P.A.R. | 351 | 388 | 403
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-361 | Northport-Norwalk NNC-3C | 351 | 388 | 400.63
129281 GLNWD GT 138 129282 GLNWD NO 138 1 Max | [5 empty] | 463.04
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-365 | 351 | 388 | 463.05
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 35 :GLNSO BUS | 351 | 388 | 463.05
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 351 | 388 | 454.12
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-361 | 351 | 388 | 447.15
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-363 | 351 | 388 | 445.83
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 21 :SRD BUS2 | 351 | 388 | 422.52
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | NNC-3C | 351 | 388 | 418.59
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | Northport-Norwalk NNC-3C | 351 | 388 | 418.59
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | 72 :NPT BUS1-2 | 351 | 388 | 418.56
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | Y49 | 351 | 388 | 412.66
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 8 :VST BUS1 | 351 | 388 | 409.51
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | VLY STRM 138/69 kV Bank #5 | 351 | 388 | 409.19
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | JAMCA - VLLYSTRM 901L&M 138 | 351 | 388 | 404.25
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 901 L&M | 351 | 388 | 404.25
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | NNC-3C | 138-365 | 351 | 388 | 403.06
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | NNC-3C | 35 :GLNSO BUS | 351 | 388 | 403.06
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Northport-Norwalk NNC-3C | 35 :GLNSO BUS | 351 | 388 | 403.06
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Northport-Norwalk NNC-3C | 138-365 | 351 | 388 | 403.06
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | VLY STRM 138 kV P.A.R. | 351 | 388 | 403
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-361 | Northport-Norwalk NNC-3C | 351 | 388 | 400.63
129281 GLNWD GT 138 129288 ROSLYN 138 1 Max | [5 empty] | 463.05
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 138-365 | 381 | 446 | 475.83
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 35 :GLNSO BUS | 381 | 446 | 475.83
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 381 | 446 | 474.86
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 138-361 | 381 | 446 | 446
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 138-363 | 381 | 446 | 444.7
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 21 :SRD BUS2 | 381 | 446 | 441.79
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | 72 :NPT BUS1-2 | 381 | 446 | 425.21
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | NNC-3C | 381 | 446 | 425.21
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | Northport-Norwalk NNC-3C | 381 | 446 | 425.21
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | Y49 | 381 | 446 | 416.66
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | NNC-3C | 138-365 | 381 | 446 | 415.69
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | NNC-3C | 35 :GLNSO BUS | 381 | 446 | 415.69
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Northport-Norwalk NNC-3C | 35 :GLNSO BUS | 381 | 446 | 415.69
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Northport-Norwalk NNC-3C | 138-365 | 381 | 446 | 415.69
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Northport-Norwalk NNC-3C | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 381 | 446 | 413
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | NNC-3C | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 381 | 446 | 413
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 8 :VST BUS1 | 381 | 446 | 408.96
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | VLY STRM 138/69 kV Bank #5 | 381 | 446 | 408.64
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 901 L&M | 381 | 446 | 405.22
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | JAMCA - VLLYSTRM 901L&M 138 | 381 | 446 | 405.22
129282 GLNWD NO 138 129293 SHORE RD 138 1 Max | [5 empty] | 475.83
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | VLY STRM 138/69 kV Bank #5 | 351 | 388 | 564.93
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | 8 :VST BUS1 | 351 | 388 | 563.74
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | JAMCA - VLLYSTRM 901L&M 138 | 351 | 388 | 553.61
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | 901 L&M | 351 | 388 | 553.61
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | VLY STRM 138 kV P.A.R. | 351 | 388 | 552.1
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 138-366 | 351 | 388 | 548.85
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 36 :GLNNO BUS | 351 | 388 | 548.85
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 351 | 388 | 547.43
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | Y49 | 351 | 388 | 525.83
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 138-362 | 351 | 388 | 512.48
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 37 :GLNGT BUS | 351 | 388 | 511.62
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 138-364 | 351 | 388 | 511.62
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 351 | 388 | 511.61
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 20 :SRD BUS1 | 351 | 388 | 503.96
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | Northport-Norwalk NNC-3C | 351 | 388 | 488.32
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | NNC-3C | 351 | 388 | 488.32
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | 72 :NPT BUS1-2 | 351 | 388 | 488.3
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | Y49 | 351 | 388 | 479.91
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | NNC-3C | 138-366 | 351 | 388 | 477.71
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | NNC-3C | 36 :GLNNO BUS | 351 | 388 | 477.71
129283 GLNWD SO 138 129294 SHORE RD2 138 1 Max | [5 empty] | 564.93
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 138-677 | 72 :NPT BUS1-2 | 365 | 602 | 151.53
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 138-677 | Northport Bus Tie No.1-1 | 365 | 602 | 142.74
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | RAINEY - CORONA PAR | Base Case | 365 | 602 | 127.04
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | RAINEY-CORONA PAR 2 | Base Case | 365 | 602 | 126.59
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | EFISHKILL - PLSNTVLLE F38/Y86 345 | Base Case | 365 | 602 | 120.12
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | 138-677 | Base Case | 365 | 602 | 118.41
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW EGC 5 | Base Case | 365 | 602 | 108.02
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW Holbrook 2 | Base Case | 365 | 602 | 106.19
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW Barret 2 | Base Case | 365 | 602 | 106.19
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | GOWANUS 345/138 2TR | Base Case | 365 | 602 | 105.45
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 365 | 602 | 105.41
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | SPRNBRK - TREMONT X28 345 | Base Case | 365 | 602 | 105.33
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | ASTORIA 345/138 PS | Base Case | 365 | 602 | 105.24
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | MILLWOOD - SPRNBRK W82/W65 345 | Base Case | 365 | 602 | 105.21
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | MILLWOOD - SPRNBRK W85/W78 345 | Base Case | 365 | 602 | 105.21
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | SPRNBRK - ACDMY 345 M29 | Base Case | 365 | 602 | 105.04
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | Northport-Norwalk NNC-3C | Base Case | 365 | 602 | 104.93
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | NNC-3C | Base Case | 365 | 602 | 104.93
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | SPRNBRK - W49ST 345 M52 | Base Case | 365 | 602 | 104.84
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | SPRNBRK - W49ST 345 M51 | Base Case | 365 | 602 | 104.79
129305 LCST GRV 138 129310 NEWBRGE 138 1 Max | [5 empty] | 151.53
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 138-677 | 72 :NPT BUS1-2 | 529 | 591 | 155.72
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 138-677 | Northport Bus Tie No.1-1 | 529 | 591 | 146.73
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 138-677 | Northport-Norwalk NNC-3C | 529 | 591 | 108.04
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 138-677 | NNC-3C | 529 | 591 | 108.04
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 138-563 | 72 :NPT BUS1-2 | 529 | 591 | 103.24
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 138-564 | 72 :NPT BUS1-2 | 529 | 591 | 103.24
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 138-561 | 72 :NPT BUS1-2 | 529 | 591 | 103.04
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | SYOSSET 138/69 Bank #5 | 72 :NPT BUS1-2 | 529 | 591 | 102.1
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 69-533 | 72 :NPT BUS1-2 | 529 | 591 | 101.53
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 69-532 | 72 :NPT BUS1-2 | 529 | 591 | 101.27
129305 LCST GRV 138 129315 SYOSSET 138 1 | 11 | 69-531 | 72 :NPT BUS1-2 | 529 | 591 | 101.03
129305 LCST GRV 138 129315 SYOSSET 138 1 Max | [5 empty] | 155.72
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | 138-559 | 577 | 618 | 110.02
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | Northport-Norwalk NNC-3C | 138-559 | 577 | 618 | 110.02
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | 138-558 | 577 | 618 | 109.7
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | Northport-Norwalk NNC-3C | 138-558 | 577 | 618 | 109.7
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | NNC-3C | 577 | 618 | 108.58
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | Northport-Norwalk NNC-3C | 577 | 618 | 108.58
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | Northport-Norwalk NNC-3C | 75 :NPT BUS3 | 577 | 618 | 108.44
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | 75 :NPT BUS3 | 577 | 618 | 108.44
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | NRTHPRT P.A.R. #2 (Bus) | 577 | 618 | 108.34
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | Northport-Norwalk NNC-3C | NRTHPRT P.A.R. #2 (Bus) | 577 | 618 | 108.34
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 72 :NPT BUS1-2 | 577 | 618 | 108.22
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | Northport-Norwalk NNC-3C | 138-562 | 577 | 618 | 106.71
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | Northport-Norwalk NNC-3C | 138-561 | 577 | 618 | 106.71
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | 138-561 | 577 | 618 | 106.71
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | 138-562 | 577 | 618 | 106.71
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | 138-567 | 577 | 618 | 106.34
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | Northport-Norwalk NNC-3C | 138-567 | 577 | 618 | 106.34
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | GEN: OSW EGC 5 | 138-559 | 577 | 618 | 106.27
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | GEN: OSW EGC 5 | 138-558 | 577 | 618 | 105.95
129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 11 | GEN: OSW EGC 5 | 75 :NPT BUS3 | 577 | 618 | 104.69
129310 NEWBRGE 138 129324 BETHPAGE 138 1 Max | [5 empty] | 110.02
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | 138-567 | 302 | 331 | 266.43
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | 138-562 | 302 | 331 | 266
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | Northport-Norwalk NNC-3C | 138-562 | 302 | 331 | 236.69
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | NNC-3C | 138-562 | 302 | 331 | 236.69
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | Northport-Norwalk NNC-3C | 138-567 | 302 | 331 | 234.84
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | NNC-3C | 138-567 | 302 | 331 | 234.84
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | GEN: OSW EGC 5 | 138-562 | 302 | 331 | 232.39
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | GEN: OSW EGC 5 | 138-567 | 302 | 331 | 230.68
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | Northport-Norwalk NNC-3C | 302 | 331 | 230.12
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | NNC-3C | 302 | 331 | 230.12
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | 72 :NPT BUS1-2 | 302 | 331 | 228.55
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | NNC-3C | 302 | 331 | 227.91
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | Northport-Norwalk NNC-3C | 302 | 331 | 227.91
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-563 | 138-562 | 302 | 331 | 226.86
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | 72 :NPT BUS1-2 | 302 | 331 | 226.36
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-563 | 138-567 | 302 | 331 | 225.63
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-564 | 138-562 | 302 | 331 | 225.04
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | ASTORIA 345/138 PS | 138-562 | 302 | 331 | 224.35
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | GOWANUS 345/138 2TR | 138-562 | 302 | 331 | 224.34
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-564 | 138-567 | 302 | 331 | 223.9
129310 NEWBRGE 138 129361 RULND RD 138 1 Max | [5 empty] | 266.43
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | 138-561 | 302 | 331 | 266
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | 138-567 | 302 | 331 | 265.42
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | NNC-3C | 138-561 | 302 | 331 | 236.68
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | Northport-Norwalk NNC-3C | 138-561 | 302 | 331 | 236.68
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | Northport-Norwalk NNC-3C | 138-567 | 302 | 331 | 234.82
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | NNC-3C | 138-567 | 302 | 331 | 234.82
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | GEN: OSW EGC 5 | 138-561 | 302 | 331 | 232.38
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | GEN: OSW EGC 5 | 138-567 | 302 | 331 | 230.67
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | NNC-3C | 302 | 331 | 229.35
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | Northport-Norwalk NNC-3C | 302 | 331 | 229.35
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | NNC-3C | 302 | 331 | 227.9
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | Northport-Norwalk NNC-3C | 302 | 331 | 227.9
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | 72 :NPT BUS1-2 | 302 | 331 | 227.85
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-563 | 138-561 | 302 | 331 | 226.85
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | 72 :NPT BUS1-2 | 302 | 331 | 226.34
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-563 | 138-567 | 302 | 331 | 225.62
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-564 | 138-561 | 302 | 331 | 225.03
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | ASTORIA 345/138 PS | 138-561 | 302 | 331 | 224.34
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | GOWANUS 345/138 2TR | 138-561 | 302 | 331 | 224.33
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-564 | 138-567 | 302 | 331 | 223.89
129310 NEWBRGE 138 129361 RULND RD 138 2 Max | [5 empty] | 266
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-562 | Base Case | 259 | 388 | 233.54
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-561 | Base Case | 259 | 388 | 232.58
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | NNC-3C | Base Case | 259 | 388 | 225.57
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | Northport-Norwalk NNC-3C | Base Case | 259 | 388 | 225.57
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-562 | 138-561 | 259 | 388 | 225.33
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-561 | 138-562 | 259 | 388 | 224.49
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | GEN: OSW EGC 5 | Base Case | 259 | 388 | 223.14
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | ASTORIA 345/138 PS | Base Case | 259 | 388 | 215.28
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | GOWANUS 345/138 2TR | Base Case | 259 | 388 | 215.26
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | SPRNBRK - TREMONT X28 345 | Base Case | 259 | 388 | 214.42
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | SPRNBRK - DUNWDIE 345 W75 | Base Case | 259 | 388 | 214.26
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | SPRNBRK - ACDMY 345 M29 | Base Case | 259 | 388 | 214.01
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | MILLWOOD - SPRNBRK W85/W78 345 | Base Case | 259 | 388 | 213.81
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | MILLWOOD - SPRNBRK W82/W65 345 | Base Case | 259 | 388 | 213.81
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | SPRNBRK - W49ST 345 M52 | Base Case | 259 | 388 | 213.78
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | SPRNBRK - W49ST 345 M51 | Base Case | 259 | 388 | 213.77
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-563 | Base Case | 259 | 388 | 213.63
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | MILLWOOD - SPRNBRK W99/W64 345 | Base Case | 259 | 388 | 213.04
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | RAMAPO - BUCHN 345 Y94 | Base Case | 259 | 388 | 212.56
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | BUCH - SPRNBRK W93/W79 345 | Base Case | 259 | 388 | 212.42
129310 NEWBRGE 138 129361 RULND RD 138 3 Max | [5 empty] | 233.54
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | ELWOOD 138/69 kV Bank #3 | 72 :NPT BUS1-2 | 265 | 368 | 157.49
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-674 | 72 :NPT BUS1-2 | 265 | 368 | 155.56
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-675 | 72 :NPT BUS1-2 | 265 | 368 | 155.01
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | ELWOOD 138/69 kV Bank #3 | Northport-Norwalk NNC-3C | 265 | 368 | 151.87
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | ELWOOD 138/69 kV Bank #3 | NNC-3C | 265 | 368 | 151.87
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-674 | Northport-Norwalk NNC-3C | 265 | 368 | 150.06
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-674 | NNC-3C | 265 | 368 | 150.06
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-675 | NNC-3C | 265 | 368 | 149.57
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-675 | Northport-Norwalk NNC-3C | 265 | 368 | 149.57
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-681 | 72 :NPT BUS1-2 | 265 | 368 | 148.25
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-677 | 72 :NPT BUS1-2 | 265 | 368 | 146.74
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | ELWOOD 138/69 kV Bank #3 | Base Case | 265 | 368 | 142.81
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-681 | Northport-Norwalk NNC-3C | 265 | 368 | 142.29
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-681 | NNC-3C | 265 | 368 | 142.29
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-674 | Base Case | 265 | 368 | 140.13
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-675 | Base Case | 265 | 368 | 139.36
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-677 | Northport Bus Tie No.1-1 | 265 | 368 | 138.59
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-681 | Base Case | 265 | 368 | 133.31
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | ELWOOD 138/69 kV Bank #3 | 138-564 | 265 | 368 | 127.43
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | ELWOOD 138/69 kV Bank #3 | 129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 265 | 368 | 127.05
129315 SYOSSET 138 129333 GRENLAWN 138 1 Max | [5 empty] | 157.49
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-676 | 72 :NPT BUS1-2 | 265 | 368 | 152.4
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-678 | 72 :NPT BUS1-2 | 265 | 368 | 148.11
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-676 | NNC-3C | 265 | 368 | 147.12
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-676 | Northport-Norwalk NNC-3C | 265 | 368 | 147.12
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-673 | 72 :NPT BUS1-2 | 265 | 368 | 146.72
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-677 | 72 :NPT BUS1-2 | 265 | 368 | 143.2
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-678 | Northport-Norwalk NNC-3C | 265 | 368 | 142.32
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-678 | NNC-3C | 265 | 368 | 142.32
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-673 | NNC-3C | 265 | 368 | 140.86
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-673 | Northport-Norwalk NNC-3C | 265 | 368 | 140.86
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-676 | Base Case | 265 | 368 | 137.44
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-677 | Northport Bus Tie No.1-1 | 265 | 368 | 136.49
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-678 | Base Case | 265 | 368 | 131.83
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-673 | Base Case | 265 | 368 | 130.33
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-676 | 138-564 | 265 | 368 | 122.94
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-676 | 129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 265 | 368 | 122.61
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-676 | 138-563 | 265 | 368 | 122.6
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-676 | 129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 265 | 368 | 122.6
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | RAINEY - CORONA PAR | 138-676 | 265 | 368 | 117.54
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-678 | 138-564 | 265 | 368 | 117.38
129315 SYOSSET 138 129351 OAKWOOD 138 1 Max | [5 empty] | 152.4
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | Base Case | 418 | 618 | 139.56
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | Northport-Norwalk NNC-3C | Base Case | 418 | 618 | 139.56
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | GEN: OSW EGC 5 | Base Case | 418 | 618 | 135.86
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | ASTORIA 345/138 PS | Base Case | 418 | 618 | 128.24
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | GOWANUS 345/138 2TR | Base Case | 418 | 618 | 128.05
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | SPRNBRK - ACDMY 345 M29 | Base Case | 418 | 618 | 127.29
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | SPRNBRK - TREMONT X28 345 | Base Case | 418 | 618 | 127.12
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | MILLWOOD - SPRNBRK W82/W65 345 | Base Case | 418 | 618 | 127.08
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | MILLWOOD - SPRNBRK W85/W78 345 | Base Case | 418 | 618 | 127.07
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | SPRNBRK - W49ST 345 M52 | Base Case | 418 | 618 | 126.96
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | 138-559 | 418 | 618 | 110.28
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | 138-558 | 418 | 618 | 109.94
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | Northport-Norwalk NNC-3C | 418 | 618 | 108.75
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | 75 :NPT BUS3 | 418 | 618 | 108.68
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | NRTHPRT P.A.R. #2 (Bus) | 418 | 618 | 108.59
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 72 :NPT BUS1-2 | 418 | 618 | 108.51
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | 138-561 | 418 | 618 | 106.92
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | Northport-Norwalk NNC-3C | 138-562 | 418 | 618 | 106.92
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | NNC-3C | 138-567 | 418 | 618 | 106.47
129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 11 | GEN: OSW EGC 5 | 138-559 | 418 | 618 | 106.44
129321 BAGATELLE 138 129324 BETHPAGE 138 1 Max | [5 empty] | 139.56
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | Northport-Norwalk NNC-3C | 138-559 | 572 | 617 | 111.12
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | NNC-3C | 138-559 | 572 | 617 | 111.12
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | Northport-Norwalk NNC-3C | 138-558 | 572 | 617 | 110.78
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | NNC-3C | 138-558 | 572 | 617 | 110.78
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | Northport-Norwalk NNC-3C | 572 | 617 | 109.59
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | NNC-3C | 572 | 617 | 109.59
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | Northport-Norwalk NNC-3C | 75 :NPT BUS3 | 572 | 617 | 109.51
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | NNC-3C | 75 :NPT BUS3 | 572 | 617 | 109.51
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | NNC-3C | NRTHPRT P.A.R. #2 (Bus) | 572 | 617 | 109.42
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | Northport-Norwalk NNC-3C | NRTHPRT P.A.R. #2 (Bus) | 572 | 617 | 109.42
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 72 :NPT BUS1-2 | 572 | 617 | 109.35
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | Northport-Norwalk NNC-3C | 138-562 | 572 | 617 | 107.75
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | Northport-Norwalk NNC-3C | 138-561 | 572 | 617 | 107.75
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | NNC-3C | 138-561 | 572 | 617 | 107.75
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | NNC-3C | 138-562 | 572 | 617 | 107.75
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | NNC-3C | 138-567 | 572 | 617 | 107.3
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | Northport-Norwalk NNC-3C | 138-567 | 572 | 617 | 107.3
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | GEN: OSW EGC 5 | 138-559 | 572 | 617 | 107.27
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | GEN: OSW EGC 5 | 138-558 | 572 | 617 | 106.93
129321 BAGATELLE 138 129355 PILGRIM 138 1 | 11 | GEN: OSW EGC 5 | 75 :NPT BUS3 | 572 | 617 | 105.67
129321 BAGATELLE 138 129355 PILGRIM 138 1 Max | [5 empty] | 111.12
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | 138-882 | 68 : PIL BUS2 | 351 | 375 | 137.22
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | HOLBROOK 138/69 Bank #2 | PILGRIM 138/69 Bank #4 | 351 | 375 | 137.22
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 68 : PIL BUS2 | 351 | 375 | 137.22
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | 138-882 | PILGRIM 138/69 Bank #4 | 351 | 375 | 137.22
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | 138-882 | 138-881 NEW | 351 | 375 | 135.37
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-881 NEW | 351 | 375 | 135.37
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | 138-882 | 138-881 | 351 | 375 | 133.86
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-881 | 351 | 375 | 133.86
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | PILGRIM 138/69 Bank #4 | 138-882 | 351 | 375 | 103.63
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | PILGRIM 138/69 Bank #4 | 108:HOL BUS2 | 351 | 375 | 103.63
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | PILGRIM 138/69 Bank #4 | HOLBROOK 138/69 Bank #2 | 351 | 375 | 103.63
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | PILGRIM 138/69 Bank #4 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 351 | 375 | 102.53
129337 HAUPAGUE 138 129356 PILGRM P 138 1 Max | [5 empty] | 137.22
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-882 | 68 : PIL BUS2 | 215 | 288 | 180.71
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-882 | PILGRIM 138/69 Bank #4 | 215 | 288 | 180.71
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | HOLBROOK 138/69 Bank #2 | PILGRIM 138/69 Bank #4 | 215 | 288 | 180.71
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 68 : PIL BUS2 | 215 | 288 | 180.71
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-881 NEW | 215 | 288 | 178.3
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-882 | 138-881 NEW | 215 | 288 | 178.3
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-882 | 138-881 | 215 | 288 | 176.33
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-881 | 215 | 288 | 176.33
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | PILGRIM 138/69 Bank #4 | 138-882 | 215 | 288 | 137.14
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | PILGRIM 138/69 Bank #4 | 108:HOL BUS2 | 215 | 288 | 137.14
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | PILGRIM 138/69 Bank #4 | HOLBROOK 138/69 Bank #2 | 215 | 288 | 137.14
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | PILGRIM 138/69 Bank #4 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 215 | 288 | 135.72
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 NEW | 108:HOL BUS2 | 215 | 288 | 133.11
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 NEW | 138-882 | 215 | 288 | 133.11
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 NEW | HOLBROOK 138/69 Bank #2 | 215 | 288 | 133.11
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 | 108:HOL BUS2 | 215 | 288 | 132.05
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 | 138-882 | 215 | 288 | 132.05
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 | HOLBROOK 138/69 Bank #2 | 215 | 288 | 132.05
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 NEW | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 215 | 288 | 131.57
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 215 | 288 | 130.51
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 Max | [5 empty] | 180.71
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-875 | 572 | 617 | 131.34
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-882 | 138-875 | 572 | 617 | 131.34
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-883 | 572 | 617 | 130.4
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-882 | 138-883 | 572 | 617 | 130.4
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 108:HOL BUS2 | 572 | 617 | 128.9
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 138-882 | 572 | 617 | 128.9
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | C.ISLIP 138/69 Bank #3 | HOLBROOK 138/69 Bank #2 | 572 | 617 | 128.9
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 86 :CISL BUS3 | 572 | 617 | 128.33
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-882 | C.ISLIP 138/69 Bank #3 | 572 | 617 | 128.33
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-882 | 86 :CISL BUS3 | 572 | 617 | 128.33
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | C.ISLIP 138/69 Bank #3 | 572 | 617 | 128.33
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 572 | 617 | 128.07
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-875 | 138-882 | 572 | 617 | 123.47
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-875 | 108:HOL BUS2 | 572 | 617 | 123.47
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-875 | HOLBROOK 138/69 Bank #2 | 572 | 617 | 123.47
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-883 | 108:HOL BUS2 | 572 | 617 | 122.68
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-883 | HOLBROOK 138/69 Bank #2 | 572 | 617 | 122.68
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-883 | 138-882 | 572 | 617 | 122.68
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-875 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 572 | 617 | 122.46
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-883 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 572 | 617 | 121.68
129339 KINGS 138 129355 PILGRIM 138 1 Max | [5 empty] | 131.34
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-875 | 577 | 618 | 132.52
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-882 | 138-875 | 577 | 618 | 132.52
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-883 | 577 | 618 | 131.58
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-882 | 138-883 | 577 | 618 | 131.58
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 138-882 | 577 | 618 | 130.08
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 108:HOL BUS2 | 577 | 618 | 130.08
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | HOLBROOK 138/69 Bank #2 | 577 | 618 | 130.08
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 86 :CISL BUS3 | 577 | 618 | 129.52
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | C.ISLIP 138/69 Bank #3 | 577 | 618 | 129.52
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-882 | C.ISLIP 138/69 Bank #3 | 577 | 618 | 129.52
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-882 | 86 :CISL BUS3 | 577 | 618 | 129.52
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 577 | 618 | 129.26
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-875 | 138-882 | 577 | 618 | 124.66
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-875 | HOLBROOK 138/69 Bank #2 | 577 | 618 | 124.66
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-875 | 108:HOL BUS2 | 577 | 618 | 124.66
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-883 | 108:HOL BUS2 | 577 | 618 | 123.87
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-883 | 138-882 | 577 | 618 | 123.87
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-883 | HOLBROOK 138/69 Bank #2 | 577 | 618 | 123.87
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-875 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 577 | 618 | 123.65
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-883 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 577 | 618 | 122.88
129339 KINGS 138 129428 WEST BUS 138 1 Max | [5 empty] | 132.52
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 72 :NPT BUS1-2 | 517 | 591 | 198.65
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | Northport Bus Tie No.1-1 | 517 | 591 | 197.06
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | Northport-Norwalk NNC-3C | 517 | 591 | 124.12
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | NNC-3C | 517 | 591 | 124.12
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | GEN: OSW Holbrook 1 | 72 :NPT BUS1-2 | 517 | 591 | 117.38
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-361 | 72 :NPT BUS1-2 | 517 | 591 | 115.47
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-363 | 72 :NPT BUS1-2 | 517 | 591 | 115.31
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-364 | 72 :NPT BUS1-2 | 517 | 591 | 114.85
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | GEN: OSW Holbrook 1 | Northport-Norwalk NNC-3C | 517 | 591 | 113.14
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | GEN: OSW Holbrook 1 | NNC-3C | 517 | 591 | 113.14
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-361 | NNC-3C | 517 | 591 | 111.01
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-361 | Northport-Norwalk NNC-3C | 517 | 591 | 111.01
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-363 | Northport-Norwalk NNC-3C | 517 | 591 | 110.85
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-363 | NNC-3C | 517 | 591 | 110.85
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-364 | NNC-3C | 517 | 591 | 110.37
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-364 | Northport-Norwalk NNC-3C | 517 | 591 | 110.37
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 69-558 | 72 :NPT BUS1-2 | 517 | 591 | 109.88
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 69-573 | 72 :NPT BUS1-2 | 517 | 591 | 109.85
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 69-552 | 72 :NPT BUS1-2 | 517 | 591 | 109.77
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | GRENLAWN 138/69 Bank #5 | 72 :NPT BUS1-2 | 517 | 591 | 109.47
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 Max | [5 empty] | 198.65
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | Northport Bus Tie No.1-1 | 362 | 590 | 192.02
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 72 :NPT BUS1-2 | 362 | 590 | 191.3
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | GEN: OSW W49 Street 5 | Northport Bus Tie No.1-1 | 362 | 590 | 150.59
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | PV - EFISHKILL 345 F37 | Northport Bus Tie No.1-1 | 362 | 590 | 141.5
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | PV - EFISHKILL 345 F36 | Northport Bus Tie No.1-1 | 362 | 590 | 141.5
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 138-564 | Northport Bus Tie No.1-1 | 362 | 590 | 135.72
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 138-563 | Northport Bus Tie No.1-1 | 362 | 590 | 134.52
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 69-533 | Northport Bus Tie No.1-1 | 362 | 590 | 129.71
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 69-532 | Northport Bus Tie No.1-1 | 362 | 590 | 129.7
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 69-531 | Northport Bus Tie No.1-1 | 362 | 590 | 129.68
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | PILGRIM 138/69 Bank #3 | Northport Bus Tie No.1-1 | 362 | 590 | 129.22
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | NNC-3C | Northport Bus Tie No.1-1 | 362 | 590 | 127.67
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | Northport-Norwalk NNC-3C | Northport Bus Tie No.1-1 | 362 | 590 | 127.67
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | Northport-Norwalk NNC-3C | 72 :NPT BUS1-2 | 362 | 590 | 127.26
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | NNC-3C | 72 :NPT BUS1-2 | 362 | 590 | 127.26
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 138-562 | Northport Bus Tie No.1-1 | 362 | 590 | 126.55
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 138-567 | Northport Bus Tie No.1-1 | 362 | 590 | 126.31
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | GEN: OSW EGC 5 | Northport Bus Tie No.1-1 | 362 | 590 | 126.21
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | ASTORIA 345/138 PS | Northport Bus Tie No.1-1 | 362 | 590 | 125.49
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | SPRNBRK - ACDMY 345 M29 | Northport Bus Tie No.1-1 | 362 | 590 | 125.28
129341 NRTHPRT1 138 129355 PILGRIM 138 1 Max | [5 empty] | 192.02
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | SHORE RD 345/138 Bank #2 | 20 :SRD BUS1 | 465 | 599 | 252.22
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | SHORE RD 345/138 Bank #1 | 21 :SRD BUS2 | 465 | 599 | 250.45
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | SHORE RD 345/138 Bank #2 | Y50 | 465 | 599 | 243.91
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | 69-533 | Y50 | 465 | 599 | 243.49
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | 69-531 | Y50 | 465 | 599 | 243.34
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | 69-532 | Y50 | 465 | 599 | 243.29
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | BELMR 69/34.5 kV BK#5 | Y50 | 465 | 599 | 242.99
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | SHORE RD 345/138 Bank #2 | SHORE RD 345/138 Bank #1 | 465 | 599 | 242.9
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | GLNWD NO 138/69 Bank #5 | Y50 | 465 | 599 | 242.65
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | SHORE RD 345/138 Bank #1 | Y50 | 465 | 599 | 242.55
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | 138-564 | Y50 | 465 | 599 | 242.54
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | NB REA | Y50 | 465 | 599 | 241.53
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | NEWBRGE 138/69 Bank #6 | Y50 | 465 | 599 | 241.53
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | SHORE RD 345/138 Bank #1 | SHORE RD 345/138 Bank #2 | 465 | 599 | 241.49
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | SIN:350 Hellgate#4-Astoria E | Y50 | 465 | 599 | 241.38
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | SIN:340-Hellgate#1-Astoria E | Y50 | 465 | 599 | 241.3
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | BARRETT 138 kV P.A.R. | Y50 | 465 | 599 | 241.24
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | 138-461 | Y50 | 465 | 599 | 240.91
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | 138-459 | Y50 | 465 | 599 | 240.32
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | 138-368 | Y50 | 465 | 599 | 239.96
129344 NRTHPT1 138 129343 NRTHPT P 138 1 Max | [5 empty] | 252.22
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-679 | Northport Bus Tie No.1-1 | 179 | 295 | 241.8
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-679 | 74 :NPT BUS2 | 179 | 295 | 142.07
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | SHORE RD 345/138 Bank #1 | Northport Bus Tie No.1-1 | 179 | 295 | 104.95
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | SHORE RD 345/138 Bank #2 | Northport Bus Tie No.1-1 | 179 | 295 | 104.63
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | GEN: OSW Northport 4 | Base Case | 179 | 295 | 101.06
129344 NRTHPT1 138 129355 PILGRIM 138 3 Max | [5 empty] | 241.8
129346 NRTHPT3 138 129355 PILGRIM 138 2 | 11 | 138-672 | Northport Bus Tie No.1-1 | 367 | 594 | 123.27
129346 NRTHPT3 138 129355 PILGRIM 138 2 Max | [5 empty] | 123.27
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | 138-882 | PILGRIM 138/69 Bank #4 | 300 | 375 | 140.02
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | 138-882 | 68 : PIL BUS2 | 300 | 375 | 140.02
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | PILGRIM 138/69 Bank #4 | 300 | 375 | 140.02
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 68 : PIL BUS2 | 300 | 375 | 140.02
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | 138-882 | 138-881 NEW | 300 | 375 | 138.05
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-881 NEW | 300 | 375 | 138.05
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-881 | 300 | 375 | 136.52
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | 138-882 | 138-881 | 300 | 375 | 136.52
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | PILGRIM 138/69 Bank #4 | HOLBROOK 138/69 Bank #2 | 300 | 375 | 105.82
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | PILGRIM 138/69 Bank #4 | 108:HOL BUS2 | 300 | 375 | 105.82
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | PILGRIM 138/69 Bank #4 | 138-882 | 300 | 375 | 105.82
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | PILGRIM 138/69 Bank #4 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 300 | 375 | 104.7
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | PILGRIM 138/69 Bank #4 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 300 | 375 | 102.64
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | 138-881 NEW | HOLBROOK 138/69 Bank #2 | 300 | 375 | 102.54
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | 138-881 NEW | 138-882 | 300 | 375 | 102.54
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | 138-881 NEW | 108:HOL BUS2 | 300 | 375 | 102.54
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | PILGRIM 138/69 Bank #4 | GEN: OSW Holbrook 1 | 300 | 375 | 102.51
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | 138-881 NEW | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 300 | 375 | 102.5
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | 138-881 NEW | GEN: OSW Holbrook 1 | 300 | 375 | 102.38
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | 138-881 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 300 | 375 | 102.38
129356 PILGRM P 138 129355 PILGRIM 138 1 Max | [5 empty] | 140.02
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 NEW | 138-875 | 529 | 591 | 123.52
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | PILGRIM 138/69 Bank #4 | 138-875 | 529 | 591 | 123.37
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 NEW | 138-883 | 529 | 591 | 122.69
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | PILGRIM 138/69 Bank #4 | 138-883 | 529 | 591 | 122.49
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 | 138-875 | 529 | 591 | 122.47
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 | 138-883 | 529 | 591 | 121.65
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 NEW | C.ISLIP 138/69 Bank #3 | 529 | 591 | 119.36
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 NEW | 86 :CISL BUS3 | 529 | 591 | 119.36
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 138-881 NEW | 529 | 591 | 119.21
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 68 : PIL BUS2 | 529 | 591 | 118.94
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | C.ISLIP 138/69 Bank #3 | PILGRIM 138/69 Bank #4 | 529 | 591 | 118.94
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | PILGRIM 138/69 Bank #4 | 86 :CISL BUS3 | 529 | 591 | 118.84
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | PILGRIM 138/69 Bank #4 | C.ISLIP 138/69 Bank #3 | 529 | 591 | 118.84
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 | C.ISLIP 138/69 Bank #3 | 529 | 591 | 118.35
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 | 86 :CISL BUS3 | 529 | 591 | 118.35
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 138-881 | 529 | 591 | 118.2
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-875 | 138-881 NEW | 529 | 591 | 114.31
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-883 | 138-881 NEW | 529 | 591 | 113.62
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-875 | 138-881 | 529 | 591 | 113.31
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-875 | 68 : PIL BUS2 | 529 | 591 | 113.12
129361 RULND RD 138 129421 HOLBROOK 138 1 Max | [5 empty] | 123.52
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 138-882 | 138-881 NEW | 440 | 591 | 125.34
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-881 NEW | 440 | 591 | 125.34
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | HOLBROOK 138/69 Bank #2 | PILGRIM 138/69 Bank #4 | 440 | 591 | 124.98
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 138-882 | PILGRIM 138/69 Bank #4 | 440 | 591 | 124.98
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 138-882 | 68 : PIL BUS2 | 440 | 591 | 124.98
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 68 : PIL BUS2 | 440 | 591 | 124.98
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 138-882 | 138-881 | 440 | 591 | 124.19
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-881 | 440 | 591 | 124.19
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | PILGRIM 138/69 Bank #4 | 108:HOL BUS2 | 440 | 591 | 114.02
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | PILGRIM 138/69 Bank #4 | 138-882 | 440 | 591 | 114.02
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | PILGRIM 138/69 Bank #4 | HOLBROOK 138/69 Bank #2 | 440 | 591 | 114.02
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 138-881 NEW | 108:HOL BUS2 | 440 | 591 | 113.99
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 138-881 NEW | 138-882 | 440 | 591 | 113.99
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 138-881 NEW | HOLBROOK 138/69 Bank #2 | 440 | 591 | 113.99
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 138-881 | 138-882 | 440 | 591 | 113.06
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 138-881 | HOLBROOK 138/69 Bank #2 | 440 | 591 | 113.06
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 138-881 | 108:HOL BUS2 | 440 | 591 | 113.06
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | PILGRIM 138/69 Bank #4 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 440 | 591 | 112.67
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 138-881 NEW | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 440 | 591 | 112.59
129393 C.ISLIP 138 129454 RONKONK 138 1 | 11 | 138-881 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 440 | 591 | 111.67
129393 C.ISLIP 138 129454 RONKONK 138 1 Max | [5 empty] | 125.34
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-875 | 577 | 618 | 127.4
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-882 | 138-875 | 577 | 618 | 127.4
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-883 | 577 | 618 | 126.46
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-882 | 138-883 | 577 | 618 | 126.46
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 108:HOL BUS2 | 577 | 618 | 125.12
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | HOLBROOK 138/69 Bank #2 | 577 | 618 | 125.12
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 138-882 | 577 | 618 | 125.12
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | C.ISLIP 138/69 Bank #3 | 577 | 618 | 124.67
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 86 :CISL BUS3 | 577 | 618 | 124.67
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-882 | C.ISLIP 138/69 Bank #3 | 577 | 618 | 124.67
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-882 | 86 :CISL BUS3 | 577 | 618 | 124.67
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 577 | 618 | 123.71
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-875 | 138-882 | 577 | 618 | 120.47
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-875 | HOLBROOK 138/69 Bank #2 | 577 | 618 | 120.47
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-875 | 108:HOL BUS2 | 577 | 618 | 120.47
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-883 | 138-882 | 577 | 618 | 119.66
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-883 | 108:HOL BUS2 | 577 | 618 | 119.66
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-883 | HOLBROOK 138/69 Bank #2 | 577 | 618 | 119.66
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-875 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 577 | 618 | 118.8
129421 HOLBROOK 138 129428 WEST BUS 138 1 | 11 | 138-883 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 577 | 618 | 118
129421 HOLBROOK 138 129428 WEST BUS 138 1 Max | [5 empty] | 127.4
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-881 NEW | 572 | 617 | 121.32
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 138-882 | 138-881 NEW | 572 | 617 | 121.32
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 138-882 | 68 : PIL BUS2 | 572 | 617 | 120.96
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 68 : PIL BUS2 | 572 | 617 | 120.96
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | HOLBROOK 138/69 Bank #2 | PILGRIM 138/69 Bank #4 | 572 | 617 | 120.96
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 138-882 | PILGRIM 138/69 Bank #4 | 572 | 617 | 120.96
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 138-881 | 572 | 617 | 120.21
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 138-882 | 138-881 | 572 | 617 | 120.21
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | PILGRIM 138/69 Bank #4 | 108:HOL BUS2 | 572 | 617 | 110.46
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | PILGRIM 138/69 Bank #4 | HOLBROOK 138/69 Bank #2 | 572 | 617 | 110.46
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | PILGRIM 138/69 Bank #4 | 138-882 | 572 | 617 | 110.46
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 138-881 NEW | 138-882 | 572 | 617 | 110.42
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 138-881 NEW | HOLBROOK 138/69 Bank #2 | 572 | 617 | 110.42
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 138-881 NEW | 108:HOL BUS2 | 572 | 617 | 110.42
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 138-881 | HOLBROOK 138/69 Bank #2 | 572 | 617 | 109.53
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 138-881 | 108:HOL BUS2 | 572 | 617 | 109.53
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 138-881 | 138-882 | 572 | 617 | 109.53
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | PILGRIM 138/69 Bank #4 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 572 | 617 | 109.17
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 138-881 NEW | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 572 | 617 | 109.08
129421 HOLBROOK 138 129454 RONKONK 138 1 | 11 | 138-881 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 572 | 617 | 108.2
129421 HOLBROOK 138 129454 RONKONK 138 1 Max | [5 empty] | 121.32

## NConv_SLL_Alt
AnalysisType | Areas | First Level Contingency | Second Level Contingency
N-1-1 | 11 | GEN:CAITH | 11 :BRT BUS1
N-1-1 | 9 | GEN:CAITH | P5_SHORERD_138
N-1-1 | 9/11 | GEN:CAITH | P5_BARRETT_138_R
N-1-1 | 7 | GEN:CAITH | P5_EGC_138_M
N-1-1 | 11 | GEN: OSW Gowanus 1 | 128824 EGC DUM 345 128830 HMP HRBR 345 1
N-1-1 | 11 | GEN: OSW Gowanus 1 | 128824 EGC DUM 345 128825 EGC PAR 345 1
N-1-1 | 9 | GEN: OSW Gowanus 1 | Y50
N-1-1 | 9 | GEN: OSW Gowanus 1 | DNWDIE - SHORERD 345 Y50
N-1-1 | 9 | GEN: OSW Gowanus 1 | SB:DUNW345_6
N-1-1 | 9 | GEN: OSW Gowanus 1 | SB:DUNW345_4
N-1-1 | 9 | GEN: OSW Gowanus 1 | T:W89&W90_UC20
N-1-1 | 9 | GEN: OSW Astoria 2 | 139:EGC-CP2C
N-1-1 | 9 | GEN: OSW Astoria 2 | 140:CP-ROS2C
N-1-1 | 9 | GEN: OSW Astoria 2 | 141:ROS-GL2C
N-1-1 | 11 | Northport-Norwalk NNC-3C | 20 :SRD BUS1
N-1-1 | 11 | Northport-Norwalk NNC-3C | 21 :SRD BUS2
N-1-1 | 11 | Northport-Norwalk NNC-3C | 8 :VST BUS1
N-1-1 | 11 | Northport-Norwalk NNC-3C | VLY STRM 138/69 kV Bank #5
N-1-1 | 11 | Northport-Norwalk NNC-3C | VLY STRM 138 kV P.A.R.
N-1-1 | 11 | Northport-Norwalk NNC-3C | 901 L&M
N-1-1 | 11 | Northport-Norwalk NNC-3C | JAMCA - VLLYSTRM 901L&M 138
N-1-1 | 11 | Northport-Norwalk NNC-3C | SHORE RD 345/138 Bank #1
N-1-1 | 9 | Northport-Norwalk NNC-3C | 17 :SRD1370
N-1-1 | 9 | Northport-Norwalk NNC-3C | 18 :SRD1380
N-1-1 | 9/11 | Northport-Norwalk NNC-3C | P5_VALLEYSTREAM_138_M
N-1-1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | NNC-3C
N-1-1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Northport-Norwalk NNC-3C
N-1-1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | 72 :NPT BUS1-2
N-1-1 | 9/11 | JAMCA - VLLYSTRM 901L&M 138 | 74 :NPT 1410
N-1-1 | 9/11 | JAMCA - VLLYSTRM 901L&M 138 | 67 :NPT 1300
N-1-1 | 11 | 138-291 | Barrett Bus Tie
N-1-1 | 11 | 138-291 | 12 :BRT BUS2
N-1-1 | 9/11 | 138-291 | 9 :BRT 1380
N-1-1 | 11 | 138-362 | 35 :GLNSO BUS
N-1-1 | 11 | 138-362 | 138-365
N-1-1 | 9 | 138-362 | 30 :GLN1320
N-1-1 | 9 | 138-883 | 136:HOL-RU2C
N-1-1 | 9 | 69-965 | 370:EH-BUE2C
N-1-1 | 9 | 69-965 | 350:BLL 210
N-1-1 | 9 | 69-965 | 346:BLLBUS1
N-1-1 | 9 | 69-970 | 369:BRH-EH2C
N-1 | 11 | 11 :BRT BUS1
N-1 | 11 | P5_BARRETT_138_R
N-1 | 11 | P5_EGC_138_M
N-1 | 9 | P5_SHORERD_138
N-1 | 9 | Y50
N-1 | 9 | DNWDIE - SHORERD 345 Y50
N-1 | 9 | SB:DUNW345_6
N-1 | 9 | SB:DUNW345_4
N-1 | 11 | T:W89&W90_UC20

## N-1_SUM_Base
Monitored Facility | Areas | Cont Name | Rate Base (MVA) | Rate Cont (MVA) | SCD AC %Loading
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | P5_EGC_138_M | 273 | 365 | 102.15
126455 JAMAICA 138 129235 V STRM P 138 1 Max |  |  |  |  | 102.15
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 | 10 | FARRAGUTW 345/138 4TR | 128 | 136 | 147.42
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 | 10 | SB:FARR345_2W | 128 | 136 | 147.41
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 | 10 | SB:FARR345_1W | 128 | 136 | 147.18
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 | 10 | SB:FARR345_1E | 128 | 136 | 146.27
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 | 10 | FARRAGUTE 345/138 3TR | 128 | 136 | 146.16
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 | 10 | SB:FARR345_2E | 128 | 136 | 146.16
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 Max |  |  |  |  | 147.42
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 38 :NBR 1320 | 452 | 563 | 119.4
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.37
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 49 :NBR 1430 | 452 | 563 | 119.37
128847 NWBRG 345 129310 NEWBRGE 138 1 Max |  |  |  |  | 119.4
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | P5_EGC_138_M | 462 | 563 | 119.39
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.38
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 39 :NBR 1330 | 462 | 563 | 119.38
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 50 :NBR 1440 | 462 | 563 | 119.36
128847 NWBRG 345 129310 NEWBRGE 138 2 Max |  |  |  |  | 119.39
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Barrett Bus Tie | 201 | 296 | 360.51
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 12 :BRT BUS2 | 201 | 296 | 352.91
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 9 :BRT 1380 | 201 | 296 | 349.45
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 5 :VST NEW1 | 201 | 296 | 255.79
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-292 | 201 | 296 | 255.78
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Base Case | 201 | 296 | 193.4
129202 BARRETT1 138 129233 VLY STRM 138 1 Max |  |  |  |  | 360.51
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | P5_VALLEYSTREAM_138_M | 187 | 275 | 299.83
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | Base Case | 187 | 275 | 102.79
129203 BARRETT2 138 129204 BRRT PH 138 1 Max |  |  |  |  | 299.83
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 196 | 294 | 261.35
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 8 :VST BUS1 | 196 | 294 | 250.95
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 196 | 294 | 250.29
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | Base Case | 196 | 294 | 218.48
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | 196 | 294 | 178.59
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | 196 | 294 | 178.5
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 14 :FRP 1350 | 196 | 294 | 178.41
129203 BARRETT2 138 129234 VLY STRM2 138 2 Max |  |  |  |  | 261.35
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | P5_VALLEYSTREAM_138_M | 187 | 275 | 294.03
129204 BRRT PH 138 129276 FREEPORT 138 1 Max |  |  |  |  | 294.03
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 117 | 146 | 187.24
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 | 11 | 12 :BRT BUS2 | 117 | 146 | 126.97
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 | 11 | P5_RULANDRD_138_M | 117 | 146 | 124.15
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 | 11 | Base Case | 117 | 146 | 116.75
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 Max |  |  |  |  | 187.24
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | P5_EGC_138_M | 274 | 366 | 102.96
129233 VLY STRM 138 129235 V STRM P 138 1 Max |  |  |  |  | 102.96
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | NEW_VS1430 | 214 | 298 | 124.28
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 12 :BRT BUS2 | 214 | 298 | 111.47
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 9 :BRT 1380 | 214 | 298 | 110.16
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | BARRETT 138 kV P.A.R. | 214 | 298 | 103.59
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-459 | 214 | 298 | 103.21
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 214 | 298 | 103.18
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 Max |  |  |  |  | 124.28
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 24 :EGC 1360 | 263 | 303 | 101.9
129265 CARLE PL 138 129270 E.G.C. 138 1 Max |  |  |  |  | 101.9
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | P5_VALLEYSTREAM_138_M | 235 | 305 | 247.33
129276 FREEPORT 138 129310 NEWBRGE 138 1 Max |  |  |  |  | 247.33
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 | 11 | P5_EGC_138_M | 120 | 148 | 109.89
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 109.89
129421 HOLBROOK 138 129807 HOLBRK2 69.0 2 | 11 | 98 :HOL 1370 | 104 | 128 | 111.1
129421 HOLBROOK 138 129807 HOLBRK2 69.0 2 | 11 | 97 :HOL 1360 | 104 | 128 | 108.33
129421 HOLBROOK 138 129807 HOLBRK2 69.0 2 | 11 | 138-888 | 104 | 128 | 104.46
129421 HOLBROOK 138 129807 HOLBRK2 69.0 2 | 11 | 107:HOL BUS1 | 104 | 128 | 104.46
129421 HOLBROOK 138 129807 HOLBRK2 69.0 2 | 11 | HOLBROOK 138/69 Bank #1 | 104 | 128 | 104.46
129421 HOLBROOK 138 129807 HOLBRK2 69.0 2 Max |  |  |  |  | 111.1
129501 BARRETT 69.0 129572 BALDWIN1 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 104 | 155 | 148.16
129501 BARRETT 69.0 129572 BALDWIN1 69.0 1 | 11 | P5_RULANDRD_138_M | 104 | 155 | 104.59
129501 BARRETT 69.0 129572 BALDWIN1 69.0 1 | 11 | Base Case | 104 | 155 | 101.62
129501 BARRETT 69.0 129572 BALDWIN1 69.0 1 Max |  |  |  |  | 148.16
129528 VLYSTRM2 69.0 129592 LAKEVIEW 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 47 | 59 | 168.7
129528 VLYSTRM2 69.0 129592 LAKEVIEW 69.0 1 Max |  |  |  |  | 168.7
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 69 | 87 | 113.6
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 Max |  |  |  |  | 113.6
129546 MALVERN 69.0 129561 W.HEMP 1 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 47 | 59 | 163.23
129546 MALVERN 69.0 129561 W.HEMP 1 69.0 1 Max |  |  |  |  | 163.23
129562 W.HEMP 2 69.0 129592 LAKEVIEW 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 47 | 59 | 171.71
129562 W.HEMP 2 69.0 129592 LAKEVIEW 69.0 1 Max |  |  |  |  | 171.71
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 69 | 87 | 108.68
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 Max |  |  |  |  | 108.68
129572 BALDWIN1 69.0 129617 BELMR 1 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 104 | 155 | 114.48
129572 BALDWIN1 69.0 129617 BELMR 1 69.0 1 Max |  |  |  |  | 114.48
129580 E.G.C.1 69.0 129593 HEMPSTEAD 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 138 | 138 | 105.32
129580 E.G.C.1 69.0 129593 HEMPSTEAD 69.0 1 Max |  |  |  |  | 105.32
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | 44 :NBR 1380 | 55 | 67 | 109.34
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | NEWBRGE 138/69 Bank #6 | 55 | 67 | 108.5
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | 38 :NBR 1320 | 55 | 67 | 108.5
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | NB REA | 55 | 67 | 108.45
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | 43 :NBR BH BUS | 55 | 67 | 108.45
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | 42 :NBR 1360 | 55 | 67 | 107.81
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 Max |  |  |  |  | 109.34
129630 MASPEQUA2 69.0 129646 PLNEDGE 69.0 1 | 11 | 225:MS 660 | 62 | 74 | 109.64
129630 MASPEQUA2 69.0 129646 PLNEDGE 69.0 1 Max |  |  |  |  | 109.64
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 | 11 | P5_VALLEYSTREAM_138_M | 70 | 80 | 169.96
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 | 11 | 129202 BARRETT1 138 129205 BRTGT1-8 138 1 | 70 | 80 | 112.14
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 | 11 | 129205 BRTGT1-8 138 129501 BARRETT 69.0 1 | 70 | 80 | 105.67
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 | 11 | Barrett G1-8* | 70 | 80 | 105.67
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 | 11 | BRT69KV | 70 | 80 | 104.79
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 | 11 | 166:BRT6010 | 70 | 80 | 104.79
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 Max |  |  |  |  | 169.96

## N-1-1_SUM_Base
Monitored Facility | Areas | First Level Scenario | Cont Name | Rate Base (MVA) | Rate Cont (MVA) | SCD AC %Loading
126282 FRESH KILLS 345 126424 21192 T 138 1 | 10 | GOWANUS 345/138 2TR | FRSHKILLS 345/138 TA1 | 349 | 418 | 101.27
126282 FRESH KILLS 345 126424 21192 T 138 1 | 10 | GOWANUS 345/138 2TR | SB:FRES345_1 | 349 | 418 | 101.02
126282 FRESH KILLS 345 126424 21192 T 138 1 | 10 | GOWANUS 345/138 2TR | SB:FRES345_2 | 349 | 418 | 101.02
126282 FRESH KILLS 345 126424 21192 T 138 1 Max | [5 empty] | 101.27
126287 GOWANUS 345 126429 GOWNUST14 138 1 | 10 | GOETHALS-FOXHILLS PAR | Base Case | 271 | 335 | 101.26
126287 GOWANUS 345 126429 GOWNUST14 138 1 | 10 | FRSHKILLS 345/138 TB1 | SB:GOWANUS_2 | 271 | 335 | 101.15
126287 GOWANUS 345 126429 GOWNUST14 138 1 Max | [5 empty] | 101.26
126434 GRENWOOD N 138 126454 KENTTAP 138 1 | 10 | GOETHALS-FOXHILLS PAR | Base Case | 194 | 263 | 101.73
126434 GRENWOOD N 138 126454 KENTTAP 138 1 Max | [5 empty] | 101.73
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 901 L&M | GEN: OSW Astoria 2 | 252 | 345 | 112.62
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | JAMCA - VLLYSTRM 901L&M 138 | GEN: OSW Astoria 2 | 252 | 345 | 112.62
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | VLY STRM 138 kV P.A.R. | GEN: OSW Astoria 2 | 252 | 345 | 111.07
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | VLY STRM 138/69 kV Bank #5 | GEN: OSW Astoria 2 | 252 | 345 | 110.96
126455 JAMAICA 138 129249 L SUCSPH 138 1 Max | [5 empty] | 112.62
126506 VERNON-E 138 126646 GRENWOOD S 138 1 | 10 | GOWANUS 345/138 2TR | Base Case | 193 | 262 | 101.36
126506 VERNON-E 138 126646 GRENWOOD S 138 1 Max | [5 empty] | 101.36
126642 RAINEY WEST 345 999949 XFMR 8W 138 1 | 10 | GOETHALS-FOXHILLS PAR | GEN:POLETTIX | 273 | 336 | 101.02
126642 RAINEY WEST 345 999949 XFMR 8W 138 1 Max | [5 empty] | 101.02
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | NEWBRGE 345/138 Bank #2 | Base Case | 452 | 563 | 148.71
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | GEN:CAITH | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.25
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | GOWANUS 345/138 2TR | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.25
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | W49ST 345/138 1TR | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.25
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | Grmn B GT4* | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.25
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 138-868 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | WOLFH CAP | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | DER CAP | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 69-872 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 69-963 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 69-974 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | Canal DVAR | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | MAC CAP | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | SOUTH MAHWAY TR BANK-258 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | RAINEYW 345/138 7WTR | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | RAINEY 345/138 3WTR | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | RAINEYE - RAVENSWOOD 60M 345 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 138-877 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | GEN: BAYONNE | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | BAYONNE - GOWANUS G27 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 1 Max | [5 empty] | 148.71
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | NEWBRGE 345/138 Bank #1 | Base Case | 462 | 563 | 145.49
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 69-487 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | EFISHKILL - PLSNTVLLE F39/Y87 345 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | DUNWOODIE-PLEASANTVILLE W89/W73 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | Barrett G9-12* | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 69-570 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 69-475 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 69-372 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 69-265 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | PILG CAP1 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | MASPQ CAP | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | PILG CAP2 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-673 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 69-877 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.15
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | SIN:350 Hellgate#4-Astoria E | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.14
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | S:E13TH_45 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.14
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 69-532 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.14
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-674 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.14
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 69-533 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.14
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-678 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.14
128847 NWBRG 345 129310 NEWBRGE 138 2 Max | [5 empty] | 145.49
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Barrett G1-8* | Barrett Bus Tie | 201 | 296 | 409.73
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Barrett G1-8* | 12 :BRT BUS2 | 201 | 296 | 408.6
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-292 | Base Case | 201 | 296 | 402.54
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-359 | Barrett Bus Tie | 201 | 296 | 386.93
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-359 | 12 :BRT BUS2 | 201 | 296 | 376.2
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | BELMR 69/34.5 kV BK#5 | Barrett Bus Tie | 201 | 296 | 375.46
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-459 | Barrett Bus Tie | 201 | 296 | 375.35
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | BARRETT 69/34.5 kV BK#3 | Barrett Bus Tie | 201 | 296 | 364.86
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-459 | 12 :BRT BUS2 | 201 | 296 | 363.57
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | BELMR 69/34.5 kV BK#5 | 12 :BRT BUS2 | 201 | 296 | 363.4
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-559 | Barrett Bus Tie | 201 | 296 | 363.36
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-766 | Barrett Bus Tie | 201 | 296 | 363.31
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-565 | Barrett Bus Tie | 201 | 296 | 363.23
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-566 | Barrett Bus Tie | 201 | 296 | 363.18
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-574 | Barrett Bus Tie | 201 | 296 | 363.13
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-883 | Barrett Bus Tie | 201 | 296 | 363.11
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-752 | Barrett Bus Tie | 201 | 296 | 363.11
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-875 | Barrett Bus Tie | 201 | 296 | 362.96
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Y50 | Barrett Bus Tie | 201 | 296 | 362.93
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-267 | Barrett Bus Tie | 201 | 296 | 362.88
129202 BARRETT1 138 129233 VLY STRM 138 1 Max | [5 empty] | 409.73
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-291 | 138-292 | 187 | 275 | 305.21
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | 138-291 | 187 | 275 | 304.04
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 187 | 275 | 302.53
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | 8 :VST BUS1 | 187 | 275 | 302.1
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 187 | 275 | 302.07
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | Valley Stream Bus Tie | 187 | 275 | 146.38
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-261 | 138-262 | 187 | 275 | 121.03
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-262 | 138-261 | 187 | 275 | 118.07
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 69-459 | Base Case | 187 | 275 | 117.15
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-870 | Base Case | 187 | 275 | 117.12
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-869 | Base Case | 187 | 275 | 117.1
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | Northport Unit 3* | Base Case | 187 | 275 | 117.09
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | Northport Unit 4* | Base Case | 187 | 275 | 117.09
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN:NRTPTG4 | Base Case | 187 | 275 | 117.09
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN:NRTPTG3 | Base Case | 187 | 275 | 117.09
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | NEPTUNE - RAR NEPTUNE | Base Case | 187 | 275 | 117.08
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN:NRTPTG1 | Base Case | 187 | 275 | 117.07
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | Northport Unit 1* | Base Case | 187 | 275 | 117.07
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | Northport Unit 2* | Base Case | 187 | 275 | 117.05
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN:NRTPTG2 | Base Case | 187 | 275 | 117.05
129203 BARRETT2 138 129204 BRRT PH 138 1 Max | [5 empty] | 305.21
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | Base Case | 196 | 294 | 413.81
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | Base Case | 196 | 294 | 405.16
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | BARRETT 138 kV P.A.R. | 196 | 294 | 335.86
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 138-459 | 196 | 294 | 335.66
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 129204 BRRT PH 138 129276 FREEPORT 138 1 | 196 | 294 | 335.66
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | 138-291 | 196 | 294 | 335.64
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | 138-291 | 196 | 294 | 335.44
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | BARRETT 138 kV P.A.R. | 196 | 294 | 330.45
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 138-459 | 196 | 294 | 330.28
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 129204 BRRT PH 138 129276 FREEPORT 138 1 | 196 | 294 | 330.28
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | 8 :VST BUS1 | 196 | 294 | 329.58
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | 8 :VST BUS1 | 196 | 294 | 329.41
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | VLY STRM 138/69 kV Bank #5 | 196 | 294 | 329.41
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | VLY STRM 138/69 kV Bank #5 | 196 | 294 | 329.24
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 138-461 | 196 | 294 | 318.44
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-461 | 138-291 | 196 | 294 | 318.22
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 138-461 | 196 | 294 | 313.23
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 129202 BARRETT1 138 129205 BRTGT1-8 138 1 | 196 | 294 | 313.08
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-461 | 8 :VST BUS1 | 196 | 294 | 312.31
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-461 | VLY STRM 138/69 kV Bank #5 | 196 | 294 | 312.13
129203 BARRETT2 138 129234 VLY STRM2 138 2 Max | [5 empty] | 413.81
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-291 | 138-292 | 187 | 275 | 299.28
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | 138-291 | 187 | 275 | 298.14
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 187 | 275 | 296.66
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | 8 :VST BUS1 | 187 | 275 | 296.24
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 187 | 275 | 296.21
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | Valley Stream Bus Tie | 187 | 275 | 142.99
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-261 | 138-262 | 187 | 275 | 118.29
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-262 | 138-261 | 187 | 275 | 115.39
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 69-459 | Base Case | 187 | 275 | 114.7
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | NEPTUNE - RAR NEPTUNE | Base Case | 187 | 275 | 114.62
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-870 | Base Case | 187 | 275 | 114.6
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | Northport Unit 3* | Base Case | 187 | 275 | 114.59
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | Northport Unit 4* | Base Case | 187 | 275 | 114.59
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN:NRTPTG3 | Base Case | 187 | 275 | 114.59
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN:NRTPTG4 | Base Case | 187 | 275 | 114.59
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-869 | Base Case | 187 | 275 | 114.57
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | Northport Unit 1* | Base Case | 187 | 275 | 114.55
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN:NRTPTG1 | Base Case | 187 | 275 | 114.55
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN:NRTPTG2 | Base Case | 187 | 275 | 114.49
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | Northport Unit 2* | Base Case | 187 | 275 | 114.49
129204 BRRT PH 138 129276 FREEPORT 138 1 Max | [5 empty] | 299.28
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 12 :BRT BUS2 | 214 | 298 | 173.33
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-261 | 214 | 298 | 165.18
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | BARRETT 138 kV P.A.R. | 214 | 298 | 161.98
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 138-459 | 214 | 298 | 161.53
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 129204 BRRT PH 138 129276 FREEPORT 138 1 | 214 | 298 | 161.52
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | BARRETT 138 kV P.A.R. | 138-261 | 214 | 298 | 161.42
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-459 | 138-261 | 214 | 298 | 161.02
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | Base Case | 214 | 298 | 158.93
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | VLY STRM 138/69 kV Bank #5 | 214 | 298 | 153.9
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Base Case | 214 | 298 | 152.96
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 8 :VST BUS1 | 214 | 298 | 150.15
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | BARRETT 138 kV P.A.R. | Base Case | 214 | 298 | 148.88
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-459 | Base Case | 214 | 298 | 148.43
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 138-461 | 214 | 298 | 147.64
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | VLY STRM 138/69 Bank #6 | 214 | 298 | 147.42
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | VSBUS2 | 214 | 298 | 146.46
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-461 | 138-261 | 214 | 298 | 145.98
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | BARRETT 138 kV P.A.R. | 214 | 298 | 144.42
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-459 | 214 | 298 | 144.19
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 129204 BRRT PH 138 129276 FREEPORT 138 1 | 214 | 298 | 144.19
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 Max | [5 empty] | 173.33
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | Base Case | 280 | 442 | 112.4
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 12 :BRT BUS2 | 280 | 442 | 106.4
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 Max | [5 empty] | 112.4
129247 L SUCS 138 129293 SHORE RD 138 1 | 11 | 138-368 | Base Case | 249 | 430 | 127.74
129247 L SUCS 138 129293 SHORE RD 138 1 Max | [5 empty] | 127.74
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 901 L&M | GEN: OSW Astoria 2 | 253 | 346 | 109.91
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | GEN: OSW Astoria 2 | 253 | 346 | 109.91
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | VLY STRM 138 kV P.A.R. | GEN: OSW Astoria 2 | 253 | 346 | 109.38
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | GEN: OSW Astoria 2 | 253 | 346 | 109.16
129248 L SUCS2 138 129249 L SUCSPH 138 1 Max | [5 empty] | 109.91
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | 138-367 | Base Case | 249 | 430 | 127.81
129248 L SUCS2 138 129294 SHORE RD2 138 2 | 11 | LKE SCSS 138/69 Bank #5 | Base Case | 249 | 430 | 114.01
129248 L SUCS2 138 129294 SHORE RD2 138 2 Max | [5 empty] | 127.81
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 138-362 | 263 | 303 | 169.84
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 37 :GLNGT BUS | 263 | 303 | 164.25
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 138-364 | 263 | 303 | 164.25
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 263 | 303 | 164.25
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 138-366 | 263 | 303 | 162.5
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 36 :GLNNO BUS | 263 | 303 | 162.5
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 263 | 303 | 155.94
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 20 :SRD BUS1 | 263 | 303 | 147.54
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | Base Case | 263 | 303 | 140.26
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | VLY STRM 138/69 kV Bank #5 | 263 | 303 | 138.5
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 8 :VST BUS1 | 263 | 303 | 137.01
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | VLY STRM 138 kV P.A.R. | 263 | 303 | 131.71
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | JAMCA - VLLYSTRM 901L&M 138 | 263 | 303 | 131.69
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 901 L&M | 263 | 303 | 131.69
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | NEWBUS2 | 263 | 303 | 130.65
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | E.G.C. 138/69 Bank #1 | 263 | 303 | 128.42
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | EGCBUS1 | 263 | 303 | 128.39
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | VSBUS2 | 263 | 303 | 126.53
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | VLY STRM 138/69 Bank #6 | 263 | 303 | 126.19
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | SS BUS2 | 263 | 303 | 126.01
129265 CARLE PL 138 129270 E.G.C. 138 1 Max | [5 empty] | 169.84
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 138-362 | 264 | 324 | 141.42
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 37 :GLNGT BUS | 264 | 324 | 136.27
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 138-364 | 264 | 324 | 136.27
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 264 | 324 | 136.27
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 36 :GLNNO BUS | 264 | 324 | 134.57
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 138-366 | 264 | 324 | 134.57
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 264 | 324 | 128.44
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 20 :SRD BUS1 | 264 | 324 | 120.44
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | Base Case | 264 | 324 | 118.46
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | VLY STRM 138/69 kV Bank #5 | 264 | 324 | 112.07
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 8 :VST BUS1 | 264 | 324 | 110.69
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | VLY STRM 138 kV P.A.R. | 264 | 324 | 105.78
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 901 L&M | 264 | 324 | 105.7
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | JAMCA - VLLYSTRM 901L&M 138 | 264 | 324 | 105.7
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | NEWBUS2 | 264 | 324 | 104.8
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | E.G.C. 138/69 Bank #1 | 264 | 324 | 102.66
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | EGCBUS1 | 264 | 324 | 102.62
129265 CARLE PL 138 129283 GLNWD SO 138 1 Max | [5 empty] | 141.42
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-361 | 263 | 303 | 162.91
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-363 | 263 | 303 | 154.99
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 35 :GLNSO BUS | 263 | 303 | 153.45
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-365 | 263 | 303 | 153.45
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 263 | 303 | 146.93
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 21 :SRD BUS2 | 263 | 303 | 139.32
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | Base Case | 263 | 303 | 127.65
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | VLY STRM 138/69 kV Bank #5 | 263 | 303 | 127.13
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 8 :VST BUS1 | 263 | 303 | 125.68
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | VLY STRM 138 kV P.A.R. | 263 | 303 | 120.52
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | JAMCA - VLLYSTRM 901L&M 138 | 263 | 303 | 120.48
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 901 L&M | 263 | 303 | 120.48
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | NEWBUS2 | 263 | 303 | 119.51
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-361 | Y49 | 263 | 303 | 117.5
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | E.G.C. 138/69 Bank #1 | 263 | 303 | 117.3
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | EGCBUS1 | 263 | 303 | 117.27
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y50 | 138-361 | 263 | 303 | 116.95
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | VSBUS2 | 263 | 303 | 115.46
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | VLY STRM 138/69 Bank #6 | 263 | 303 | 115.13
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | SS BUS2 | 263 | 303 | 114.96
129270 E.G.C. 138 129288 ROSLYN 138 1 Max | [5 empty] | 162.91
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 207 | 287 | 126.52
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-291 | 138-292 | 207 | 287 | 125.92
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 138-291 | 207 | 287 | 125.6
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 8 :VST BUS1 | 207 | 287 | 123.06
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 207 | 287 | 122.78
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | 138-463 | 207 | 287 | 122.44
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-463 | 138-465 | 207 | 287 | 121.29
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | Base Case | 207 | 287 | 114.17
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-463 | Base Case | 207 | 287 | 112.51
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-463 | 138-467 | 207 | 287 | 106.88
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | 138-467 | 207 | 287 | 106.64
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-467 | 138-463 | 207 | 287 | 106.17
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-467 | 138-465 | 207 | 287 | 105.02
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-467 | Base Case | 207 | 287 | 102.13
129270 E.G.C. 138 129310 NEWBRGE 138 1 Max | [5 empty] | 126.52
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 201 | 295 | 118.56
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-291 | 138-292 | 201 | 295 | 117.82
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-292 | 138-291 | 201 | 295 | 117.51
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | 138-463 | 201 | 295 | 115.62
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-292 | 8 :VST BUS1 | 201 | 295 | 115.21
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | Base Case | 201 | 295 | 115.04
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 201 | 295 | 114.94
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-463 | 138-462 | 201 | 295 | 114.12
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-463 | Base Case | 201 | 295 | 111.57
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | 138-467 | 201 | 295 | 102.91
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-467 | Base Case | 201 | 295 | 101.91
129270 E.G.C. 138 129310 NEWBRGE 138 3 Max | [5 empty] | 118.56
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | Base Case | 174 | 293 | 132.56
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-465 | Base Case | 174 | 293 | 130.4
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 174 | 293 | 123.42
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-291 | 138-292 | 174 | 293 | 122.79
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-292 | 138-291 | 174 | 293 | 122.41
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-292 | 8 :VST BUS1 | 174 | 293 | 119.45
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 174 | 293 | 119.11
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | 138-465 | 174 | 293 | 118.97
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-465 | 138-462 | 174 | 293 | 118.54
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-467 | Base Case | 174 | 293 | 117.96
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | NB REA | Base Case | 174 | 293 | 111.38
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | NEWBRGE 138/69 Bank #6 | Base Case | 174 | 293 | 110.47
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GEN: OSW Farragut 3 | Base Case | 174 | 293 | 109.59
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GEN: OSW Farragut 4 | Base Case | 174 | 293 | 109.59
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GEN: OSW W49 Street 5 | Base Case | 174 | 293 | 109.58
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | HVDC: HQ Rainey 7 | Base Case | 174 | 293 | 109.56
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GEN: OSW Astoria 2 | Base Case | 174 | 293 | 108.92
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 69-533 | Base Case | 174 | 293 | 106.56
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GEN: OSW Gowanus 1 | Base Case | 174 | 293 | 106.31
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | BELMR 69/34.5 kV BK#6 | Base Case | 174 | 293 | 105.39
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 Max | [5 empty] | 132.56
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-291 | 138-292 | 235 | 305 | 252.06
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 138-291 | 235 | 305 | 251.03
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 235 | 305 | 249.68
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 8 :VST BUS1 | 235 | 305 | 249.31
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 235 | 305 | 249.28
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | Valley Stream Bus Tie | 235 | 305 | 111.21
129276 FREEPORT 138 129310 NEWBRGE 138 1 Max | [5 empty] | 252.06
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 138-361 | 264 | 324 | 140.37
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 138-363 | 264 | 324 | 133.03
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 138-365 | 264 | 324 | 131.54
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 35 :GLNSO BUS | 264 | 324 | 131.54
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 264 | 324 | 125.44
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 21 :SRD BUS2 | 264 | 324 | 118.2
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | Base Case | 264 | 324 | 112.51
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | VLY STRM 138/69 kV Bank #5 | 264 | 324 | 106.88
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 8 :VST BUS1 | 264 | 324 | 105.53
129281 GLNWD GT 138 129282 GLNWD NO 138 1 Max | [5 empty] | 140.37
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-361 | 264 | 324 | 140.39
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-363 | 264 | 324 | 133.06
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 138-365 | 264 | 324 | 131.57
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 35 :GLNSO BUS | 264 | 324 | 131.57
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 264 | 324 | 125.46
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 21 :SRD BUS2 | 264 | 324 | 118.22
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | Base Case | 264 | 324 | 112.54
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | VLY STRM 138/69 kV Bank #5 | 264 | 324 | 106.9
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 8 :VST BUS1 | 264 | 324 | 105.55
129281 GLNWD GT 138 129288 ROSLYN 138 1 Max | [5 empty] | 140.39
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 138-361 | 285 | 366 | 117.31
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 138-363 | 285 | 366 | 110.07
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 35 :GLNSO BUS | 285 | 366 | 107.26
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 138-365 | 285 | 366 | 107.26
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 285 | 366 | 106.93
129282 GLNWD NO 138 129293 SHORE RD 138 1 Max | [5 empty] | 117.31
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 138-362 | 264 | 324 | 133.3
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 37 :GLNGT BUS | 264 | 324 | 127.58
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 264 | 324 | 127.58
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 138-364 | 264 | 324 | 127.58
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 138-366 | 264 | 324 | 124.15
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 36 :GLNNO BUS | 264 | 324 | 124.15
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 264 | 324 | 123.57
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 20 :SRD BUS1 | 264 | 324 | 114.04
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | Base Case | 264 | 324 | 103.29
129283 GLNWD SO 138 129294 SHORE RD2 138 1 Max | [5 empty] | 133.3

## NConv_SUM_Base
AnalysisType | Areas | First Level Contingency | Second Level Contingency
N-1-1 | 11 | GEN:CAITH | 11 :BRT BUS1
N-1-1 | 11 | 138-291 | 12 :BRT BUS2
N-1-1 | 11 | 138-291 | Barrett Bus Tie
N-1 | 11 | 11 :BRT BUS1
N-1 | 11 | P5_BARRETT_138_R

## N-1_SUM_Alt
Monitored Facility | Areas | Cont Name | Rate Base (MVA) | Rate Cont (MVA) | SCD AC %Loading
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | SB:FISH345_6 | 31 | 31 | 131.39
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | P5_EGC_138_M | 31 | 31 | 131.2
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | SB:FISH345_11 | 31 | 31 | 129.65
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | PV 345/115 TBS1 | 31 | 31 | 129.61
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | EFISHKILL 345/115 1TR | 31 | 31 | 129.35
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 | 101 | Base Case | 31 | 31 | 113.16
120380 SALISBURY 69.0 120389 NE_690_NY 69.0 1 Max |  |  |  |  | 131.39
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Y49 | 690 | 963 | 152.98
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Base Case | 690 | 963 | 111.96
126266 DUNWOODIE 345 128835 SHORE RD 345 1 Max |  |  |  |  | 152.98
126274 E13ST 47 345 126870 E13 TX17 T 69.0 17 | 10 | GEN:ERG7 | 249 | 282 | 103.64
126274 E13ST 47 345 126870 E13 TX17 T 69.0 17 | 10 | GEN:ERG6 | 249 | 282 | 103.22
126274 E13ST 47 345 126870 E13 TX17 T 69.0 17 Max |  |  |  |  | 103.64
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | P5_SHORERD_138 | 1243 | 1386 | 128.78
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | 139:EGC-CP2C | 1243 | 1386 | 122.92
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | 140:CP-ROS2C | 1243 | 1386 | 121.73
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | 141:ROS-GL2C | 1243 | 1386 | 120.8
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 1243 | 1386 | 120.69
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | Base Case | 1243 | 1386 | 107.77
126298 SPRAINBROOK 345 126299 REACBUS 345 BY Max |  |  |  |  | 128.78
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | Base Case | 708 | 948 | 190.83
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | P5_SHORERD_138 | 708 | 948 | 189.68
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 139:EGC-CP2C | 708 | 948 | 181.11
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 140:CP-ROS2C | 708 | 948 | 179.37
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 141:ROS-GL2C | 708 | 948 | 178.03
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | DNWDIE - SHORERD 345 Y50 | 708 | 948 | 177.59
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | Y50 | 708 | 948 | 177.59
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | SB:DUNW345_4 | 708 | 948 | 176.84
126299 REACBUS 345 147857 DVNPT NK 345 1 Max |  |  |  |  | 190.83
126317 38M72 TAP 138 126551 ASTOR T5 TAP 138 1 | 10 | Base Case | 175 | 260 | 101.69
126317 38M72 TAP 138 126551 ASTOR T5 TAP 138 1 Max |  |  |  |  | 101.69
126442 HG 1 138 126647 E179 ST E 138 1 | 10 | Base Case | 183 | 329 | 101.13
126442 HG 1 138 126647 E179 ST E 138 1 Max |  |  |  |  | 101.13
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | P5_EGC_138_M | 273 | 365 | 164.99
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Y49 | 273 | 365 | 121.45
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 139:EGC-CP2C | 273 | 365 | 102.92
126455 JAMAICA 138 129235 V STRM P 138 1 Max |  |  |  |  | 164.99
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | Y50 | 252 | 345 | 126.67
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | T:W89&W90_UC20 | 252 | 345 | 126.67
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | DNWDIE - SHORERD 345 Y50 | 252 | 345 | 126.67
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | SB:DUNW345_4 | 252 | 345 | 126.36
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | SB:DUNW345_6 | 252 | 345 | 126.28
126455 JAMAICA 138 129249 L SUCSPH 138 1 Max |  |  |  |  | 126.67
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 | 10 | SB:FARR345_2W | 128 | 136 | 147.29
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 | 10 | FARRAGUTW 345/138 4TR | 128 | 136 | 147.29
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 | 10 | SB:FARR345_1W | 128 | 136 | 147.26
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 | 10 | SB:FARR345_1E | 128 | 136 | 146.4
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 | 10 | SB:FARR345_2E | 128 | 136 | 146.26
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 | 10 | FARRAGUTE 345/138 3TR | 128 | 136 | 146.04
126645 FARRAGUT EAS 345 126412 FGT_X5 138 1 Max |  |  |  |  | 147.29
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Base Case | 707 | 948 | 197.5
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | P5_SHORERD_138 | 707 | 948 | 194.36
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 139:EGC-CP2C | 707 | 948 | 185.88
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 140:CP-ROS2C | 707 | 948 | 184.22
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 141:ROS-GL2C | 707 | 948 | 182.92
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 707 | 948 | 181.49
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | Y50 | 707 | 948 | 181.49
128824 EGC DUM 345 128825 EGC PAR 345 1 Max |  |  |  |  | 197.5
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | Base Case | 707 | 948 | 204.46
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | P5_SHORERD_138 | 707 | 948 | 198.85
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 139:EGC-CP2C | 707 | 948 | 190.55
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 140:CP-ROS2C | 707 | 948 | 188.96
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 141:ROS-GL2C | 707 | 948 | 187.72
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | Y50 | 707 | 948 | 185.48
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 707 | 948 | 185.48
128824 EGC DUM 345 128830 HMP HRBR 345 1 Max |  |  |  |  | 204.46
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | Base Case | 708 | 948 | 201.11
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | P5_SHORERD_138 | 708 | 948 | 196.94
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 139:EGC-CP2C | 708 | 948 | 188.55
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 140:CP-ROS2C | 708 | 948 | 186.93
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 141:ROS-GL2C | 708 | 948 | 185.67
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | Y50 | 708 | 948 | 183.76
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | DNWDIE - SHORERD 345 Y50 | 708 | 948 | 183.76
128830 HMP HRBR 345 147857 DVNPT NK 345 1 Max |  |  |  |  | 201.11
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | Y49 | 450 | 563 | 133.3
128835 SHORE RD 345 129293 SHORE RD 138 1 Max |  |  |  |  | 133.3
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | Y49 | 462 | 562 | 124.61
128835 SHORE RD 345 129294 SHORE RD2 138 2 Max |  |  |  |  | 124.61
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 38 :NBR 1320 | 452 | 563 | 119.46
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 49 :NBR 1430 | 452 | 563 | 119.44
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.43
128847 NWBRG 345 129310 NEWBRGE 138 1 Max |  |  |  |  | 119.46
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.44
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 39 :NBR 1330 | 462 | 563 | 119.43
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | P5_EGC_138_M | 462 | 563 | 119.42
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 50 :NBR 1440 | 462 | 563 | 119.4
128847 NWBRG 345 129310 NEWBRGE 138 2 Max |  |  |  |  | 119.44
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Barrett Bus Tie | 201 | 296 | 388.67
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 12 :BRT BUS2 | 201 | 296 | 381.71
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 9 :BRT 1380 | 201 | 296 | 378.12
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 5 :VST NEW1 | 201 | 296 | 284.99
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-292 | 201 | 296 | 284.98
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Base Case | 201 | 296 | 216.74
129202 BARRETT1 138 129233 VLY STRM 138 1 Max |  |  |  |  | 388.67
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | P5_VALLEYSTREAM_138_M | 187 | 275 | 327.2
129203 BARRETT2 138 129204 BRRT PH 138 1 Max |  |  |  |  | 327.2
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 196 | 294 | 291.73
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 8 :VST BUS1 | 196 | 294 | 280.32
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 196 | 294 | 279.55
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | Base Case | 196 | 294 | 245.59
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | P5_EGC_138_M | 196 | 294 | 224.9
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 14 :FRP 1350 | 196 | 294 | 195.47
129203 BARRETT2 138 129234 VLY STRM2 138 2 Max |  |  |  |  | 291.73
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | P5_VALLEYSTREAM_138_M | 187 | 275 | 320.93
129204 BRRT PH 138 129276 FREEPORT 138 1 Max |  |  |  |  | 320.93
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 117 | 146 | 199.2
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 | 11 | 12 :BRT BUS2 | 117 | 146 | 124.62
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 | 11 | 9 :BRT 1380 | 117 | 146 | 121.39
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 | 11 | Base Case | 117 | 146 | 112.47
129205 BRTGT1-8 138 129501 BARRETT 69.0 1 Max |  |  |  |  | 199.2
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | P5_EGC_138_M | 274 | 366 | 165.64
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | Y49 | 274 | 366 | 121.75
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 139:EGC-CP2C | 274 | 366 | 103.51
129233 VLY STRM 138 129235 V STRM P 138 1 Max |  |  |  |  | 165.64
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | NEW_VS1430 | 214 | 298 | 137.28
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 12 :BRT BUS2 | 214 | 298 | 111.83
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 214 | 298 | 110.6
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 9 :BRT 1380 | 214 | 298 | 110.55
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | NEW_EGC 1390 | 214 | 298 | 109.46
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | Base Case | 214 | 298 | 106.82
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 Max |  |  |  |  | 137.28
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | DNWDIE - SHORERD 345 Y50 | 253 | 346 | 127.27
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | Y50 | 253 | 346 | 127.27
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | SB:DUNW345_4 | 253 | 346 | 126.97
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | SB:DUNW345_6 | 253 | 346 | 126.89
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | T:W89&W90_UC20 | 253 | 346 | 126.5
129248 L SUCS2 138 129249 L SUCSPH 138 1 Max |  |  |  |  | 127.27
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Y49 | 263 | 303 | 293.67
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 24 :EGC 1360 | 263 | 303 | 266.02
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | 263 | 303 | 254.05
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 20 :EGC 1320 | 263 | 303 | 253.45
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | 263 | 303 | 250.09
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | Base Case | 263 | 303 | 217.79
129265 CARLE PL 138 129270 E.G.C. 138 1 Max |  |  |  |  | 293.67
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Y49 | 264 | 324 | 256.2
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 24 :EGC 1360 | 264 | 324 | 230.94
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | 264 | 324 | 219.81
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 20 :EGC 1320 | 264 | 324 | 219.24
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | 264 | 324 | 216.12
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | Base Case | 264 | 324 | 195.24
129265 CARLE PL 138 129283 GLNWD SO 138 1 Max |  |  |  |  | 256.2
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | Y49 | 450 | 540 | 109.4
129270 E.G.C. 138 128822 E.G.C.-1 345 1 Max |  |  |  |  | 109.4
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Y49 | 263 | 303 | 278.53
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-361 | 263 | 303 | 245.01
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 26 :EGC 1380 | 263 | 303 | 244
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | EGCNEWBRKR | 263 | 303 | 243.6
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | NEW_EGC 1370 | 263 | 303 | 242.64
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Base Case | 263 | 303 | 203.29
129270 E.G.C. 138 129288 ROSLYN 138 1 Max |  |  |  |  | 278.53
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 129270 E.G.C. 138 129271 E.G.C.-2 138 1 | 207 | 287 | 236.79
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | P5_VALLEYSTREAM_138_M | 207 | 287 | 178.36
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 46 :NBR 1400 | 207 | 287 | 162.24
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | Base Case | 207 | 287 | 159.04
129270 E.G.C. 138 129310 NEWBRGE 138 1 Max |  |  |  |  | 236.79
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 129270 E.G.C. 138 129271 E.G.C.-2 138 1 | 201 | 295 | 222.21
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | P5_VALLEYSTREAM_138_M | 201 | 295 | 167.29
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | Base Case | 201 | 295 | 158.02
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 46 :NBR 1400 | 201 | 295 | 152.09
129270 E.G.C. 138 129310 NEWBRGE 138 3 Max |  |  |  |  | 222.21
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | Y49 | 450 | 540 | 107.3
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 Max |  |  |  |  | 107.3
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | Base Case | 174 | 293 | 180.88
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | P5_VALLEYSTREAM_138_M | 174 | 293 | 170.34
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 41 :NBR 1350 | 174 | 293 | 148.52
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 43 :NBR 1370 | 174 | 293 | 146.72
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 Max |  |  |  |  | 180.88
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | P5_VALLEYSTREAM_138_M | 235 | 305 | 271.43
129276 FREEPORT 138 129310 NEWBRGE 138 1 Max |  |  |  |  | 271.43
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Y49 | 264 | 324 | 247.79
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-361 | 264 | 324 | 216.96
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 26 :EGC 1380 | 264 | 324 | 216.02
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | EGCNEWBRKR | 264 | 324 | 215.65
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | NEW_EGC 1370 | 264 | 324 | 214.76
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | Base Case | 264 | 324 | 187.61
129281 GLNWD GT 138 129282 GLNWD NO 138 1 Max |  |  |  |  | 247.79
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Y49 | 264 | 324 | 247.8
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-361 | 264 | 324 | 216.98
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 26 :EGC 1380 | 264 | 324 | 216.05
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | EGCNEWBRKR | 264 | 324 | 215.67
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | NEW_EGC 1370 | 264 | 324 | 214.78
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Base Case | 264 | 324 | 187.63
129281 GLNWD GT 138 129288 ROSLYN 138 1 Max |  |  |  |  | 247.8
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Y49 | 285 | 366 | 223.69
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-361 | 285 | 366 | 193.78
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 26 :EGC 1380 | 285 | 366 | 193.1
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | EGCNEWBRKR | 285 | 366 | 192.63
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | NEW_EGC 1370 | 285 | 366 | 192.03
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 285 | 366 | 189.73
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Base Case | 285 | 366 | 168.32
129282 GLNWD NO 138 129293 SHORE RD 138 1 Max |  |  |  |  | 223.69
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Y49 | 264 | 324 | 260.71
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 24 :EGC 1360 | 264 | 324 | 233.11
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | 264 | 324 | 220.88
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 20 :EGC 1320 | 264 | 324 | 220.4
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 129282 GLNWD NO 138 129293 SHORE RD 138 1 | 264 | 324 | 218.12
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 33 :GLN 1340 | 264 | 324 | 217.49
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 36 :GLNNO BUS | 264 | 324 | 217.49
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | 264 | 324 | 217.49
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | Base Case | 264 | 324 | 189.48
129283 GLNWD SO 138 129294 SHORE RD2 138 1 Max |  |  |  |  | 260.71
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 54 :NBR 1480 | 240 | 278 | 106.57
129310 NEWBRGE 138 129361 RULND RD 138 2 Max |  |  |  |  | 106.57
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 135:RUL-NB2C | 243 | 324 | 112.69
129310 NEWBRGE 138 129361 RULND RD 138 3 Max |  |  |  |  | 112.69
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 | 11 | P5_EGC_138_M | 120 | 148 | 201.71
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 | 11 | 139:EGC-CP2C | 120 | 148 | 121.65
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 | 11 | 140:CP-ROS2C | 120 | 148 | 120.38
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 | 11 | 141:ROS-GL2C | 120 | 148 | 119.33
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 | 11 | Base Case | 120 | 148 | 106.78
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 120 | 148 | 106.68
129310 NEWBRGE 138 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 201.71
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 62 : PIL1370 | 396 | 482 | 103.75
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 Max |  |  |  |  | 103.75
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | Northport Bus Tie No.1-1 | 387 | 545 | 134.48
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 74 :NPT 1410 | 387 | 545 | 133.33
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 72 :NPT BUS1-2 | 387 | 545 | 131.32
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 67 :NPT 1300 | 387 | 545 | 131.32
129341 NRTHPRT1 138 129355 PILGRIM 138 1 Max |  |  |  |  | 134.48
129421 HOLBROOK 138 129807 HOLBRK2 69.0 2 | 11 | 98 :HOL 1370 | 104 | 128 | 119.99
129421 HOLBROOK 138 129807 HOLBRK2 69.0 2 | 11 | 97 :HOL 1360 | 104 | 128 | 110.5
129421 HOLBROOK 138 129807 HOLBRK2 69.0 2 | 11 | HOLBROOK 138/69 Bank #1 | 104 | 128 | 106.86
129421 HOLBROOK 138 129807 HOLBRK2 69.0 2 | 11 | 107:HOL BUS1 | 104 | 128 | 106.86
129421 HOLBROOK 138 129807 HOLBRK2 69.0 2 | 11 | 138-888 | 104 | 128 | 106.86
129421 HOLBROOK 138 129807 HOLBRK2 69.0 2 Max |  |  |  |  | 119.99
129501 BARRETT 69.0 129572 BALDWIN1 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 104 | 155 | 153.51
129501 BARRETT 69.0 129572 BALDWIN1 69.0 1 Max |  |  |  |  | 153.51
129507 CORONA 69.0 129528 VLYSTRM2 69.0 1 | 11 | P5_EGC_138_M | 106 | 126 | 110
129507 CORONA 69.0 129528 VLYSTRM2 69.0 1 | 11 | 69-262 | 106 | 126 | 101.99
129507 CORONA 69.0 129528 VLYSTRM2 69.0 1 Max |  |  |  |  | 110
129507 CORONA 69.0 129565 WHITESDE 69.0 1 | 11 | P5_EGC_138_M | 77 | 92 | 112.3
129507 CORONA 69.0 129565 WHITESDE 69.0 1 | 11 | 69-262 | 77 | 92 | 101.43
129507 CORONA 69.0 129565 WHITESDE 69.0 1 Max |  |  |  |  | 112.3
129527 VLYSTRM1 69.0 129233 VLY STRM 138 1 | 11 | P5_EGC_138_M | 249 | 277 | 109.65
129527 VLYSTRM1 69.0 129233 VLY STRM 138 1 | 11 | 2 :VST 1420 | 249 | 277 | 108.86
129527 VLYSTRM1 69.0 129233 VLY STRM 138 1 | 11 | NEW_VS1430 | 249 | 277 | 106.29
129527 VLYSTRM1 69.0 129233 VLY STRM 138 1 | 11 | VSBUS2 | 249 | 277 | 105.03
129527 VLYSTRM1 69.0 129233 VLY STRM 138 1 | 11 | VLY STRM 138/69 Bank #6 | 249 | 277 | 103.47
129527 VLYSTRM1 69.0 129233 VLY STRM 138 1 Max |  |  |  |  | 109.65
129527 VLYSTRM1 69.0 129565 WHITESDE 69.0 1 | 11 | 69-265 | 77 | 92 | 127.48
129527 VLYSTRM1 69.0 129565 WHITESDE 69.0 1 | 11 | P5_EGC_138_M | 77 | 92 | 114.8
129527 VLYSTRM1 69.0 129565 WHITESDE 69.0 1 | 11 | 155:COR 650 | 77 | 92 | 106.44
129527 VLYSTRM1 69.0 129565 WHITESDE 69.0 1 | 11 | 69-266 | 77 | 92 | 102.79
129527 VLYSTRM1 69.0 129565 WHITESDE 69.0 1 Max |  |  |  |  | 127.48
129528 VLYSTRM2 69.0 129234 VLY STRM2 138 2 | 11 | P5_EGC_138_M | 239 | 277 | 120.62
129528 VLYSTRM2 69.0 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 239 | 277 | 109.83
129528 VLYSTRM2 69.0 129234 VLY STRM2 138 2 | 11 | 8 :VST BUS1 | 239 | 277 | 109.47
129528 VLYSTRM2 69.0 129234 VLY STRM2 138 2 | 11 | 129527 VLYSTRM1 69.0 129233 VLY STRM 138 1 | 239 | 277 | 108.5
129528 VLYSTRM2 69.0 129234 VLY STRM2 138 2 | 11 | VS BUS 1 | 239 | 277 | 102.62
129528 VLYSTRM2 69.0 129234 VLY STRM2 138 2 Max |  |  |  |  | 120.62
129528 VLYSTRM2 69.0 129592 LAKEVIEW 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 47 | 59 | 182.87
129528 VLYSTRM2 69.0 129592 LAKEVIEW 69.0 1 | 11 | P5_EGC_138_M | 47 | 59 | 147.36
129528 VLYSTRM2 69.0 129592 LAKEVIEW 69.0 1 Max |  |  |  |  | 182.87
129529 VS_3_NEW 69.0 129546 MALVERN 69.0 1 | 11 | P5_EGC_138_M | 77 | 92 | 112.69
129529 VS_3_NEW 69.0 129546 MALVERN 69.0 1 Max |  |  |  |  | 112.69
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | 139:EGC-CP2C | 77 | 92 | 186.48
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | 140:CP-ROS2C | 77 | 92 | 182.52
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | 141:ROS-GL2C | 77 | 92 | 179.1
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | P5_EGC_138_M | 77 | 92 | 158.65
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | P5_SHORERD_138 | 77 | 92 | 149.12
129540 HERRICK 69.0 129558 SPERRY 69.0 1 | 11 | Base Case | 77 | 92 | 108.37
129540 HERRICK 69.0 129558 SPERRY 69.0 1 Max |  |  |  |  | 186.48
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | 139:EGC-CP2C | 118 | 139 | 144.91
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | 140:CP-ROS2C | 118 | 139 | 142.23
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | 141:ROS-GL2C | 118 | 139 | 139.91
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | P5_EGC_138_M | 118 | 139 | 126.63
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 | 11 | P5_SHORERD_138 | 118 | 139 | 120.14
129540 HERRICK 69.0 129580 E.G.C.1 69.0 1 Max |  |  |  |  | 144.91
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | 139:EGC-CP2C | 94 | 119 | 131.48
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | P5_EGC_138_M | 94 | 119 | 129.49
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | 140:CP-ROS2C | 94 | 119 | 128.24
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | 141:ROS-GL2C | 94 | 119 | 125.46
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 | 11 | P5_SHORERD_138 | 94 | 119 | 111.17
129543 LKE SCSS 69.0 129558 SPERRY 69.0 1 Max |  |  |  |  | 131.48
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | P5_EGC_138_M | 69 | 87 | 157.43
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 139:EGC-CP2C | 69 | 87 | 126.88
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 140:CP-ROS2C | 69 | 87 | 122.34
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 141:ROS-GL2C | 69 | 87 | 119.67
129543 LKE SCSS 69.0 129602 STWMANOR TAP 69.0 1 Max |  |  |  |  | 157.43
129546 MALVERN 69.0 129561 W.HEMP 1 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 47 | 59 | 176.82
129546 MALVERN 69.0 129561 W.HEMP 1 69.0 1 | 11 | P5_EGC_138_M | 47 | 59 | 140.57
129546 MALVERN 69.0 129561 W.HEMP 1 69.0 1 Max |  |  |  |  | 176.82
129562 W.HEMP 2 69.0 129592 LAKEVIEW 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 47 | 59 | 185.92
129562 W.HEMP 2 69.0 129592 LAKEVIEW 69.0 1 | 11 | P5_EGC_138_M | 47 | 59 | 144.39
129562 W.HEMP 2 69.0 129592 LAKEVIEW 69.0 1 Max |  |  |  |  | 185.92
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | P5_EGC_138_M | 69 | 87 | 161.87
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 139:EGC-CP2C | 69 | 87 | 131.35
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 140:CP-ROS2C | 69 | 87 | 126.78
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 | 11 | 141:ROS-GL2C | 69 | 87 | 124.08
129565 WHITESDE 69.0 129602 STWMANOR TAP 69.0 1 Max |  |  |  |  | 161.87
129572 BALDWIN1 69.0 129617 BELMR 1 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 104 | 155 | 119.52
129572 BALDWIN1 69.0 129617 BELMR 1 69.0 1 Max |  |  |  |  | 119.52
129580 E.G.C.1 69.0 129270 E.G.C. 138 1 | 11 | P5_VALLEYSTREAM_138_M | 239 | 277 | 105.79
129580 E.G.C.1 69.0 129270 E.G.C. 138 1 Max |  |  |  |  | 105.79
129580 E.G.C.1 69.0 129593 HEMPSTEAD 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 138 | 138 | 111.74
129580 E.G.C.1 69.0 129593 HEMPSTEAD 69.0 1 Max |  |  |  |  | 111.74
129582 E.G.C.2 69.0 129595 LINDBERGH 69.0 1 | 11 | 44 :NBR 1380 | 69 | 100 | 106.03
129582 E.G.C.2 69.0 129595 LINDBERGH 69.0 1 | 11 | 38 :NBR 1320 | 69 | 100 | 105.41
129582 E.G.C.2 69.0 129595 LINDBERGH 69.0 1 | 11 | NEWBRGE 138/69 Bank #6 | 69 | 100 | 105.41
129582 E.G.C.2 69.0 129595 LINDBERGH 69.0 1 | 11 | 43 :NBR BH BUS | 69 | 100 | 105.37
129582 E.G.C.2 69.0 129595 LINDBERGH 69.0 1 | 11 | NB REA | 69 | 100 | 105.37
129582 E.G.C.2 69.0 129595 LINDBERGH 69.0 1 Max |  |  |  |  | 106.03
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 | 11 | P5_EGC_138_M | 124 | 163 | 124.81
129590 GLNWD#3A 69.0 129594 MTCHGRDN 69.0 1 Max |  |  |  |  | 124.81
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | P5_EGC_138_M | 124 | 163 | 140.95
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | 139:EGC-CP2C | 124 | 163 | 116.81
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | 140:CP-ROS2C | 124 | 163 | 114.36
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 | 11 | 141:ROS-GL2C | 124 | 163 | 112.52
129594 MTCHGRDN 69.0 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 140.95
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | 44 :NBR 1380 | 55 | 67 | 139.26
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | 38 :NBR 1320 | 55 | 67 | 138.32
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | NEWBRGE 138/69 Bank #6 | 55 | 67 | 138.32
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | NB REA | 55 | 67 | 138.28
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 | 11 | 55 :NBR 1490 | 55 | 67 | 138.28
129595 LINDBERGH 69.0 129633 MEDBROOK 69.0 1 Max |  |  |  |  | 139.26
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 | 11 | P5_EGC_138_M | 77 | 92 | 166.73
129598 ORCHARD 69.0 129627 LCST VLY 69.0 1 Max |  |  |  |  | 166.73
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 | 11 | P5_EGC_138_M | 77 | 92 | 201.39
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 | 11 | P5_VALLEYSTREAM_138_M | 77 | 92 | 148.99
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 | 11 | 139:EGC-CP2C | 77 | 92 | 114.47
129617 BELMR 1 69.0 129635 N.BELLMR 69.0 1 Max |  |  |  |  | 201.39
129619 BELMR 2 69.0 129639 NEWBRGE1 69.0 1 | 11 | P5_EGC_138_M | 92 | 123 | 157.85
129619 BELMR 2 69.0 129639 NEWBRGE1 69.0 1 | 11 | 224:MS 650 | 92 | 123 | 118.33
129619 BELMR 2 69.0 129639 NEWBRGE1 69.0 1 | 11 | 129202 BARRETT1 138 129205 BRTGT1-8 138 1 | 92 | 123 | 112.56
129619 BELMR 2 69.0 129639 NEWBRGE1 69.0 1 Max |  |  |  |  | 157.85
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 | 11 | P5_EGC_138_M | 94 | 119 | 128.53
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 | 11 | MG BUS1 | 94 | 119 | 113.7
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 | 11 | 139:EGC-CP2C | 94 | 119 | 110.97
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 | 11 | 140:CP-ROS2C | 94 | 119 | 109.03
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 | 11 | 141:ROS-GL2C | 94 | 119 | 107.57
129625 JERICHO 69.0 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 128.53
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | P5_EGC_138_M | 77 | 92 | 193.36
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | 139:EGC-CP2C | 77 | 92 | 124.54
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | 140:CP-ROS2C | 77 | 92 | 121.83
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | 141:ROS-GL2C | 77 | 92 | 119.87
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 | 11 | NEWBUS2 | 77 | 92 | 105.68
129627 LCST VLY 69.0 129642 OYSTRBAY 69.0 1 Max |  |  |  |  | 193.36
129630 MASPEQUA2 69.0 129646 PLNEDGE 69.0 1 | 11 | 225:MS 660 | 62 | 74 | 109
129630 MASPEQUA2 69.0 129646 PLNEDGE 69.0 1 Max |  |  |  |  | 109
129630 MASPEQUA2 69.0 129765 STERLING 69.0 1 | 11 | P5_EGC_138_M | 132 | 162 | 105.13
129630 MASPEQUA2 69.0 129765 STERLING 69.0 1 Max |  |  |  |  | 105.13
129633 MEDBROOK 69.0 129640 NEWBRGE2 69.0 1 | 11 | 44 :NBR 1380 | 55 | 69 | 129.64
129633 MEDBROOK 69.0 129640 NEWBRGE2 69.0 1 | 11 | 38 :NBR 1320 | 55 | 69 | 128.72
129633 MEDBROOK 69.0 129640 NEWBRGE2 69.0 1 | 11 | NEWBRGE 138/69 Bank #6 | 55 | 69 | 128.71
129633 MEDBROOK 69.0 129640 NEWBRGE2 69.0 1 | 11 | 43 :NBR BH BUS | 55 | 69 | 128.67
129633 MEDBROOK 69.0 129640 NEWBRGE2 69.0 1 | 11 | NB REA | 55 | 69 | 128.67
129633 MEDBROOK 69.0 129640 NEWBRGE2 69.0 1 | 11 | 55 :NBR 1490 | 55 | 69 | 128.67
129633 MEDBROOK 69.0 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 129.64
129635 N.BELLMR 69.0 129640 NEWBRGE2 69.0 1 | 11 | P5_EGC_138_M | 106 | 126 | 122.9
129635 N.BELLMR 69.0 129640 NEWBRGE2 69.0 1 Max |  |  |  |  | 122.9
129642 OYSTRBAY 69.0 129650 SYOSSET 69.0 1 | 11 | P5_EGC_138_M | 147 | 163 | 131.08
129642 OYSTRBAY 69.0 129650 SYOSSET 69.0 1 Max |  |  |  |  | 131.08
129644 PLN TAP 69.0 129648 PLNVIEW 69.0 1 | 11 | SS BUS1 | 71 | 95 | 122.56
129644 PLN TAP 69.0 129648 PLNVIEW 69.0 1 | 11 | 213:SS 630 | 71 | 95 | 122.56
129644 PLN TAP 69.0 129648 PLNVIEW 69.0 1 | 11 | P5_SYOSSET_138 | 71 | 95 | 109.96
129644 PLN TAP 69.0 129648 PLNVIEW 69.0 1 | 11 | 36 :SYT 1340 | 71 | 95 | 108.32
129644 PLN TAP 69.0 129648 PLNVIEW 69.0 1 | 11 | SYOSSET 138/69 Bank #5 | 71 | 95 | 107.9
129644 PLN TAP 69.0 129648 PLNVIEW 69.0 1 Max |  |  |  |  | 122.56
129644 PLN TAP 69.0 129692 RULND RD 69.0 1 | 11 | SS BUS1 | 87 | 101 | 115.15
129644 PLN TAP 69.0 129692 RULND RD 69.0 1 | 11 | 213:SS 630 | 87 | 101 | 115.15
129644 PLN TAP 69.0 129692 RULND RD 69.0 1 | 11 | P5_SYOSSET_138 | 87 | 101 | 103.18
129644 PLN TAP 69.0 129692 RULND RD 69.0 1 | 11 | 36 :SYT 1340 | 87 | 101 | 101.63
129644 PLN TAP 69.0 129692 RULND RD 69.0 1 | 11 | SYOSSET 138/69 Bank #5 | 87 | 101 | 101.23
129644 PLN TAP 69.0 129692 RULND RD 69.0 1 Max |  |  |  |  | 115.15
129662 BETHPAGE 69.0 129759 S.FARM2 69.0 1 | 11 | 225:MS 660 | 132 | 162 | 101.82
129662 BETHPAGE 69.0 129759 S.FARM2 69.0 1 Max |  |  |  |  | 101.82
129671 ELWOOD 69.0 129689 PULASKI 69.0 1 | 11 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 106 | 126 | 110.44
129671 ELWOOD 69.0 129689 PULASKI 69.0 1 | 11 | GEN: OSW Holbrook 1 | 106 | 126 | 110.39
129671 ELWOOD 69.0 129689 PULASKI 69.0 1 Max |  |  |  |  | 110.44
129686 PILGRM2 69.0 129727 BRNTWOOD 69.0 2 | 11 | PL BUS1 | 87 | 101 | 120.13
129686 PILGRM2 69.0 129727 BRNTWOOD 69.0 2 Max |  |  |  |  | 120.13
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 | 11 | P5_VALLEYSTREAM_138_M | 70 | 80 | 184.82
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 | 11 | 129202 BARRETT1 138 129205 BRTGT1-8 138 1 | 70 | 80 | 111.24
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 | 11 | BRT69KV | 70 | 80 | 107.38
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 | 11 | 166:BRT6010 | 70 | 80 | 107.38
129970 BARRETT2 34.5 129206 BRTGT9-12 138 1 Max |  |  |  |  | 184.82

## N-1-1_SUM_Alt
Monitored Facility | Areas | First Level Scenario | Cont Name | Rate Base (MVA) | Rate Cont (MVA) | SCD AC %Loading
121408 NE_601_NY 138 129343 NRTHPT P 138 1 | 101/11 | DNWDIE - SHORERD 345 Y50 | Y49 | 155 | 192 | 137.98
121408 NE_601_NY 138 129343 NRTHPT P 138 1 Max | [5 empty] | 137.98
121409 NE_602_NY 138 129343 NRTHPT P 138 2 | 101/11 | DNWDIE - SHORERD 345 Y50 | Y49 | 155 | 192 | 137.56
121409 NE_602_NY 138 129343 NRTHPT P 138 2 Max | [5 empty] | 137.56
121410 NE_603_NY 138 129343 NRTHPT P 138 3 | 101/11 | DNWDIE - SHORERD 345 Y50 | Y49 | 155 | 192 | 136.66
121410 NE_603_NY 138 129343 NRTHPT P 138 3 Max | [5 empty] | 136.66
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | JAMCA - VLLYSTRM 901L&M 138 | Y49 | 690 | 963 | 174.04
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | 901 L&M | Y49 | 690 | 963 | 174.04
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | VLY STRM 138 kV P.A.R. | Y49 | 690 | 963 | 173.88
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | VLY STRM 138/69 kV Bank #5 | Y49 | 690 | 963 | 173.75
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | NNC-3C | Y49 | 690 | 963 | 172.94
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | Northport-Norwalk NNC-3C | Y49 | 690 | 963 | 172.94
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | GEN: OSW Astoria 2 | Y49 | 690 | 963 | 158.51
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | SPRNBRK - EGC 345 Y49 | Base Case | 690 | 963 | 158.39
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | HVDC: HQ Rainey 7 | Y49 | 690 | 963 | 157.39
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | GEN: OSW W49 Street 5 | Y49 | 690 | 963 | 157.35
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | GEN: OSW Farragut 4 | Y49 | 690 | 963 | 157.33
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | GEN: OSW Farragut 3 | Y49 | 690 | 963 | 157.33
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | JAMCA - LKSUCCESS 903 138 | Y49 | 690 | 963 | 157.18
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | 903 | Y49 | 690 | 963 | 157.18
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | LKE SCSS 138 kV P.A.R. | Y49 | 690 | 963 | 157.08
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | GEN: OSW Gowanus 1 | Y49 | 690 | 963 | 154.94
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | E.G.C. 345 kV P.A.R. #2 | Y49 | 690 | 963 | 154.94
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | EGC REA | Y49 | 690 | 963 | 154.44
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | E.G.C. 345 kV P.A.R. #1 | Y49 | 690 | 963 | 154.44
126266 DUNWOODIE 345 128835 SHORE RD 345 1 | 9/11 | 138-366 | Y49 | 690 | 963 | 153.64
126266 DUNWOODIE 345 128835 SHORE RD 345 1 Max | [5 empty] | 174.04
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 | 10 | DNWDIE - SHORERD 345 Y50 | Y49 | 120 | 160 | 127.22
126280 FARRAGUT TX9 345 126437 FGT_X9 138 1 Max | [5 empty] | 127.22
126287 GOWANUS 345 126429 GOWNUST14 138 1 | 10 | GOETHALS-FOXHILLS PAR | Base Case | 271 | 335 | 101.61
126287 GOWANUS 345 126429 GOWNUST14 138 1 Max | [5 empty] | 101.61
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | Base Case | 1243 | 1386 | 167.33
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 139:EGC-CP2C | 1243 | 1386 | 156.33
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 140:CP-ROS2C | 1243 | 1386 | 155.81
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | P5_LAKESUCCES_138 | 1243 | 1386 | 155.66
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 903 | 1243 | 1386 | 155.59
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | JAMCA - LKSUCCESS 903 138 | 1243 | 1386 | 155.59
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 16 :LKS BUS2 | 1243 | 1386 | 155.58
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | LKE SCSS 138 kV P.A.R. | 1243 | 1386 | 155.56
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | P5_SHORERD_138 | 1243 | 1386 | 155.52
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 141:ROS-GL2C | 1243 | 1386 | 155.3
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | VLY STRM 138/69 kV Bank #5 | 1243 | 1386 | 153.56
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 12 :CRP 1350 | 1243 | 1386 | 153.48
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | JAMCA - VLLYSTRM 901L&M 138 | 1243 | 1386 | 152.99
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 901 L&M | 1243 | 1386 | 152.99
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | VLY STRM 138 kV P.A.R. | 1243 | 1386 | 152.94
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 8 :VST BUS1 | 1243 | 1386 | 152.92
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 13 :ROS 1350 | 1243 | 1386 | 152.74
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 34 :LG 1350 | 1243 | 1386 | 152.5
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 83 :ROK 1350 | 1243 | 1386 | 152.11
126298 SPRAINBROOK 345 126299 REACBUS 345 BY | 9 | DNWDIE - SHORERD 345 Y50 | 258:ST 650 | 1243 | 1386 | 151.99
126298 SPRAINBROOK 345 126299 REACBUS 345 BY Max | [5 empty] | 167.33
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | DNWDIE - SHORERD 345 Y50 | Base Case | 708 | 948 | 295.41
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | JAMCA - LKSUCCESS 903 138 | Base Case | 708 | 948 | 255.24
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 903 | Base Case | 708 | 948 | 255.24
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | LKE SCSS 138 kV P.A.R. | Base Case | 708 | 948 | 255.23
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | BELMR 69/34.5 kV BK#5 | Base Case | 708 | 948 | 239.12
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | LKE SCSS 138/69 Bank #6 | Base Case | 708 | 948 | 236.08
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 69-574 | Base Case | 708 | 948 | 235.78
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 69-366 364 | Base Case | 708 | 948 | 235.65
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 69-481 | Base Case | 708 | 948 | 235.62
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 69-372 | Base Case | 708 | 948 | 235.49
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | 69-371 | Base Case | 708 | 948 | 235.4
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | DNWDIE - SHORERD 345 Y50 | 139:EGC-CP2C | 708 | 948 | 229.79
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | DNWDIE - SHORERD 345 Y50 | 140:CP-ROS2C | 708 | 948 | 229.02
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | DNWDIE - SHORERD 345 Y50 | P5_LAKESUCCES_138 | 708 | 948 | 228.81
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | DNWDIE - SHORERD 345 Y50 | JAMCA - LKSUCCESS 903 138 | 708 | 948 | 228.71
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | DNWDIE - SHORERD 345 Y50 | 903 | 708 | 948 | 228.71
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | DNWDIE - SHORERD 345 Y50 | 16 :LKS BUS2 | 708 | 948 | 228.7
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | DNWDIE - SHORERD 345 Y50 | LKE SCSS 138 kV P.A.R. | 708 | 948 | 228.67
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | DNWDIE - SHORERD 345 Y50 | P5_SHORERD_138 | 708 | 948 | 228.6
126299 REACBUS 345 147857 DVNPT NK 345 1 | 9 | DNWDIE - SHORERD 345 Y50 | 141:ROS-GL2C | 708 | 948 | 228.28
126299 REACBUS 345 147857 DVNPT NK 345 1 Max | [5 empty] | 295.41
126364 CORONA1R 138 126455 JAMAICA 138 1 | 10 | DNWDIE - SHORERD 345 Y50 | Y49 | 159 | 235 | 136.22
126364 CORONA1R 138 126455 JAMAICA 138 1 Max | [5 empty] | 136.22
126365 CORONA2R 138 126455 JAMAICA 138 1 | 10 | DNWDIE - SHORERD 345 Y50 | Y49 | 159 | 235 | 152.88
126365 CORONA2R 138 126455 JAMAICA 138 1 Max | [5 empty] | 152.88
126399 TAP X9 138 126437 FGT_X9 138 1 | 10 | DNWDIE - SHORERD 345 Y50 | Y49 | 165 | 165 | 126.4
126399 TAP X9 138 126437 FGT_X9 138 1 Max | [5 empty] | 126.4
126415 CORONA-N 138 126365 CORONA2R 138 1 | 10 | DNWDIE - SHORERD 345 Y50 | Y49 | 239 | 305 | 116.9
126415 CORONA-N 138 126365 CORONA2R 138 1 Max | [5 empty] | 116.9
126416 FOX HILLS 138 126883 GOTHLS PAR 138 1 | 10 | FRSHKILLS 345/138 TA1 | Base Case | 329 | 415 | 101.39
126416 FOX HILLS 138 126883 GOTHLS PAR 138 1 Max | [5 empty] | 101.39
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | DNWDIE - SHORERD 345 Y50 | Y49 | 273 | 365 | 237.77
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | LKE SCSS 138 kV P.A.R. | Y49 | 273 | 365 | 157.92
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 903 | Y49 | 273 | 365 | 157.71
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | JAMCA - LKSUCCESS 903 138 | Y49 | 273 | 365 | 157.71
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | SHORE RD 345/138 Bank #1 | Y49 | 273 | 365 | 147.11
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | SHORE RD 345/138 Bank #2 | Y49 | 273 | 365 | 145.92
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | LKE SCSS 138/69 Bank #6 | Y49 | 273 | 365 | 140.12
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | BELMR 69/34.5 kV BK#5 | Y49 | 273 | 365 | 140.09
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 69-481 | Y49 | 273 | 365 | 139.5
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 69-372 | Y49 | 273 | 365 | 139.47
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 69-371 | Y49 | 273 | 365 | 139.42
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 69-366 364 | Y49 | 273 | 365 | 139.29
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | LKE SCSS 138/69 Bank #5 | Y49 | 273 | 365 | 139.13
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | GLNWD SO 138/69 kV Bank #6 | Y49 | 273 | 365 | 138.65
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 69-574 | Y49 | 273 | 365 | 138.62
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | GLNWD NO 138/69 Bank #5 | Y49 | 273 | 365 | 138.49
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 69-576 | Y49 | 273 | 365 | 138
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | 69-533 | Y49 | 273 | 365 | 137.94
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | NNC-3C | Y49 | 273 | 365 | 137.83
126455 JAMAICA 138 129235 V STRM P 138 1 | 10/11 | Northport-Norwalk NNC-3C | Y49 | 273 | 365 | 137.83
126455 JAMAICA 138 129235 V STRM P 138 1 Max | [5 empty] | 237.77
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | DNWDIE - SHORERD 345 Y50 | Y49 | 252 | 345 | 240.59
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | SPRNBRK - EGC 345 Y49 | Y50 | 252 | 345 | 199.37
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-362 | Y50 | 252 | 345 | 158.41
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-366 | Y50 | 252 | 345 | 157.83
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-364 | Y50 | 252 | 345 | 155.72
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-365 | Y50 | 252 | 345 | 144.81
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | DNWDIE - SHORERD 345 Y50 | Y49 | 252 | 345 | 143.83
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-361 | Y50 | 252 | 345 | 143.73
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 138-363 | Y50 | 252 | 345 | 142.96
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | VLY STRM 138/69 kV Bank #5 | Y49 | 252 | 345 | 141.47
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | VLY STRM 138 kV P.A.R. | Y49 | 252 | 345 | 138.47
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | JAMCA - VLLYSTRM 901L&M 138 | Y49 | 252 | 345 | 138.02
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 901 L&M | Y49 | 252 | 345 | 138.02
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | E.G.C. 345 kV P.A.R. #2 | Y50 | 252 | 345 | 137.54
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | JAMCA - VLLYSTRM 901L&M 138 | Y50 | 252 | 345 | 137.26
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | 901 L&M | Y50 | 252 | 345 | 137.26
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | VLY STRM 138 kV P.A.R. | Y50 | 252 | 345 | 137.25
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | VLY STRM 138/69 kV Bank #5 | Y50 | 252 | 345 | 135.47
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | E.G.C. 345 kV P.A.R. #1 | Y50 | 252 | 345 | 135.29
126455 JAMAICA 138 129249 L SUCSPH 138 1 | 10/11 | EGC REA | Y50 | 252 | 345 | 135.29
126455 JAMAICA 138 129249 L SUCSPH 138 1 Max | [5 empty] | 240.59
126506 VERNON-E 138 126646 GRENWOOD S 138 1 | 10 | GOWANUS 345/138 2TR | Base Case | 193 | 262 | 104.86
126506 VERNON-E 138 126646 GRENWOOD S 138 1 | 10 | FRSHKILLS 345/138 TA1 | Base Case | 193 | 262 | 104.8
126506 VERNON-E 138 126646 GRENWOOD S 138 1 | 10 | FRSHKILLS 345/138 TB1 | Base Case | 193 | 262 | 103.85
126506 VERNON-E 138 126646 GRENWOOD S 138 1 Max | [5 empty] | 104.86
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 | 10 | DNWDIE - SHORERD 345 Y50 | Y49 | 120 | 160 | 127.26
126644 FARRAGUT WES 345 126451 FGT_X8 138 1 Max | [5 empty] | 127.26
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | Y49 | 450 | 630 | 192.05
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | E.G.C. 345 kV P.A.R. #2 | 450 | 630 | 113.79
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 450 | 630 | 113.79
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 450 | 630 | 113.79
128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | Base Case | 450 | 630 | 108.87
128822 E.G.C.-1 345 128825 EGC PAR 345 1 Max | [5 empty] | 192.05
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | Y49 | 450 | 630 | 191.74
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | EGC REA | Y49 | 450 | 630 | 191.74
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 450 | 630 | 114.68
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 33 :EGC BUS2 | 450 | 630 | 114.68
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | EGC REA | 450 | 630 | 114.68
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | E.G.C. 345 kV P.A.R. #1 | 450 | 630 | 114.68
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 450 | 630 | 114.68
128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | Base Case | 450 | 630 | 111.17
128823 E.G.C.-2 345 128825 EGC PAR 345 1 Max | [5 empty] | 191.74
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | Base Case | 707 | 948 | 300.66
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | JAMCA - LKSUCCESS 903 138 | Base Case | 707 | 948 | 261.32
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 903 | Base Case | 707 | 948 | 261.32
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | LKE SCSS 138 kV P.A.R. | Base Case | 707 | 948 | 261.31
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | BELMR 69/34.5 kV BK#5 | Base Case | 707 | 948 | 246.02
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | LKE SCSS 138/69 Bank #6 | Base Case | 707 | 948 | 243.01
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 69-574 | Base Case | 707 | 948 | 242.72
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 69-366 364 | Base Case | 707 | 948 | 242.51
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 69-481 | Base Case | 707 | 948 | 242.49
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 69-372 | Base Case | 707 | 948 | 242.31
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 903 | 707 | 948 | 232.23
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | JAMCA - LKSUCCESS 903 138 | 707 | 948 | 232.23
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 16 :LKS BUS2 | 707 | 948 | 232.22
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | LKE SCSS 138 kV P.A.R. | 707 | 948 | 232.19
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | VLY STRM 138/69 kV Bank #5 | 707 | 948 | 229.29
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | 69-465 | Base Case | 707 | 948 | 228.65
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | JAMCA - VLLYSTRM 901L&M 138 | 707 | 948 | 228.46
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 901 L&M | 707 | 948 | 228.46
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | VLY STRM 138 kV P.A.R. | 707 | 948 | 228.38
128824 EGC DUM 345 128825 EGC PAR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 8 :VST BUS1 | 707 | 948 | 228.35
128824 EGC DUM 345 128825 EGC PAR 345 1 Max | [5 empty] | 300.66
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | Base Case | 707 | 948 | 305.06
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | LKE SCSS 138 kV P.A.R. | Base Case | 707 | 948 | 266.86
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | JAMCA - LKSUCCESS 903 138 | Base Case | 707 | 948 | 266.86
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 903 | Base Case | 707 | 948 | 266.86
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | BELMR 69/34.5 kV BK#5 | Base Case | 707 | 948 | 252.45
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | LKE SCSS 138/69 Bank #6 | Base Case | 707 | 948 | 249.49
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 69-574 | Base Case | 707 | 948 | 249.22
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 69-366 364 | Base Case | 707 | 948 | 248.95
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 69-481 | Base Case | 707 | 948 | 248.95
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 69-372 | Base Case | 707 | 948 | 248.73
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 139:EGC-CP2C | 707 | 948 | 236.41
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 140:CP-ROS2C | 707 | 948 | 235.67
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | P5_LAKESUCCES_138 | 707 | 948 | 235.46
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 903 | 707 | 948 | 235.36
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | JAMCA - LKSUCCESS 903 138 | 707 | 948 | 235.36
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 16 :LKS BUS2 | 707 | 948 | 235.35
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | 69-465 | Base Case | 707 | 948 | 235.33
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | LKE SCSS 138 kV P.A.R. | 707 | 948 | 235.32
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | P5_SHORERD_138 | 707 | 948 | 235.26
128824 EGC DUM 345 128830 HMP HRBR 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 141:ROS-GL2C | 707 | 948 | 234.94
128824 EGC DUM 345 128830 HMP HRBR 345 1 Max | [5 empty] | 305.06
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | DNWDIE - SHORERD 345 Y50 | Base Case | 708 | 948 | 302.82
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 903 | Base Case | 708 | 948 | 264.13
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | JAMCA - LKSUCCESS 903 138 | Base Case | 708 | 948 | 264.13
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | LKE SCSS 138 kV P.A.R. | Base Case | 708 | 948 | 264.12
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | BELMR 69/34.5 kV BK#5 | Base Case | 708 | 948 | 249.34
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | LKE SCSS 138/69 Bank #6 | Base Case | 708 | 948 | 246.36
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 69-574 | Base Case | 708 | 948 | 246.08
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 69-366 364 | Base Case | 708 | 948 | 245.84
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 69-481 | Base Case | 708 | 948 | 245.83
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 69-372 | Base Case | 708 | 948 | 245.62
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | 69-371 | Base Case | 708 | 948 | 245.57
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | DNWDIE - SHORERD 345 Y50 | 139:EGC-CP2C | 708 | 948 | 235.14
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | DNWDIE - SHORERD 345 Y50 | 140:CP-ROS2C | 708 | 948 | 234.39
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | DNWDIE - SHORERD 345 Y50 | P5_LAKESUCCES_138 | 708 | 948 | 234.18
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | DNWDIE - SHORERD 345 Y50 | JAMCA - LKSUCCESS 903 138 | 708 | 948 | 234.08
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | DNWDIE - SHORERD 345 Y50 | 903 | 708 | 948 | 234.08
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | DNWDIE - SHORERD 345 Y50 | 16 :LKS BUS2 | 708 | 948 | 234.07
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | DNWDIE - SHORERD 345 Y50 | LKE SCSS 138 kV P.A.R. | 708 | 948 | 234.04
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | DNWDIE - SHORERD 345 Y50 | P5_SHORERD_138 | 708 | 948 | 233.98
128830 HMP HRBR 345 147857 DVNPT NK 345 1 | 11/9 | DNWDIE - SHORERD 345 Y50 | 141:ROS-GL2C | 708 | 948 | 233.66
128830 HMP HRBR 345 147857 DVNPT NK 345 1 Max | [5 empty] | 302.82
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SHORE RD 345/138 Bank #2 | Y49 | 450 | 563 | 205.23
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SPRNBRK - EGC 345 Y49 | SHORE RD 345/138 Bank #2 | 450 | 563 | 152.78
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | 901 L&M | Y49 | 450 | 563 | 149.86
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Y49 | 450 | 563 | 149.86
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | NNC-3C | Y49 | 450 | 563 | 149.84
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | Northport-Norwalk NNC-3C | Y49 | 450 | 563 | 149.84
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | VLY STRM 138 kV P.A.R. | Y49 | 450 | 563 | 149.79
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Y49 | 450 | 563 | 149.1
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 21 :SRD BUS2 | 450 | 563 | 138.03
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | JAMCA - LKSUCCESS 903 138 | Y49 | 450 | 563 | 136.56
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | 903 | Y49 | 450 | 563 | 136.56
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | LKE SCSS 138 kV P.A.R. | Y49 | 450 | 563 | 136.48
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | GEN: OSW Astoria 2 | Y49 | 450 | 563 | 136.15
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | HVDC: HQ Rainey 7 | Y49 | 450 | 563 | 135.77
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | GEN: OSW W49 Street 5 | Y49 | 450 | 563 | 135.72
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | GEN: OSW Farragut 4 | Y49 | 450 | 563 | 135.71
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | GEN: OSW Farragut 3 | Y49 | 450 | 563 | 135.71
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | EGC REA | Y49 | 450 | 563 | 133.99
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | E.G.C. 345 kV P.A.R. #1 | Y49 | 450 | 563 | 133.99
128835 SHORE RD 345 129293 SHORE RD 138 1 | 11 | E.G.C. 345 kV P.A.R. #2 | Y49 | 450 | 563 | 133.96
128835 SHORE RD 345 129293 SHORE RD 138 1 Max | [5 empty] | 205.23
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | Y49 | 462 | 562 | 202.31
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SPRNBRK - EGC 345 Y49 | SHORE RD 345/138 Bank #1 | 462 | 562 | 148.71
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Y49 | 462 | 562 | 140.1
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | 901 L&M | Y49 | 462 | 562 | 140.1
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | Northport-Norwalk NNC-3C | Y49 | 462 | 562 | 140.07
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | NNC-3C | Y49 | 462 | 562 | 140.07
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | VLY STRM 138 kV P.A.R. | Y49 | 462 | 562 | 140.03
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | Y49 | 462 | 562 | 139.38
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SPRNBRK - EGC 345 Y49 | 20 :SRD BUS1 | 462 | 562 | 135.3
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | 903 | Y49 | 462 | 562 | 127.66
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | JAMCA - LKSUCCESS 903 138 | Y49 | 462 | 562 | 127.66
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | LKE SCSS 138 kV P.A.R. | Y49 | 462 | 562 | 127.59
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | GEN: OSW Astoria 2 | Y49 | 462 | 562 | 127.28
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | HVDC: HQ Rainey 7 | Y49 | 462 | 562 | 126.92
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | GEN: OSW W49 Street 5 | Y49 | 462 | 562 | 126.88
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | GEN: OSW Farragut 3 | Y49 | 462 | 562 | 126.87
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | GEN: OSW Farragut 4 | Y49 | 462 | 562 | 126.87
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | SHORE RD 345/138 Bank #1 | Y49 | 462 | 562 | 125.39
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | EGC REA | Y49 | 462 | 562 | 125.26
128835 SHORE RD 345 129294 SHORE RD2 138 2 | 11 | E.G.C. 345 kV P.A.R. #1 | Y49 | 462 | 562 | 125.26
128835 SHORE RD 345 129294 SHORE RD2 138 2 Max | [5 empty] | 202.31
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | NEWBRGE 345/138 Bank #2 | Base Case | 452 | 563 | 148.79
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | FARRAGUTW 345/138 8TR | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.31
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | FARRAGUTE 345/138 9TR | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.31
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | LKE SCSS 138 kV P.A.R. | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.3
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | GEN: OSW Farragut 4 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.29
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | GEN: OSW Farragut 3 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.29
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | GEN: OSW Gowanus 1 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.29
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 138-365 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.27
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 138-362 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.27
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | SPRNBRK - DUNWDIE 345 W75 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.27
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | E.G.C. 345 kV P.A.R. #2 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.27
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 138-363 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.26
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | PV - MILLWOOD F31/W81 345 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.26
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | JAMCA - LKSUCCESS 903 138 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.26
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | 903 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.26
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | PV - MILLWOOD 345 F30/W80 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.26
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | GEN: OSW Astoria 2 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.25
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | SPRNBRK - EGC 345 Y49 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.25
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | GEN: OSW W49 Street 5 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.25
128847 NWBRG 345 129310 NEWBRGE 138 1 | 11 | HVDC: HQ Rainey 7 | NEWBRGE 345/138 Bank #2 | 452 | 563 | 119.25
128847 NWBRG 345 129310 NEWBRGE 138 1 Max | [5 empty] | 148.79
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | NEWBRGE 345/138 Bank #1 | Base Case | 462 | 563 | 145.57
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-292 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.36
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-291 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.31
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-567 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.3
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-459 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.28
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | NRTHPRT P.A.R. #2 (Bus) | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.25
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-261 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.25
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-262 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | BARRETT 138 kV P.A.R. | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-461 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.24
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-563 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.21
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-562 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.21
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | E.G.C. 345 kV P.A.R. #2 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.21
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | SPRNBRK - DUNWDIE 345 W75 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.21
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-681 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.21
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-561 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.21
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | PV - MILLWOOD 345 F30/W80 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.2
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | Barrett G1-8* | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.2
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-678 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.2
128847 NWBRG 345 129310 NEWBRGE 138 2 | 11 | 138-676 | NEWBRGE 345/138 Bank #1 | 462 | 563 | 119.2
128847 NWBRG 345 129310 NEWBRGE 138 2 Max | [5 empty] | 145.57
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 138-292 | Base Case | 201 | 296 | 445.72
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Barrett G1-8* | Barrett Bus Tie | 201 | 296 | 437.04
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | Barrett G1-8* | 12 :BRT BUS2 | 201 | 296 | 436.67
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-359 | Y49 | 201 | 296 | 413.45
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-359 | 12 :BRT BUS2 | 201 | 296 | 403.43
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | BELMR 69/34.5 kV BK#5 | Barrett Bus Tie | 201 | 296 | 402.18
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-459 | Barrett Bus Tie | 201 | 296 | 401.95
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-574 | Barrett Bus Tie | 201 | 296 | 393.3
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | BARRETT 69/34.5 kV BK#3 | Barrett Bus Tie | 201 | 296 | 392.12
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | GEN: OSW EGC 5 | Barrett Bus Tie | 201 | 296 | 391.87
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | DNWDIE - SHORERD 345 Y50 | Barrett Bus Tie | 201 | 296 | 391.56
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-576 | Barrett Bus Tie | 201 | 296 | 391.2
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | BELMR 69/34.5 kV BK#5 | 12 :BRT BUS2 | 201 | 296 | 390.98
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-459 | 12 :BRT BUS2 | 201 | 296 | 390.9
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | NEPTUNE - RAR NEPTUNE | Barrett Bus Tie | 201 | 296 | 390.72
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | LKE SCSS 138 kV P.A.R. | Barrett Bus Tie | 201 | 296 | 390.57
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | NEPTUNE | Barrett Bus Tie | 201 | 296 | 390.43
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 69-474 | Barrett Bus Tie | 201 | 296 | 390.42
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | JAMCA - LKSUCCESS 903 138 | Barrett Bus Tie | 201 | 296 | 390.29
129202 BARRETT1 138 129233 VLY STRM 138 1 | 11 | 903 | Barrett Bus Tie | 201 | 296 | 390.29
129202 BARRETT1 138 129233 VLY STRM 138 1 Max | [5 empty] | 445.72
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-291 | 138-292 | 187 | 275 | 332.1
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | 138-291 | 187 | 275 | 330.93
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | 8 :VST BUS1 | 187 | 275 | 328.85
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 187 | 275 | 328.81
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 187 | 275 | 327.81
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-292 | Valley Stream Bus Tie | 187 | 275 | 159.5
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-261 | 138-262 | 187 | 275 | 127.63
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | 138-262 | 138-261 | 187 | 275 | 124.31
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Northport 4 | Base Case | 187 | 275 | 116.75
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Ruland 3 | Base Case | 187 | 275 | 116.67
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | NEPTUNE - RAR NEPTUNE | Base Case | 187 | 275 | 114.29
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | GEN: OSW Holbrook 1 | Base Case | 187 | 275 | 114.14
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | NEPTUNE | Base Case | 187 | 275 | 113.73
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | Northport-Norwalk NNC-3C | Base Case | 187 | 275 | 113.54
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | NNC-3C | Base Case | 187 | 275 | 113.54
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | NEWBRGE 345/138 Bank #2 | Base Case | 187 | 275 | 113.34
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | DNWDIE - SHORERD 345 Y50 | Base Case | 187 | 275 | 113.07
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | VLY STRM 138/69 Bank #6 | Base Case | 187 | 275 | 105.27
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | VLY STRM 138 kV P.A.R. | Base Case | 187 | 275 | 103.84
129203 BARRETT2 138 129204 BRRT PH 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Base Case | 187 | 275 | 103.79
129203 BARRETT2 138 129204 BRRT PH 138 1 Max | [5 empty] | 332.1
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | Base Case | 196 | 294 | 459.15
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | Base Case | 196 | 294 | 450.11
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | 138-291 | 196 | 294 | 364.18
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | 138-291 | 196 | 294 | 364.18
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | BARRETT 138 kV P.A.R. | 196 | 294 | 364.03
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 138-459 | 196 | 294 | 364.02
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 129204 BRRT PH 138 129276 FREEPORT 138 1 | 196 | 294 | 364.02
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | 8 :VST BUS1 | 196 | 294 | 358.19
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | 8 :VST BUS1 | 196 | 294 | 358.14
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-459 | VLY STRM 138/69 kV Bank #5 | 196 | 294 | 357.96
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | BARRETT 138 kV P.A.R. | VLY STRM 138/69 kV Bank #5 | 196 | 294 | 357.91
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 129204 BRRT PH 138 129276 FREEPORT 138 1 | 196 | 294 | 357.29
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 138-459 | 196 | 294 | 357.29
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | BARRETT 138 kV P.A.R. | 196 | 294 | 357.21
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-461 | 138-291 | 196 | 294 | 347.76
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 138-461 | 196 | 294 | 347.08
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-291 | 129202 BARRETT1 138 129205 BRTGT1-8 138 1 | 196 | 294 | 343.27
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-461 | 8 :VST BUS1 | 196 | 294 | 341.87
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | 138-461 | VLY STRM 138/69 kV Bank #5 | 196 | 294 | 341.63
129203 BARRETT2 138 129234 VLY STRM2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 138-461 | 196 | 294 | 340.6
129203 BARRETT2 138 129234 VLY STRM2 138 2 Max | [5 empty] | 459.15
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-291 | 138-292 | 187 | 275 | 325.7
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | 138-291 | 187 | 275 | 324.54
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | 8 :VST BUS1 | 187 | 275 | 322.51
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 187 | 275 | 322.47
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 187 | 275 | 321.49
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-292 | Valley Stream Bus Tie | 187 | 275 | 156.39
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-261 | 138-262 | 187 | 275 | 125.19
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | 138-262 | 138-261 | 187 | 275 | 121.99
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Ruland 3 | Base Case | 187 | 275 | 114.64
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Northport 4 | Base Case | 187 | 275 | 114.49
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | NEPTUNE - RAR NEPTUNE | Base Case | 187 | 275 | 112.45
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | NEWBRGE 345/138 Bank #2 | Base Case | 187 | 275 | 112.26
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | NNC-3C | Base Case | 187 | 275 | 112.12
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | Northport-Norwalk NNC-3C | Base Case | 187 | 275 | 112.12
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | GEN: OSW Holbrook 1 | Base Case | 187 | 275 | 112.11
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | NEPTUNE | Base Case | 187 | 275 | 111.98
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | DNWDIE - SHORERD 345 Y50 | Base Case | 187 | 275 | 111.57
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | VLY STRM 138/69 Bank #6 | Base Case | 187 | 275 | 104.24
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | VLY STRM 138 kV P.A.R. | Base Case | 187 | 275 | 102.97
129204 BRRT PH 138 129276 FREEPORT 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Base Case | 187 | 275 | 102.95
129204 BRRT PH 138 129276 FREEPORT 138 1 Max | [5 empty] | 325.7
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | DNWDIE - SHORERD 345 Y50 | Y49 | 274 | 366 | 236.18
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | LKE SCSS 138 kV P.A.R. | Y49 | 274 | 366 | 158.43
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | JAMCA - LKSUCCESS 903 138 | Y49 | 274 | 366 | 157.62
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 903 | Y49 | 274 | 366 | 157.62
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | SHORE RD 345/138 Bank #1 | Y49 | 274 | 366 | 146.34
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | SHORE RD 345/138 Bank #2 | Y49 | 274 | 366 | 145.18
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | LKE SCSS 138/69 Bank #6 | Y49 | 274 | 366 | 139.6
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | BELMR 69/34.5 kV BK#5 | Y49 | 274 | 366 | 139.49
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 69-481 | Y49 | 274 | 366 | 138.97
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 69-372 | Y49 | 274 | 366 | 138.93
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 69-371 | Y49 | 274 | 366 | 138.89
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 69-366 364 | Y49 | 274 | 366 | 138.82
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | LKE SCSS 138/69 Bank #5 | Y49 | 274 | 366 | 138.56
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | GLNWD SO 138/69 kV Bank #6 | Y49 | 274 | 366 | 138.15
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 69-574 | Y49 | 274 | 366 | 138.07
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | GLNWD NO 138/69 Bank #5 | Y49 | 274 | 366 | 137.99
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 69-576 | Y49 | 274 | 366 | 137.48
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 69-533 | Y49 | 274 | 366 | 137.35
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 69-266 | Y49 | 274 | 366 | 136.95
129233 VLY STRM 138 129235 V STRM P 138 1 | 11 | 69-474 | Y49 | 274 | 366 | 136.94
129233 VLY STRM 138 129235 V STRM P 138 1 Max | [5 empty] | 236.18
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 12 :BRT BUS2 | 214 | 298 | 177.61
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-261 | 214 | 298 | 174.01
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-459 | 138-261 | 214 | 298 | 170.45
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | BARRETT 138 kV P.A.R. | 138-261 | 214 | 298 | 170.43
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | Base Case | 214 | 298 | 170.15
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | BARRETT 138 kV P.A.R. | 214 | 298 | 168.83
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 129204 BRRT PH 138 129276 FREEPORT 138 1 | 214 | 298 | 168.82
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 138-459 | 214 | 298 | 168.82
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | VLY STRM 138/69 kV Bank #5 | 214 | 298 | 163.42
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | VLY STRM 138/69 Bank #6 | 214 | 298 | 163.07
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | VSBUS2 | 214 | 298 | 162.6
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Base Case | 214 | 298 | 160.79
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 8 :VST BUS1 | 214 | 298 | 159.53
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-461 | 138-261 | 214 | 298 | 157.98
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-459 | Base Case | 214 | 298 | 156.13
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | BARRETT 138 kV P.A.R. | Base Case | 214 | 298 | 156.05
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 138-461 | 214 | 298 | 155.06
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | 1103 RUL_138_OSW3 138 129361 RULND RD 138 1 | 214 | 298 | 153.52
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | 138-261 | GEN: OSW Ruland 3 | 214 | 298 | 153.48
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 | 11 | VLY STRM 138/69 Bank #6 | VLY STRM 138/69 kV Bank #5 | 214 | 298 | 152.77
129234 VLY STRM2 138 129271 E.G.C.-2 138 1 Max | [5 empty] | 177.61
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | Base Case | 280 | 442 | 122.9
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 12 :BRT BUS2 | 280 | 442 | 111.18
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 129204 BRRT PH 138 129276 FREEPORT 138 1 | 280 | 442 | 106.34
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | 138-459 | 280 | 442 | 106.34
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | BARRETT 138 kV P.A.R. | 280 | 442 | 106.3
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | VLY STRM 138/69 kV Bank #5 | 138-262 | 280 | 442 | 105.23
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-459 | 138-262 | 280 | 442 | 104.13
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | BARRETT 138 kV P.A.R. | 138-262 | 280 | 442 | 104.04
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 | 11 | 138-262 | VLY STRM 138/69 kV Bank #5 | 280 | 442 | 103.24
129234 VLY STRM2 138 129271 E.G.C.-2 138 2 Max | [5 empty] | 122.9
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | DNWDIE - SHORERD 345 Y50 | Y49 | 253 | 346 | 228.24
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | SPRNBRK - EGC 345 Y49 | Y50 | 253 | 346 | 197.54
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-362 | Y50 | 253 | 346 | 158.22
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-366 | Y50 | 253 | 346 | 157.44
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-364 | Y50 | 253 | 346 | 155.67
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-365 | Y50 | 253 | 346 | 144.83
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-361 | Y50 | 253 | 346 | 143.91
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | DNWDIE - SHORERD 345 Y50 | Y49 | 253 | 346 | 143.31
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 138-363 | Y50 | 253 | 346 | 143
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | E.G.C. 345 kV P.A.R. #2 | Y50 | 253 | 346 | 137.93
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | VLY STRM 138 kV P.A.R. | Y50 | 253 | 346 | 137.4
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | 901 L&M | Y50 | 253 | 346 | 136.92
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Y50 | 253 | 346 | 136.92
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Y49 | 253 | 346 | 136.71
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | E.G.C. 345 kV P.A.R. #1 | Y50 | 253 | 346 | 135.46
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | EGC REA | Y50 | 253 | 346 | 135.46
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Y50 | 253 | 346 | 135.26
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | VLY STRM 138 kV P.A.R. | Y49 | 253 | 346 | 134.4
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | NNC-3C | Y50 | 253 | 346 | 133.8
129248 L SUCS2 138 129249 L SUCSPH 138 1 | 11 | Northport-Norwalk NNC-3C | Y50 | 253 | 346 | 133.8
129248 L SUCS2 138 129249 L SUCSPH 138 1 Max | [5 empty] | 228.24
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | Y49 | 263 | 303 | 472.51
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | Y49 | 263 | 303 | 468.39
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-364 | Y49 | 263 | 303 | 457.91
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | Base Case | 263 | 303 | 368.43
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | Base Case | 263 | 303 | 366.47
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-364 | Base Case | 263 | 303 | 359.71
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Y49 | 263 | 303 | 353.07
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Y49 | 263 | 303 | 343.36
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 901 L&M | Y49 | 263 | 303 | 343.36
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | VLY STRM 138 kV P.A.R. | Y49 | 263 | 303 | 343.25
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | NEWBUS2 | 263 | 303 | 342.78
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | Y49 | 263 | 303 | 341.86
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | VLY STRM 138/69 kV Bank #5 | 263 | 303 | 339.7
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | Y49 | 263 | 303 | 338.92
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | VLY STRM 138/69 kV Bank #5 | 263 | 303 | 338.39
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | 8 :VST BUS1 | 263 | 303 | 338.39
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | NEWBUS2 | 263 | 303 | 337.61
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-362 | EGCBUS1 | 263 | 303 | 337.05
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-366 | 8 :VST BUS1 | 263 | 303 | 337.04
129265 CARLE PL 138 129270 E.G.C. 138 1 | 11 | 138-364 | NEWBUS2 | 263 | 303 | 334.83
129265 CARLE PL 138 129270 E.G.C. 138 1 Max | [5 empty] | 472.51
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | Y49 | 264 | 324 | 422.66
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | Y49 | 264 | 324 | 418.89
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-364 | Y49 | 264 | 324 | 409.1
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | Base Case | 264 | 324 | 344.74
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | Base Case | 264 | 324 | 342.83
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-364 | Base Case | 264 | 324 | 336.13
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Y49 | 264 | 324 | 311.1
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | NEWBUS2 | 264 | 324 | 302.27
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 901 L&M | Y49 | 264 | 324 | 302.18
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Y49 | 264 | 324 | 302.18
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | VLY STRM 138 kV P.A.R. | Y49 | 264 | 324 | 302.09
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | Y49 | 264 | 324 | 301.42
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | VLY STRM 138/69 kV Bank #5 | 264 | 324 | 299.36
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | Y49 | 264 | 324 | 298.71
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | VLY STRM 138/69 kV Bank #5 | 264 | 324 | 298.17
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | 8 :VST BUS1 | 264 | 324 | 298.15
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | NEWBUS2 | 264 | 324 | 297.41
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-362 | EGCBUS1 | 264 | 324 | 296.97
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-366 | 8 :VST BUS1 | 264 | 324 | 296.91
129265 CARLE PL 138 129283 GLNWD SO 138 1 | 11 | 138-364 | NEWBUS2 | 264 | 324 | 294.82
129265 CARLE PL 138 129283 GLNWD SO 138 1 Max | [5 empty] | 422.66
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | E.G.C. 345 kV P.A.R. #2 | Y49 | 450 | 540 | 224.48
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | E.G.C. 345 kV P.A.R. #2 | 450 | 540 | 135.73
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 450 | 540 | 135.73
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 128823 E.G.C.-2 345 128825 EGC PAR 345 1 | 450 | 540 | 135.73
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | Base Case | 450 | 540 | 111.01
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | GEN: OSW Northport 4 | Y49 | 450 | 540 | 110.38
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | GEN: OSW Ruland 3 | Y49 | 450 | 540 | 110.22
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | GEN: OSW Holbrook 1 | Y49 | 450 | 540 | 110.18
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | LKE SCSS 138 kV P.A.R. | Y49 | 450 | 540 | 109.98
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | 903 | Y49 | 450 | 540 | 109.98
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | JAMCA - LKSUCCESS 903 138 | Y49 | 450 | 540 | 109.98
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | NEPTUNE - RAR NEPTUNE | Y49 | 450 | 540 | 109.9
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | NEPTUNE | Y49 | 450 | 540 | 109.84
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | GEN: OSW Holbrook 2 | Y49 | 450 | 540 | 109.55
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | GEN: OSW Barret 2 | Y49 | 450 | 540 | 109.55
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | Y49 | 450 | 540 | 109.55
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | NB REA | Y49 | 450 | 540 | 109.39
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | BP SOLAR | Y49 | 450 | 540 | 109.34
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | LKE SCSS 138/69 Bank #6 | Y49 | 450 | 540 | 109.34
129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 11 | SYOSSET 138/69 Bank #5 | Y49 | 450 | 540 | 109.33
129270 E.G.C. 138 128822 E.G.C.-1 345 1 Max | [5 empty] | 224.48
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | Y49 | 263 | 303 | 447.77
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-361 | Y49 | 263 | 303 | 446.87
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-363 | Y49 | 263 | 303 | 441.17
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Y49 | 263 | 303 | 336.42
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-361 | Base Case | 263 | 303 | 331.26
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Y49 | 263 | 303 | 327.01
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 901 L&M | Y49 | 263 | 303 | 327.01
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | VLY STRM 138 kV P.A.R. | Y49 | 263 | 303 | 326.9
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | Base Case | 263 | 303 | 326.41
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-363 | Base Case | 263 | 303 | 323.6
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-361 | Y49 | 263 | 303 | 323.02
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 138-361 | 263 | 303 | 321.9
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-365 | Y49 | 263 | 303 | 317.5
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 138-365 | 263 | 303 | 316.62
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 35 :GLNSO BUS | 263 | 303 | 316.62
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-363 | Y49 | 263 | 303 | 313.76
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 138-363 | 263 | 303 | 313.4
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | 138-361 | NEWBUS2 | 263 | 303 | 309.15
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | NNC-3C | Y49 | 263 | 303 | 307.44
129270 E.G.C. 138 129288 ROSLYN 138 1 | 11 | Northport-Norwalk NNC-3C | Y49 | 263 | 303 | 307.44
129270 E.G.C. 138 129288 ROSLYN 138 1 Max | [5 empty] | 447.77
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-463 | 138-465 | 207 | 287 | 231.03
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | 138-463 | 207 | 287 | 230.77
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | Base Case | 207 | 287 | 215.12
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-463 | Base Case | 207 | 287 | 214.11
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-463 | 138-467 | 207 | 287 | 203.81
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-467 | 138-463 | 207 | 287 | 203.24
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-465 | 138-467 | 207 | 287 | 201.12
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-467 | 138-465 | 207 | 287 | 200.83
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-467 | Base Case | 207 | 287 | 195.26
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-291 | 138-292 | 207 | 287 | 189.55
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 138-291 | 207 | 287 | 189.29
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 207 | 287 | 187.25
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 8 :VST BUS1 | 207 | 287 | 186.63
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 207 | 287 | 186.35
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW EGC 5 | Base Case | 207 | 287 | 172.28
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | NEWBRGE 138/69 Bank #6 | Base Case | 207 | 287 | 172.05
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | NB REA | Base Case | 207 | 287 | 171.99
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | HVDC: HQ Rainey 7 | Base Case | 207 | 287 | 171.2
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW W49 Street 5 | Base Case | 207 | 287 | 171.2
129270 E.G.C. 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW Farragut 3 | Base Case | 207 | 287 | 171.19
129270 E.G.C. 138 129310 NEWBRGE 138 1 Max | [5 empty] | 231.03
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | 138-463 | 201 | 295 | 217.76
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-463 | 138-462 | 201 | 295 | 217.69
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | Base Case | 201 | 295 | 216.21
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-463 | Base Case | 201 | 295 | 212.31
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-467 | Base Case | 201 | 295 | 194.23
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-462 | 138-467 | 201 | 295 | 193.52
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-467 | 138-462 | 201 | 295 | 192.91
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-463 | 138-467 | 201 | 295 | 191.17
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-467 | 138-463 | 201 | 295 | 190.64
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-291 | 138-292 | 201 | 295 | 177.67
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-292 | 138-291 | 201 | 295 | 177.43
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 201 | 295 | 175.61
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-292 | 8 :VST BUS1 | 201 | 295 | 175.02
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 201 | 295 | 174.76
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | NB REA | Base Case | 201 | 295 | 170.94
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | NEWBRGE 138/69 Bank #6 | Base Case | 201 | 295 | 170.79
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | GEN: OSW EGC 5 | Base Case | 201 | 295 | 170.77
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | GEN: OSW W49 Street 5 | Base Case | 201 | 295 | 170.07
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | HVDC: HQ Rainey 7 | Base Case | 201 | 295 | 170.07
129270 E.G.C. 138 129310 NEWBRGE 138 3 | 11 | GEN: OSW Farragut 4 | Base Case | 201 | 295 | 170.06
129270 E.G.C. 138 129310 NEWBRGE 138 3 Max | [5 empty] | 217.76
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | E.G.C. 345 kV P.A.R. #1 | Y49 | 450 | 540 | 224.35
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | EGC REA | Y49 | 450 | 540 | 224.35
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | EGC REA | 450 | 540 | 136.79
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | E.G.C. 345 kV P.A.R. #1 | 450 | 540 | 136.79
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 33 :EGC BUS2 | 450 | 540 | 136.79
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 129270 E.G.C. 138 128822 E.G.C.-1 345 1 | 450 | 540 | 136.79
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | 128822 E.G.C.-1 345 128825 EGC PAR 345 1 | 450 | 540 | 136.79
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | Base Case | 450 | 540 | 113.4
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW Northport 4 | Y49 | 450 | 540 | 108.38
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW Ruland 3 | Y49 | 450 | 540 | 108.22
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW Holbrook 1 | Y49 | 450 | 540 | 108.14
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | NEPTUNE - RAR NEPTUNE | Y49 | 450 | 540 | 107.81
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | NEPTUNE | Y49 | 450 | 540 | 107.75
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW Barret 2 | Y49 | 450 | 540 | 107.55
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | GEN: OSW Holbrook 2 | Y49 | 450 | 540 | 107.55
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | 138-364 | Y49 | 450 | 540 | 107.3
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | 138-366 | Y49 | 450 | 540 | 107.28
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | 138-362 | Y49 | 450 | 540 | 107.28
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | DNWDIE - SHORERD 345 Y50 | Y49 | 450 | 540 | 107.24
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 | 11 | SPRNBRK - DUNWDIE 345 W75 | Y49 | 450 | 540 | 107.21
129271 E.G.C.-2 138 128823 E.G.C.-2 345 1 Max | [5 empty] | 224.35
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | Base Case | 174 | 293 | 249.32
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-465 | Base Case | 174 | 293 | 245.87
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-467 | Base Case | 174 | 293 | 226.1
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | 138-465 | 174 | 293 | 223.85
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-465 | 138-462 | 174 | 293 | 223.54
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GEN: OSW EGC 5 | Base Case | 174 | 293 | 198.06
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-462 | 138-467 | 174 | 293 | 197.13
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | NB REA | Base Case | 174 | 293 | 196.99
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | NEWBRGE 138/69 Bank #6 | Base Case | 174 | 293 | 196.93
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | DNWDIE - SHORERD 345 Y50 | Base Case | 174 | 293 | 196.59
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-467 | 138-462 | 174 | 293 | 196.54
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GEN: OSW W49 Street 5 | Base Case | 174 | 293 | 195.52
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | HVDC: HQ Rainey 7 | Base Case | 174 | 293 | 195.52
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GEN: OSW Farragut 4 | Base Case | 174 | 293 | 195.51
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GEN: OSW Farragut 3 | Base Case | 174 | 293 | 195.51
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 69-533 | Base Case | 174 | 293 | 195.42
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | GEN: OSW Astoria 2 | Base Case | 174 | 293 | 194.73
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | SYOSSET 138/69 Bank #5 | Base Case | 174 | 293 | 192.81
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-465 | 138-467 | 174 | 293 | 192.07
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 | 11 | 138-467 | 138-465 | 174 | 293 | 191.84
129271 E.G.C.-2 138 129310 NEWBRGE 138 2 Max | [5 empty] | 249.32
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-462 | Base Case | 253 | 460 | 126.44
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-463 | Base Case | 253 | 460 | 126.2
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-465 | Base Case | 253 | 460 | 125.04
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-462 | 138-465 | 253 | 460 | 105.14
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-465 | 138-462 | 253 | 460 | 104.99
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-462 | 138-463 | 253 | 460 | 104.65
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-463 | 138-462 | 253 | 460 | 104.62
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-463 | 138-465 | 253 | 460 | 104.07
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 | 11 | 138-465 | 138-463 | 253 | 460 | 103.94
129271 E.G.C.-2 138 129310 NEWBRGE 138 4 Max | [5 empty] | 126.44
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-291 | 138-292 | 235 | 305 | 275.76
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 138-291 | 235 | 305 | 274.72
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | 8 :VST BUS1 | 235 | 305 | 272.87
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | VLY STRM 138/69 kV Bank #5 | 235 | 305 | 272.84
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | 138-292 | 235 | 305 | 271.94
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | 138-292 | Valley Stream Bus Tie | 235 | 305 | 123.32
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW Barret 2 | Base Case | 235 | 305 | 103.15
129276 FREEPORT 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW Holbrook 2 | Base Case | 235 | 305 | 103.15
129276 FREEPORT 138 129310 NEWBRGE 138 1 Max | [5 empty] | 275.76
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | Y49 | 264 | 324 | 405.53
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-361 | Y49 | 264 | 324 | 404.63
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-363 | Y49 | 264 | 324 | 399.39
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-361 | Base Case | 264 | 324 | 314.86
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | Base Case | 264 | 324 | 310.08
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-363 | Base Case | 264 | 324 | 307.32
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Y49 | 264 | 324 | 301.38
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Y49 | 264 | 324 | 292.67
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 901 L&M | Y49 | 264 | 324 | 292.67
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | VLY STRM 138 kV P.A.R. | Y49 | 264 | 324 | 292.58
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-361 | Y49 | 264 | 324 | 289.57
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 138-361 | 264 | 324 | 288.56
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-365 | Y49 | 264 | 324 | 284.48
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 35 :GLNSO BUS | 264 | 324 | 283.66
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 138-365 | 264 | 324 | 283.66
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-363 | Y49 | 264 | 324 | 281.02
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 138-363 | 264 | 324 | 280.67
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | 138-361 | NEWBUS2 | 264 | 324 | 276.68
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 264 | 324 | 275.07
129281 GLNWD GT 138 129282 GLNWD NO 138 1 | 11 | NNC-3C | Y49 | 264 | 324 | 274.52
129281 GLNWD GT 138 129282 GLNWD NO 138 1 Max | [5 empty] | 405.53
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | Y49 | 264 | 324 | 405.55
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-361 | Y49 | 264 | 324 | 404.63
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-363 | Y49 | 264 | 324 | 399.4
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-361 | Base Case | 264 | 324 | 314.88
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | Base Case | 264 | 324 | 310.11
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-363 | Base Case | 264 | 324 | 307.35
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Y49 | 264 | 324 | 301.39
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 901 L&M | Y49 | 264 | 324 | 292.68
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Y49 | 264 | 324 | 292.68
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | VLY STRM 138 kV P.A.R. | Y49 | 264 | 324 | 292.59
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-361 | Y49 | 264 | 324 | 289.59
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 138-361 | 264 | 324 | 288.58
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-365 | Y49 | 264 | 324 | 284.51
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 35 :GLNSO BUS | 264 | 324 | 283.67
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 138-365 | 264 | 324 | 283.67
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-363 | Y49 | 264 | 324 | 281.04
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 138-363 | 264 | 324 | 280.69
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | 138-361 | NEWBUS2 | 264 | 324 | 276.67
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 264 | 324 | 275.09
129281 GLNWD GT 138 129288 ROSLYN 138 1 | 11 | Northport-Norwalk NNC-3C | Y49 | 264 | 324 | 274.54
129281 GLNWD GT 138 129288 ROSLYN 138 1 Max | [5 empty] | 405.55
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | Y49 | 285 | 366 | 383.14
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-361 | Y49 | 285 | 366 | 377.38
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-363 | Y49 | 285 | 366 | 372.25
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-361 | Base Case | 285 | 366 | 299.04
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | Base Case | 285 | 366 | 296.13
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-363 | Base Case | 285 | 366 | 291.24
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Y49 | 285 | 366 | 274.09
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Y49 | 285 | 366 | 268.04
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 901 L&M | Y49 | 285 | 366 | 268.04
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | VLY STRM 138 kV P.A.R. | Y49 | 285 | 366 | 267.93
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-361 | Y49 | 285 | 366 | 265.33
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 138-361 | 285 | 366 | 264.66
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-365 | Y49 | 285 | 366 | 262.61
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 35 :GLNSO BUS | 285 | 366 | 262.22
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 138-365 | 285 | 366 | 262.22
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 285 | 366 | 261.59
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | SPRNBRK - EGC 345 Y49 | 138-363 | 285 | 366 | 256.9
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | 138-363 | Y49 | 285 | 366 | 256.89
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | Northport-Norwalk NNC-3C | Y49 | 285 | 366 | 250.54
129282 GLNWD NO 138 129293 SHORE RD 138 1 | 11 | NNC-3C | Y49 | 285 | 366 | 250.54
129282 GLNWD NO 138 129293 SHORE RD 138 1 Max | [5 empty] | 383.14
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | Y49 | 264 | 324 | 449.37
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | Y49 | 264 | 324 | 439.45
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-364 | Y49 | 264 | 324 | 428.64
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | Base Case | 264 | 324 | 354.72
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | Base Case | 264 | 324 | 354.01
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-364 | Base Case | 264 | 324 | 344.47
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | VLY STRM 138/69 kV Bank #5 | Y49 | 264 | 324 | 318.75
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 901 L&M | Y49 | 264 | 324 | 311.62
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | JAMCA - VLLYSTRM 901L&M 138 | Y49 | 264 | 324 | 311.62
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | VLY STRM 138 kV P.A.R. | Y49 | 264 | 324 | 311.5
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | Y49 | 264 | 324 | 311.15
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | Y49 | 264 | 324 | 310.96
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | VLY STRM 138/69 kV Bank #5 | 264 | 324 | 307.24
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | VLY STRM 138/69 kV Bank #5 | 264 | 324 | 306.28
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | 8 :VST BUS1 | 264 | 324 | 305.82
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-362 | 8 :VST BUS1 | 264 | 324 | 304.94
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-364 | Y49 | 264 | 324 | 302.68
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | LKS BUS2 | 264 | 324 | 302.13
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | VLY STRM 138 kV P.A.R. | 264 | 324 | 300.69
129283 GLNWD SO 138 129294 SHORE RD2 138 1 | 11 | 138-366 | 901 L&M | 264 | 324 | 300.57
129283 GLNWD SO 138 129294 SHORE RD2 138 1 Max | [5 empty] | 449.37
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | Base Case | 333 | 490 | 101.68
129305 LCST GRV 138 129310 NEWBRGE 138 1 | 11 | GEN: OSW Holbrook 1 | 74 :NPT BUS2 | 333 | 490 | 101.51
129305 LCST GRV 138 129310 NEWBRGE 138 1 Max | [5 empty] | 101.68
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | 138-567 | 240 | 278 | 125.85
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | 138-562 | 240 | 278 | 124.08
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-562 | 240 | 278 | 117.56
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-567 | 240 | 278 | 116.66
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-564 | 138-562 | 240 | 278 | 114.36
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-564 | 138-567 | 240 | 278 | 113.45
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | 75 :NPT BUS3 | 240 | 278 | 113.4
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-562 | NRTHPRT P.A.R. #2 (Bus) | 240 | 278 | 113.31
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | 75 :NPT BUS3 | 240 | 278 | 112.23
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-567 | NRTHPRT P.A.R. #2 (Bus) | 240 | 278 | 112.16
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-563 | 138-562 | 240 | 278 | 111.69
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-563 | 138-567 | 240 | 278 | 110.76
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-564 | 240 | 278 | 110.3
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-564 | 75 :NPT BUS3 | 240 | 278 | 108.74
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-564 | NRTHPRT P.A.R. #2 (Bus) | 240 | 278 | 108.65
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 240 | 278 | 108.32
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-563 | 240 | 278 | 108.32
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 240 | 278 | 108.31
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-563 | 75 :NPT BUS3 | 240 | 278 | 106.44
129310 NEWBRGE 138 129361 RULND RD 138 1 | 11 | 138-563 | NRTHPRT P.A.R. #2 (Bus) | 240 | 278 | 106.34
129310 NEWBRGE 138 129361 RULND RD 138 1 Max | [5 empty] | 125.85
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | 138-567 | 240 | 278 | 125.85
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | 138-561 | 240 | 278 | 124.07
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-561 | 240 | 278 | 117.56
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-567 | 240 | 278 | 116.66
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-564 | 138-561 | 240 | 278 | 114.36
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-564 | 138-567 | 240 | 278 | 113.44
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | 75 :NPT BUS3 | 240 | 278 | 113.4
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-561 | NRTHPRT P.A.R. #2 (Bus) | 240 | 278 | 113.3
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | 75 :NPT BUS3 | 240 | 278 | 112.22
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-567 | NRTHPRT P.A.R. #2 (Bus) | 240 | 278 | 112.16
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-563 | 138-561 | 240 | 278 | 111.68
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-563 | 138-567 | 240 | 278 | 110.75
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-564 | 240 | 278 | 110.29
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-564 | 75 :NPT BUS3 | 240 | 278 | 108.73
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-564 | NRTHPRT P.A.R. #2 (Bus) | 240 | 278 | 108.64
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | NRTHPRT P.A.R. #2 (Bus) | 129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 240 | 278 | 108.31
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | NRTHPRT P.A.R. #2 (Bus) | 129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 240 | 278 | 108.31
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-563 | 240 | 278 | 108.31
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-563 | 75 :NPT BUS3 | 240 | 278 | 106.44
129310 NEWBRGE 138 129361 RULND RD 138 2 | 11 | 138-563 | NRTHPRT P.A.R. #2 (Bus) | 240 | 278 | 106.34
129310 NEWBRGE 138 129361 RULND RD 138 2 Max | [5 empty] | 125.85
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-562 | 138-561 | 243 | 324 | 107.66
129310 NEWBRGE 138 129361 RULND RD 138 3 | 11 | 138-561 | 138-562 | 243 | 324 | 107.66
129310 NEWBRGE 138 129361 RULND RD 138 3 Max | [5 empty] | 107.66
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-677 | 138-681 | 249 | 356 | 113.28
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-677 | 80 :ELD BUS1 | 249 | 356 | 106.74
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-677 | ELWOOD 138/69 kV Bank #3 | 249 | 356 | 106.74
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-677 | Northport Bus Tie No.1-1 | 249 | 356 | 102.28
129315 SYOSSET 138 129333 GRENLAWN 138 1 | 11 | 138-677 | 72 :NPT BUS1-2 | 249 | 356 | 101.63
129315 SYOSSET 138 129333 GRENLAWN 138 1 Max | [5 empty] | 113.28
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-677 | 76 :NPT BUS4 | 249 | 356 | 110.81
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-677 | 138-678 | 249 | 356 | 110.81
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-677 | 81 :ELD BUS2 | 249 | 356 | 109.7
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-677 | 138-673 | 249 | 356 | 107.85
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-677 | Northport Bus Tie No.1-1 | 249 | 356 | 103.47
129315 SYOSSET 138 129351 OAKWOOD 138 1 | 11 | 138-677 | 72 :NPT BUS1-2 | 249 | 356 | 102.98
129315 SYOSSET 138 129351 OAKWOOD 138 1 Max | [5 empty] | 110.81
129328 ELWOOD 1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 72 :NPT BUS1-2 | 362 | 545 | 108.84
129328 ELWOOD 1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | Northport Bus Tie No.1-1 | 362 | 545 | 108.69
129328 ELWOOD 1 138 129342 NRTHPRT2 138 1 | 11 | 138-678 | Base Case | 362 | 545 | 107.86
129328 ELWOOD 1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 138-678 | 362 | 545 | 106.58
129328 ELWOOD 1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 76 :NPT BUS4 | 362 | 545 | 106.58
129328 ELWOOD 1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 81 :ELD BUS2 | 362 | 545 | 105.85
129328 ELWOOD 1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 138-673 | 362 | 545 | 104.53
129328 ELWOOD 1 138 129342 NRTHPRT2 138 1 | 11 | 138-673 | Base Case | 362 | 545 | 103.12
129328 ELWOOD 1 138 129342 NRTHPRT2 138 1 Max | [5 empty] | 108.84
129329 ELWOOD 2 138 129333 GRENLAWN 138 1 | 11 | 138-677 | 138-681 | 366 | 482 | 113.03
129329 ELWOOD 2 138 129333 GRENLAWN 138 1 | 11 | 138-677 | 80 :ELD BUS1 | 366 | 482 | 110.35
129329 ELWOOD 2 138 129333 GRENLAWN 138 1 | 11 | 138-677 | ELWOOD 138/69 kV Bank #3 | 366 | 482 | 110.35
129329 ELWOOD 2 138 129333 GRENLAWN 138 1 | 11 | 138-677 | Northport Bus Tie No.1-1 | 366 | 482 | 110.04
129329 ELWOOD 2 138 129333 GRENLAWN 138 1 | 11 | 138-677 | 72 :NPT BUS1-2 | 366 | 482 | 109.94
129329 ELWOOD 2 138 129333 GRENLAWN 138 1 Max | [5 empty] | 113.03
129329 ELWOOD 2 138 129342 NRTHPRT2 138 1 | 11 | ELWOOD 138/69 kV Bank #3 | Base Case | 362 | 545 | 106.17
129329 ELWOOD 2 138 129342 NRTHPRT2 138 1 | 11 | 138-681 | Base Case | 362 | 545 | 103.68
129329 ELWOOD 2 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 138-681 | 362 | 545 | 103.38
129329 ELWOOD 2 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 80 :ELD BUS1 | 362 | 545 | 101
129329 ELWOOD 2 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | ELWOOD 138/69 kV Bank #3 | 362 | 545 | 101
129329 ELWOOD 2 138 129342 NRTHPRT2 138 1 Max | [5 empty] | 106.17
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | GEN: OSW Holbrook 1 | PILGRIM 138/69 Bank #4 | 264 | 324 | 143.69
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | GEN: OSW Holbrook 1 | 68 : PIL BUS2 | 264 | 324 | 143.69
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | GEN: OSW Holbrook 1 | 138-881 | 264 | 324 | 136.58
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | GEN: OSW Holbrook 1 | 138-881 NEW | 264 | 324 | 132.72
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | GEN: OSW Holbrook 1 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 264 | 324 | 102.06
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | GEN: OSW Holbrook 1 | 138-882 | 264 | 324 | 101.37
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | GEN: OSW Holbrook 1 | HOLBROOK 138/69 Bank #2 | 264 | 324 | 101.37
129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 11 | GEN: OSW Holbrook 1 | 108:HOL BUS2 | 264 | 324 | 101.37
129337 HAUPAGUE 138 129356 PILGRM P 138 1 Max | [5 empty] | 143.69
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | GEN: OSW Holbrook 1 | PILGRIM 138/69 Bank #4 | 202 | 281 | 158.94
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | GEN: OSW Holbrook 1 | 68 : PIL BUS2 | 202 | 281 | 158.94
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | GEN: OSW Holbrook 1 | 138-881 | 202 | 281 | 150.78
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | GEN: OSW Holbrook 1 | 138-881 NEW | 202 | 281 | 146.34
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | GEN: OSW Holbrook 1 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 202 | 281 | 111.05
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | GEN: OSW Holbrook 1 | 108:HOL BUS2 | 202 | 281 | 110.27
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | GEN: OSW Holbrook 1 | 138-882 | 202 | 281 | 110.27
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | GEN: OSW Holbrook 1 | HOLBROOK 138/69 Bank #2 | 202 | 281 | 110.27
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 202 | 281 | 108.85
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | PILGRIM 138/69 Bank #4 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 202 | 281 | 108.84
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 202 | 281 | 108.81
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-882 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 202 | 281 | 108.81
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 NEW | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 202 | 281 | 108.8
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | HOLBROOK 138/69 Bank #2 | GEN: OSW Holbrook 1 | 202 | 281 | 108.68
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-882 | GEN: OSW Holbrook 1 | 202 | 281 | 108.68
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 | GEN: OSW Holbrook 1 | 202 | 281 | 108.67
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | PILGRIM 138/69 Bank #4 | GEN: OSW Holbrook 1 | 202 | 281 | 108.66
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 | 11 | 138-881 NEW | GEN: OSW Holbrook 1 | 202 | 281 | 108.62
129337 HAUPAGUE 138 129393 C.ISLIP 138 1 Max | [5 empty] | 158.94
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | PILGRIM 138/69 Bank #3 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 449 | 510 | 132.71
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | PILGRIM 138/69 Bank #3 | GEN: OSW Holbrook 1 | 449 | 510 | 132.59
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 449 | 510 | 132.53
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-882 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 449 | 510 | 132.53
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-882 | GEN: OSW Holbrook 1 | 449 | 510 | 132.41
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | HOLBROOK 138/69 Bank #2 | GEN: OSW Holbrook 1 | 449 | 510 | 132.41
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 449 | 510 | 129.53
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | 138-882 | 449 | 510 | 128.68
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | HOLBROOK 138/69 Bank #2 | 449 | 510 | 128.68
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | 108:HOL BUS2 | 449 | 510 | 128.68
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-871 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 449 | 510 | 125.35
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-871 | GEN: OSW Holbrook 1 | 449 | 510 | 125.24
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-889 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 449 | 510 | 123.38
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | 138-889 | GEN: OSW Holbrook 1 | 449 | 510 | 123.27
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | PILGRIM 138/69 Bank #3 | 449 | 510 | 122.27
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | 63 : PIL BUS1 | 449 | 510 | 122.26
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 449 | 510 | 122
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | C.ISLIP 138/69 Bank #3 | GEN: OSW Holbrook 1 | 449 | 510 | 121.88
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | 138-871 | 449 | 510 | 119.2
129339 KINGS 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | 129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 449 | 510 | 119.2
129339 KINGS 138 129355 PILGRIM 138 1 Max | [5 empty] | 132.71
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | PILGRIM 138/69 Bank #3 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 497 | 545 | 119.42
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | PILGRIM 138/69 Bank #3 | GEN: OSW Holbrook 1 | 497 | 545 | 119.32
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 497 | 545 | 119.26
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-882 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 497 | 545 | 119.26
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | HOLBROOK 138/69 Bank #2 | GEN: OSW Holbrook 1 | 497 | 545 | 119.15
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-882 | GEN: OSW Holbrook 1 | 497 | 545 | 119.15
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | GEN: OSW Holbrook 1 | 129361 RULND RD 138 129421 HOLBROOK 138 1 | 497 | 545 | 116.47
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | GEN: OSW Holbrook 1 | 108:HOL BUS2 | 497 | 545 | 115.67
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | GEN: OSW Holbrook 1 | HOLBROOK 138/69 Bank #2 | 497 | 545 | 115.67
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | GEN: OSW Holbrook 1 | 138-882 | 497 | 545 | 115.67
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-871 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 497 | 545 | 112.56
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-871 | GEN: OSW Holbrook 1 | 497 | 545 | 112.46
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-889 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 497 | 545 | 110.72
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | 138-889 | GEN: OSW Holbrook 1 | 497 | 545 | 110.61
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | GEN: OSW Holbrook 1 | 63 : PIL BUS1 | 497 | 545 | 109.69
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | GEN: OSW Holbrook 1 | PILGRIM 138/69 Bank #3 | 497 | 545 | 109.69
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 497 | 545 | 109.41
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | C.ISLIP 138/69 Bank #3 | GEN: OSW Holbrook 1 | 497 | 545 | 109.3
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | GEN: OSW Holbrook 1 | 129337 HAUPAGUE 138 129356 PILGRM P 138 1 | 497 | 545 | 106.81
129339 KINGS 138 129428 WEST BUS 138 1 | 11 | GEN: OSW Holbrook 1 | 138-871 | 497 | 545 | 106.81
129339 KINGS 138 129428 WEST BUS 138 1 Max | [5 empty] | 119.42
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 72 :NPT BUS1-2 | 396 | 482 | 241.42
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | Northport Bus Tie No.1-1 | 396 | 482 | 241.37
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | Base Case | 396 | 482 | 180.61
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 1102 BAR_138_OSW2 138 129202 BARRETT1 138 1 | 396 | 482 | 159.92
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | GEN: OSW Holbrook 2 | 396 | 482 | 159.9
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | GEN: OSW Barret 2 | 396 | 482 | 159.9
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | Northport Bus Tie Bus 1-2 | 396 | 482 | 157.08
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 78 :NPT BUS1-1 | 396 | 482 | 157.08
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | Northport Bus Tie No.1-2 | 396 | 482 | 157.03
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 73 :NPT BUS1 | 396 | 482 | 157.01
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 138-679 | 396 | 482 | 157.01
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 68 : PIL BUS2 | 396 | 482 | 154.83
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | PILGRIM 138/69 Bank #4 | 396 | 482 | 154.83
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | NEPTUNE | 396 | 482 | 154.44
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 128842 NEPTCONV 345 128847 NWBRG 345 1 | 396 | 482 | 154.44
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 138-564 | 396 | 482 | 154.15
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | NEPTUNE - RAR NEPTUNE | 396 | 482 | 154.11
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 129310 NEWBRGE 138 129324 BETHPAGE 138 1 | 396 | 482 | 152.65
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 129321 BAGATELLE 138 129324 BETHPAGE 138 1 | 396 | 482 | 152.63
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 | 11 | 138-677 | 138-563 | 396 | 482 | 152.63
129341 NRTHPRT1 138 129342 NRTHPRT2 138 1 Max | [5 empty] | 241.42
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | Northport Bus Tie No.1-1 | 387 | 545 | 211.29
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 72 :NPT BUS1-2 | 387 | 545 | 209.42
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | Northport Bus Tie Bus 1-2 | 387 | 545 | 140.3
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 78 :NPT BUS1-1 | 387 | 545 | 140.26
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | Northport Bus Tie No.1-2 | 387 | 545 | 139.24
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 73 :NPT BUS1 | 387 | 545 | 138.84
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-679 | 387 | 545 | 138.83
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 138-681 | Northport Bus Tie No.1-1 | 387 | 545 | 137.6
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | ELWOOD 138/69 kV Bank #3 | Northport Bus Tie No.1-1 | 387 | 545 | 136
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 138-681 | 72 :NPT BUS1-2 | 387 | 545 | 135.63
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 138-678 | Northport Bus Tie No.1-1 | 387 | 545 | 135.39
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | 138-673 | Northport Bus Tie No.1-1 | 387 | 545 | 135.19
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Ruland 3 | Northport Bus Tie No.1-1 | 387 | 545 | 134.99
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | ELWOOD 138/69 kV Bank #3 | 72 :NPT BUS1-2 | 387 | 545 | 134.02
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Farragut 3 | Northport Bus Tie No.1-1 | 387 | 545 | 133.78
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Farragut 4 | Northport Bus Tie No.1-1 | 387 | 545 | 133.78
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | HVDC: HQ Rainey 7 | Northport Bus Tie No.1-1 | 387 | 545 | 133.78
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | GEN: OSW W49 Street 5 | Northport Bus Tie No.1-1 | 387 | 545 | 133.78
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | SPRNBRK - EGC 345 Y49 | Northport Bus Tie No.1-1 | 387 | 545 | 133.72
129341 NRTHPRT1 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Astoria 2 | Northport Bus Tie No.1-1 | 387 | 545 | 133.62
129341 NRTHPRT1 138 129355 PILGRIM 138 1 Max | [5 empty] | 211.29
129344 NRTHPT1 138 129343 NRTHPT P 138 1 | 11 | DNWDIE - SHORERD 345 Y50 | Y49 | 459 | 545 | 148.97
129344 NRTHPT1 138 129343 NRTHPT P 138 1 Max | [5 empty] | 148.97
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-679 | 138-677 | 192 | 295 | 166.08
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-677 | Northport Bus Tie Bus 1-2 | 192 | 295 | 132.84
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-677 | 78 :NPT BUS1-1 | 192 | 295 | 132.73
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-677 | 192 | 295 | 131.03
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-677 | Northport Bus Tie No.1-2 | 192 | 295 | 130.51
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-677 | 73 :NPT BUS1 | 192 | 295 | 129.94
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-677 | 138-679 | 192 | 295 | 129.92
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | NRTHPRT P.A.R. #2 (Bus) | Northport Bus Tie Bus 1-2 | 192 | 295 | 128.43
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | NRTHPRT P.A.R. #2 (Bus) | 78 :NPT BUS1-1 | 192 | 295 | 128.4
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | NRTHPRT P.A.R. #2 (Bus) | Northport Bus Tie No.1-2 | 192 | 295 | 127.47
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | NRTHPRT P.A.R. #2 (Bus) | 73 :NPT BUS1 | 192 | 295 | 127.1
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-679 | 192 | 295 | 127.09
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-677 | NRTHPRT P.A.R. #2 (Bus) | 192 | 295 | 121.55
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-677 | 75 :NPT BUS3 | 192 | 295 | 121.46
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | NRTHPRT P.A.R. #2 (Bus) | Base Case | 192 | 295 | 120.86
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-679 | NRTHPRT P.A.R. #2 (Bus) | 192 | 295 | 119.7
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-679 | 75 :NPT BUS3 | 192 | 295 | 119.6
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-679 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 192 | 295 | 102.56
129344 NRTHPT1 138 129355 PILGRIM 138 3 | 11 | 138-679 | GEN: OSW Holbrook 1 | 192 | 295 | 102.51
129344 NRTHPT1 138 129355 PILGRIM 138 3 Max | [5 empty] | 166.08
129346 NRTHPT3 138 129355 PILGRIM 138 2 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-677 | 392 | 545 | 136.37
129346 NRTHPT3 138 129355 PILGRIM 138 2 | 11 | 138-677 | NRTHPRT P.A.R. #2 (Bus) | 392 | 545 | 126.51
129346 NRTHPT3 138 129355 PILGRIM 138 2 | 11 | 138-677 | 75 :NPT BUS3 | 392 | 545 | 126.41
129346 NRTHPT3 138 129355 PILGRIM 138 2 | 11 | NRTHPRT P.A.R. #2 (Bus) | Base Case | 392 | 545 | 113.82
129346 NRTHPT3 138 129355 PILGRIM 138 2 | 11 | 138-672 | 138-677 | 392 | 545 | 104.46
129346 NRTHPT3 138 129355 PILGRIM 138 2 | 11 | NRTHPRT P.A.R. #2 (Bus) | 138-672 | 392 | 545 | 101.95
129346 NRTHPT3 138 129355 PILGRIM 138 2 Max | [5 empty] | 136.37
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | PILGRIM 138/69 Bank #4 | 300 | 375 | 126.34
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | 68 : PIL BUS2 | 300 | 375 | 126.34
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | 138-881 | 300 | 375 | 120.11
129356 PILGRM P 138 129355 PILGRIM 138 1 | 11 | GEN: OSW Holbrook 1 | 138-881 NEW | 300 | 375 | 116.72
129356 PILGRM P 138 129355 PILGRIM 138 1 Max | [5 empty] | 126.34
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | PILGRIM 138/69 Bank #4 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 396 | 482 | 126.53
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | PILGRIM 138/69 Bank #4 | GEN: OSW Holbrook 1 | 396 | 482 | 126.43
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 396 | 482 | 120.43
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 | GEN: OSW Holbrook 1 | 396 | 482 | 120.33
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 NEW | 1101 HOL_138_OSW1 138 129421 HOLBROOK 138 1 | 396 | 482 | 116.68
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | 138-881 NEW | GEN: OSW Holbrook 1 | 396 | 482 | 116.59
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | GEN: OSW Holbrook 1 | 68 : PIL BUS2 | 396 | 482 | 108.54
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | GEN: OSW Holbrook 1 | PILGRIM 138/69 Bank #4 | 396 | 482 | 108.54
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | GEN: OSW Holbrook 1 | 138-881 | 396 | 482 | 106.52
129361 RULND RD 138 129421 HOLBROOK 138 1 | 11 | GEN: OSW Holbrook 1 | 138-881 NEW | 396 | 482 | 104.56
129361 RULND RD 138 129421 HOLBROOK 138 1 Max | [5 empty] | 126.53

## NConv_SUM_Alt
AnalysisType | Areas | First Level Contingency | Second Level Contingency
N-1-1 | 11 | GEN:CAITH | 11 :BRT BUS1
N-1-1 | 11 | GEN:CAITH | P5_BARRETT_138_R
N-1-1 | 11 | 138-291 | Barrett Bus Tie
N-1-1 | 11 | 138-291 | 12 :BRT BUS2
N-1-1 | 11 | 138-291 | 9 :BRT 1380
N-1-1 | 11 | 138-459 | P5_VALLEYSTREAM_138_M
N-1-1 | 11 | 69-965 | 350:BLL 210
N-1 | 11 | 11 :BRT BUS1
N-1 | 11 | P5_BARRETT_138_R