## Cover Page
ATTACHMENT A. NYISO Power Flow Data Bank Forms
The following forms describe the data contained in the NYISO Power Flow Data Bank.

## Area
Area Data
Area Number | Area Swing Bus | Desired Interchange | Tolerance | Area Name
where:
Area Number |  | LBMP Zone number (number 1 through 11)
Area 1 is LBMP Zone A
Area 2 is LBMP Zone B
Area 3 is LBMP Zone C
Area 4 is LBMP Zone D
Area 5 is LBMP Zone E
Area 6 is LBMP Zone F
Area 7 is LBMP Zone G
Area 8 is LBMP Zone H
Area 9 is LBMP Zone I
Area 10 is LBMP Zone J
Area 11 is LBMP Zone K
Area Swing Bus |  | A generator bus number in a specified area for area
interchange control.
Desired Interchange |  | A desired net interchange of an area entered in MW.
Positive number is for export from an area.
Negative number is for import into an area.
Tolerance |  | Interchange tolerance bandwidth entered in MW.
Area Name |  | LBMP Zonal name (up to 12 characters).
Area 1 is "WEST".
Area 2 is "GENESEE".
Area 3 is "CENTRAL".
Area 4 is "NORTH".
Area 5 is "MOHAWK".
Area 6 is "CAPITAL".
Area 7 is "HUDSON".
Area 8 is "MILLWOOD".
Area 9 is "DUNWOODI".
Area 10 is "NYC".
Area 11 is "L ISLAND".

## Owner
Owner Data
Owner Number |  | Owner Name
where:
Owner Number
141 | Central Hudson Gas & Electric Corporation
142 | Consolidated Edison Company of New York
143 | Long Island Power Authority
144 | New York State Electric & Gas
145 | National Grid
146 | Orange & Rockland
147 | New York Power Authority
148 | Rochester Gas & Electric
149 | TRANSCO
150 | NEXTERA
151 | Alcoa Long Sault
152 | Village of Arcade
153 | Generator
154 | Other
155 | LSPGNY
Owner Name
CENT HUD | Central Hudson Gas & Electric Corporation
CONED | Consolidated Edison Company of New York
LIPA | Long Island Power Authority
NYSEG | New York State Electric & Gas
NGRID | National Grid
O&R | Orange & Rockland
NYPA | New York Power Authority
RGE | Rochester Gas & Electric
TRANSCO | TRANSCO
NEXTERA | NEXTERA
ALCOA_LS | Alcoa Long Sault
ARCADE | Village of Arcade
GEN | Generator
OTHER | Other
LSPGNY | LS Power NY
Note - Connecting TOs' number and name shall be assigned to MPs' equipment
that have in-service date after January 1, 2000.

## Zone
Zone Data
Zone Number | Zone Name
where:
Zone Number |  | LBMP subzone number (145 through 179).
Zone 145 is LBMP subzone number 1. |  |  | Zone 162 is LBMP subzone number 18.
Zone 146 is LBMP subzone number 2. |  |  | Zone 163 is LBMP subzone number 19.
Zone 147 is LBMP subzone number 3. |  |  | Zone 164 is LBMP subzone number 20.
Zone 148 is LBMP subzone number 4. |  |  | Zone 165 is LBMP subzone number 21.
Zone 149 is LBMP subzone number 5. |  |  | Zone 166 is LBMP subzone number 22.
Zone 150 is LBMP subzone number 6. |  |  | Zone 167 is LBMP subzone number 23.
Zone 151 is LBMP subzone number 7. |  |  | Zone 168 is LBMP subzone number 24.
Zone 152 is LBMP subzone number 8. |  |  | Zone 169 is LBMP subzone number 25.
Zone 153 is LBMP subzone number 9. |  |  | Zone 170 is LBMP subzone number 26.
Zone 154 is LBMP subzone number 10. |  |  | Zone 171 is LBMP subzone number 27.
Zone 155 is LBMP subzone number 11. |  |  | Zone 172 is LBMP subzone number 28.
Zone 156 is LBMP subzone number 12. |  |  | Zone 173 is LBMP subzone number 29.
Zone 157 is LBMP subzone number 13. |  |  | Zone 174 is LBMP subzone number 30.
Zone 158 is LBMP subzone number 14. |  |  | Zone 175 is LBMP subzone number 31.
Zone 159 is LBMP subzone number 15. |  |  | Zone 176 is LBMP subzone number 32.
Zone 160 is LBMP subzone number 16. |  |  | Zone 177 is LBMP subzone number 33.
Zone 161 is LBMP subzone number 17. |  |  | Zone 178 is LBMP subzone number 34.
Zone Name |  | LBMP subzone name (up to 12 characters).
Zone 145 is "NGRD WES". |  |  | Zone 162 is "NYPA E".
Zone 146 is "NGRD CEN". |  |  | Zone 163 is "NYSEG NO".
Zone 147 is "NGRD MVN". |  |  | Zone 164 is "NYPA F".
Zone 148 is "NGRD EAS". |  |  | Zone 165 is "NYSEG ME".
Zone 149 is "NYSEG WE". |  |  | Zone 166 is "NYPA H".
Zone 150 is "NYSEG CE". |  |  | Zone 167 is "CON ED N".
Zone 151 is "NYSEG EA". |  |  | Zone 168 is "NYPA I".
Zone 152 is "NYSEG HU". |  |  | Zone 169 is "CON ED C".
Zone 153 is "RG&E". |  |  | Zone 170 is "NYPA J".
Zone 154 is "CENT HUD". |  |  | Zone 171 is "NYPA K".
Zone 155 is "O&R". |  |  | Zone 172 is "NYPA G".
Zone 156 is "LIPA". |  |  | Zone 173 is "NGRD GNS".
Zone 157 is "NYPA WES". |  |  | Zone 174 is "NYSEG BR".
Zone 158 is "NYPA NOR". |  |  | Zone 175 is "NGRD NTH".
Zone 159 is "CON ED". |  |  | Zone 176 is "CE UPNY".
Zone 160 is "NYPA B". |  |  | Zone 177 is "CENT H C".
Zone 161 is "NYPA C". |  |  | Zone 178 is "CRT".

## Bus
Bus Data
Bus Number | Bus Name |  | Bus kV | Bus Type | Area Number | Zone Number | Owner Number
In-Service Date | Retired Date
where:
Bus Number |  | Number 125000 through 149999 & 700000 through 701999
Bus numbers 125000 through 126148 assign to Central Hudson TO.
Bus numbers 126149 through 126249 assign to Central Hudson MPs.
Bus numbers 126250 through 128248 assign to ConEd TO.
Bus numbers 128249 through 128749 assign to ConEd MPs.
Bus numbers 128750 through 130604 assign to LIPA TO.
Bus numbers 130605 through 130749 assign to LIPA MPs.
Bus numbers 130750 through 134749 assign to NYSEG TO.
Bus numbers 134750 through 135249 assign to NYSEG MPs.
Bus numbers 135250 through 145999 assign to NGRID TO.
Bus numbers 146000 through 146749 assign to NGRID MPs.
Bus numbers 146750 through 147649 assign to O&R TO.
Bus numbers 147650 through 147749 assign to O&R MPs.
Bus numbers 147750 through 148698 assign to NYPA TO.
Bus numbers 148699 through 148999 assign to NYPA MPs.
Bus numbers 149000 through 149898 assign to RGE TO.
Bus numbers 149899 through 149999 assign to RGE MPs.
Bus numbers 701400 through 701449 assign to LSPNY TO.
Bus numbers 701450 through 701599 assign to LSPNY MPs.
Bus numbers 701600 through 701649 assign to NEXTERA TO.
Bus numbers 701650 through 701799 assign to NEXTERA MPs.
Bus numbers 701800 through 701849 assign to TRANSCO TO.
Bus numbers 701850 through 701999 assign to TRANSCO MPs.
Bus Name |  | Name (up to 12 characters) and should be unique.
Bus kV |  | Bus base voltage in kV.
Bus Type |  | Integer (1 through 4).
1 is for a load or passive bus.
2 is for a generator bus.
3 is for a swing bus.
4 is for an isolated (disconnected) bus.
Area Number |  | Integer (1 through 11).
Zone Number |  | Integer (145 through 178).
Owner Number |  | Integer (141 through 155).
In-service Date |  | Enter in-service date (mm/dd/yyyy).
Retired Date |  | Enter retired date (mm/dd/yyyy).
Note - Some MPs' equipment that are in-service or completed the Class Year Study prior to 2010
may have assigned bus numbers out of range.

## Load
Load Data
Bus Number | Load Id |  | Status | Area Number | Zone Number | Owner Number | Conforming
Season | Year |  | In-Service Date | Retired Date
| Active Constant MVA (MW) |  | Reactive Constant MVA (MVAr) | Active Constant Current (MW) | Reactive Constant Current (MVAr) | Active Constant Admittance (MW) | Reactive Constant Admittance (MVAr
Coincident
Independent
Off-peak
Nominal
where:
Bus Number |  | Number 125000 through 149999 & 700000 through 701999
Load Id |  | Identifier (up to 2 characters).
"PL" usually defines as auxiliary generating plant loads.
"99" usually defines as equivalent loads.
Status |  | Load status: 1 for in-service and 0 for out-of-service.
Area Number |  | Integer (1 through 11)
Zone Number |  | Integer (145 through 178).
Owner Number |  | Integer (141 through 155).
Conforming |  | Scalable: 1 for scalable (conforming) and 0 for non-scalable (non-conforming).
Auxiliary generating plant and industrial loads are usually non-conforming loads.
Season |  | Winter (W) or Summer (S).
Year |  | Year (4-digits) of the forecast load.
In-service Date |  | Enter in-service date (mm/dd/yyyy).
Retired Date |  | Enter retired date (mm/dd/yyyy).
Coincident |  | NYISO peak
Independent |  | Company peak or non-coincident peak
Off-peak |  | Minimum load expected on the day of the system peak.
Generally 40-45% of the season peak
Nominal |  | Typical load level expected during Spring or Fall.
Generally 70-75% of the season peak

## Station Service Auxiliary Load
Station Service Auxiliary Load
| Bus Number |  | Load Id | Area Number | Zone Number | Conforming | Season
Normal
Contingency
Sustained Outage
| Active Constant MVA (MW) |  | Reactive Constant MVA (MVAr) | Active Constant Current (MW) | Reactive Constant Current (MVAr) | Active Constant Admittance (MW) | Reactive Constant Admittance (MVAr
Normal
Contingency
Sustained Outage
where:
Bus Number |  | Number 125000 through 149999 & 700000 through 701999 (see bus data for more details). This is bus that feeds the station service auxiliary load.
Load Id |  | Identifier (up to 2 characters).
"PLN" plant load under normal condition
"PLC" plant load under contingency condition
"PLS" plant load under sustained outage condition
Area Number |  | Integer (1 through 11)
Zone Number |  | Integer (145 through 178).
Conforming |  | Scalable: 1 for scalable (conforming) and 0 for non-scalable (non-conforming).
Auxiliary generating plant and industrial loads are usually non-conforming loads.
Season |  | Winter (W) or Summer (S).
Normal |  | Expected load when the plant is in-service
Contingency |  | Expected load when the plant is tripped off-line due to an event
Sustained Outage |  | Expected load when the plant is under a sustained outage

## Fixed_Shunt
Manually Controlled Shunt Station (Fixed Shunt) Data
Bus Number | Bank Number |  | Status | GL (MW) | Type | Bank Size (MVAr) | In-Service Date | Retired Date
where:
Bus Number |  | Number 125000 through 149999 & 700000 through 701999 (see bus data for more details).
Bank Number |  | Id (up to 2 characters).
Status |  | Integer (0 through 3).
0 is for out of service.
1 is for in-service all seasons.
2 is for in-service in summer.
3 is for in-service in winter.
GL |  | Active component of shunt admittance to ground (MW)
Type |  | Shunt reactor (REAC) or shunt capacitor (CAP).
Bank Size |  | Entered in MVAr. Reactive component of shunt admittance to ground.
In-service Date |  | Enter in-service date (mm/dd/yyyy).
Retired Date |  | Enter retired date (mm/dd/yyyy).

## SW_Shunt
Switchable Shunt Data
Bus Number | Control Mode |  | Adjusted Method | Status |  | Control Bus | In-Service Date | Retired Date
Summer | Coincident |  | Independent | Off-peak |  | Nominal
Ctrl High
Ctrl Low
Winter | Coincident |  | Independent | Off-peak |  | Nominal
Ctrl High
Ctrl Low
N Bank | Bank Size |  | where:
|  |  | Bus Number |  | Number 125000 through 149999 & 700000 through 701999
(see bus data for more details).
|  |  | Control Mode |  | Enter integer (0 through 6)
0 is locked.
1 is discrete adjustment controlling voltage locally or at control bus.
2 is for continuous adjustment controlling voltage locally or at control bus.
3 is discrete adjustment controlling reactive power output of the plant.
4 is discrete adjustment controlling reactive power output of the VSC.
5 is discrete adjustment controlling admittance setting of the switched shunt.
6 is discrete adjustment controlling reactive power output of the FACTS.
Adjusted Method |  | Integer (0 through 1).
0 is for steps and blocks are switched on input order, and off in reverse
input order.
1 is for steps and blocks are switched on and off such that the next highest
(or lowest, as approriate) total admittance is achieved.
Status |  | Integer (0 through 3).
0 is for out of service.
1 is for in-service all seasons.
2 is for in-service in summer.
3 is for in-service in winter.
Control Bus |  | Bus number of the bus where voltage or connected equipment reactive
power is controlled by this switched shunt.
In-service Date |  | Enter in-service date (mm/dd/yyyy).
Retired Date |  | Enter retired date (mm/dd/yyyy).
Season |  | Winter (W) or Summer (S)
Ctrl High |  | Controlled voltage or reactive power range upper limit.
Ctrl Low |  | Controlled voltage or reactive power range lower limit.
N Bank |  | Number of steps for bank i. There are 8 banks.
Enter interger 0 to 9 for each bank.
Bank Size |  | Increment bank size for bank i. Enter in MVAr.
Positive is for shunt capacitor. Negative is for shunt reactor.

## Gen
Generator Data
Bus Number | LF Unit Id |  | Control Bus | Mbase | Zr | Zx
Control Voltage | Coincident |  | Independent | Off-peak | Nominal | In-Service Date
Summer
Winter
Machine Capability | Pmax |  | Pmin | Qmax | Qmin | Retired Date
Summer
Winter
Status | Owner Name |  | PTID | Plant Unit Name | Plant Unit Id | Plant Unit Type
where:
Bus Number |  | Number 125000 through 149999 & 700000 through 701999 (see bus data for more details).
LF Unit Id |  | Machine id defined in powerflow (up to 2 characters).
Control bus |  | Bus number of the bus where voltage is controlled by this machine.
Mbase |  | Machine base in MVA.
Zr, Zx |  | Un-saturated subtransient complex machine impedance in pu on
machine Mbase.
Control Voltage |  | Voltage setpoint for controlling voltage locally or at a remote bus.
Pmax |  | Enter seasonal DMNC MW value if auxiliary plant load is not model.
Otherwise, enter machine seasonal maximum MW value.
Pmin |  | Enter seasonal minimum MW value.
Qmax |  | Enter seasonal maximum generator reactive power output (MVAr).
Qmin |  | Enter seasonal minimum generator reactive power output (MVAr).
In-service Date |  | Enter in-service date (mm/dd/yyyy).
Retired Date |  | Enter retired date (mm/dd/yyyy).
Status |  | existing (E), under-construction (U), planned (P), or study (S).
Planned - projects accepted cost allocations.
Study - projects haven't accepted cost allocations.
Owner Name |  | Generator Owner Name
PTID |  | Point Identifier.
Plant Unit Name |  | Generating Plant Name.
Plant Unit Id |  | Unit id of the generating plant.
Plant Unit Type |  | Unit type.
CC-Combined Cycle
CG-Cogeneration
CT-Combustion Turbine Portion (CC)
CW-Waste Heat Only (CC)
ES-Energy Storage
FC-Fuel Cell
GT-Combustion Turbine
HY-Conventional Hydro
IC-Internal Combustion
IG-Integrated Coal Gasification (CC)
JE-Jet Engine
NB-Steam (BWR Nuclear)
NP-Steam (PWR Nuclear)
PS-Pumped Storage Hydro
PV-Photovoltaic
ST-Steam Turbine (Fossil)
WT-Wind Turbine

## GCap
Generator Capability Data
Bus Number | LF Unit Id |  | PSI HG
| MW |  | Max MVAr | Min Mvar
Point 1
Point 2
Point 3
Point 4
Point 5
Point 6
Point 7
Point 8
Point 9
Point 10
where:
Bus Number |  | Number 125000 through 149999 & 700000 through 701999 (see bus data for more details).
LF Unit Id |  | Machine id defined in powerflow (up to 2 characters).
PSI HG |  | The HG pressure at which this data is valid
MW |  | MW output at Point i.
Max MVAr |  | Max MVAr output at Point i.
Min MVAr |  | Min MVAr output at Point i.

## AC_Line
AC Transmission Line Data
From Bus | To Bus |  | Ckt Id | Line Status | Metered Bus | In-Service Date | Retired Date
R | X |  | B | GI | BI | GJ | BJ
Ratings (MVA) | Normal |  | LTE | STE | Assumed PF | Line Base kV | PTID
Summer
Winter
| Owner#1 |  | Owner#2 | Owner#3 | Owner#4 | Construction
Owner | [5 empty] | Type | Status
Fraction
| Length (Miles) |  | Size | Type
Conductor
where:
From Bus |  | Branch "from" bus number
To Bus |  | Branch "to" bus number
Ckt Id |  | Identifier (up to 2 characters).
"99" usually defines as an equivalent circuit.
Line Status |  | Integer (0 through 3).
0 is for out of service.
1 is for in-service all seasons.
2 is for in-service in summer.
3 is for in-service in winter.
Metered Bus |  | Integer
<= 1 for meter located at the from bus
>=2 for meter located at the to bus
In-service Date |  | Enter in-service date (mm/dd/yyyy).
Retired Date |  | Enter retired date (mm/dd/yyyy).
R, X |  | Line impedance in pu on 100 MVA system MBASE.
B |  | Total line charging susceptance in pu on 100 MVA system MBASE.
GI, BI |  | Complex admittance of the line shunt at the from bus of the line.
Enter in pu. BI positive is for a line connected capacitor.
BI negative is for a line connected reactor.
GJ, BJ |  | Complex admittance of the line shunt at the to bus of the line.
Enter in pu. BJ positive is for a line connected capacitor.
BJ negative is for a line connected reactor.
Ratings |  | Enter seasonal Normal, LTE and STE ratings in MVA.
Normal is for capacity that may be carried through consecutive twenty-four
hour load cycles without exceeding agreed upon conductor or hottest spot
equipment temperatures for this mode of operation.
LTE is for capacity that may be carried through infrequent non-consecutive of
approximately four hour periods.
STE is for capacity that may be carried during very infrequent contingencies of
fifteen minutes or less duration.
Assumed PF |  | Assumed line power factor that could be used to convert MVA ratings to
MW ratings.
Line Base kV |  | Line voltage base kV.
PTID |  | Point Identifier.
Owner |  | Enter owner number. Up to four owner can be entered.
Fraction |  | Enter the fraction that each owner owns.
Construction |  | Type: overhead (O), underground (U), or mixed (M).
Status: existing (E), firm (F), non-firm (NF), under-construction (U), planned (P)
or study (S). Planned - projects accepted cost allocations.
Study - projects haven't accepted cost allocations.
Conductor |  | Length - enter the line length in mile.
Size - enter in thousands of cmils (MCM) or AWG.
Type - CU, AL, ACSR, ACSS, ACAR, AAC, AAAC.

## Xfmr_2W
Two-Winding Transformer Data
Tap Bus | Z Bus |  | Bank Id | MAG1 | MAG2 | Metered Bus | Xfmr Name | Status
| Owner#1 |  | Owner#2 | Owner#3 | Owner#4 | In-Service Date | Retired Date | PTID
Owner
Fraction
R | X |  | Xfmr Type | WINDV | ANG | Ctrl Bus | Rmax | Rmin
Vmax | Vmin |  | Number of Tap | Table | CR | CX | VECGRP
Ratings (MVA) | Normal |  | LTE | STE | PF
Summer
Winter
where:
Tap Bus |  | Tap side bus is where tap ratio or phase shift angle may be adjusted.
Z Bus |  | Impedance side bus. If this is a dummy bus, its kV base should be 999 kV.
Bank Id |  | Transformer bank identifier (up to 2 characters).
MAG1, MAG2 |  | Transformer magnetizing admittance in pu on 100 system MVA base and tap bus
voltage base.
Metered Bus |  | Meter location: 1 for tap bus and 2 for Z bus.
Xfmr Name |  | Transformer name (up to 12 characters).
Status |  | Integer (0 through 3).
0 is for out of service.
1 is for in-service all seasons.
2 is for in-service in summer.
3 is for in-service in winter.
Owner |  | Enter owner number. Up to four owner can be entered.
Fraction |  | Enter the fraction that each owner owns.
In-service Date |  | Enter in-service date (mm/dd/yyyy).
Retired Date |  | Enter retired date (mm/dd/yyyy).
PTID |  | Point Identifier.
R, X |  | Transformer impedance in pu on 100 MVA system MBASE.
Xfmr Type |  | 0 is for no control (fixed tap and/or fixed phase angle).
1 is for voltage control (variable tap and fixed phase angle).
2 is for reactive power flow control (variable tap and fixed phase angle).
3 is for active power flow control (variable phase angle and fixed tap).
4 is for control of a dc line quantity.
WINDV |  | Off-nomimal tap setting of fixed tap transformers or initial tap setting of variable tap
transformers.
ANG |  | Fixed angle value for fixed phase shifters or initial angle value for variable phase shifters.
Ctrl Bus |  | Enter bus number of the bus for which its voltage is to be controlled by this transformer.
Rmax, Rmin |  | Upper and lower off-nominal turns ratio limits in pu or phase shift angle limits in degrees.
Vmax, Vmin |  | Upper and lower voltage limits at the controlled bus in pu, MVAr flow limits through this
transformer, or MW flow limits through this transformer.
Number of Tap |  | The number of tap positions available.
Table |  | The number of a transformer impedance correction table.
CR, CX |  | The load drop compensation impedance for voltage controlling transformers in pu.
VECGRP |  | Transformer vector group based on transformer winding connections and phase angles
Ratings |  | Enter seasonal Normal, LTE and STE ratings in MVA.
Normal is for capacity that may be carried through consecutive twenty-four
hour load cycles without exceeding agreed upon conductor or hottest spot
equipment temperatures for this mode of operation.
LTE is for capacity that may be carried through infrequent non-consecutive of
approximately four hour periods.
STE is for capacity that may be carried during very infrequent contingencies of
fifteen minutes or less duration.
Assumed PF |  | Assumed line power factor that could be used to convert MVA ratings to
MW ratings.
Note |  | For autotransformers, the voltage of Bus I must be greater than the voltage of Bus J

## Xfmr_3W
Three-Winding Transformer Data
For the steady state and dynamic model, three-winding transformers with an actively loaded tertiary winding shall be modeled using a three-winding model. For three-winding transformers with an unloaded tertiary winding, it is preferable for the transformer to be modeled using an equivalent two-winding model. For the short circuit model, three-winding transformers shall be modeled using a three-winding model.
W1 | W2 |  | W3 | Ckt Id | MAG1 | MAG2 | Metered Bus | Xfmr Name | PTID
| Owner#1 |  | Owner#2 | Owner#3 | Owner#4 |  | Z1-2 | Z2-3 | Z3-1
Owner | [5 empty] | R
Fraction | [5 empty] | X
In-Service Date | Retired Date
Winding 1 Data Portion
Xfmr Type | WINDV |  | Ctrl Bus | Rmax | Rmin | Vmax | Vmin | Number of Tap | Table
CR | CX |  | Status |  | Ratings (MVA) | Normal | LTE | STE | PF
Summer
Winter
Winding 2 Data Portion
Xfmr Type | WINDV |  | Ctrl Bus | Rmax | Rmin | Vmax | Vmin | Number of Tap | Table
CR | CX |  | Status | VECGRP | Ratings (MVA) | Normal | LTE | STE | PF
Summer
Winter
Winding 3 Data Portion
Xfmr Type | WINDV |  | Ctrl Bus | Rmax | Rmin | Vmax | Vmin | Number of Tap | Table
CR | CX |  | Status |  | Ratings (MVA) | Normal | LTE | STE | PF
Summer
Winter
where:
W1, W2, W3 |  | Bus number of winding 1, winding 2, and winding 3.
Bank Id |  | Transformer bank identifier (up to 2 characters).
MAG1, MAG2 |  | Transformer magnetizing admittance in pu on 100 system MVA base and winding 1 bus
voltage base.
Metered Bus |  | Meter location: 1 for winding 1, 2 for winding 2, and 3 for wing 3 bus.
Xfmr Name |  | Transformer name (up to 12 characters).
PTID |  | Point Identifier.
Owner |  | Enter owner number. Up to four owner can be entered.
Fraction |  | Enter the fraction that each owner owns.
In-service Date |  | Enter in-service date (mm/dd/yyyy).
Retired Date |  | Enter retired date (mm/dd/yyyy).
Z1-2 (R, X) |  | Transformer impedance between W1 and W2 in pu on 100 MVA system MBASE.
Z2-3 (R, X) |  | Transformer impedance between W2 and W3 in pu on 100 MVA system MBASE.
Z3-1 (R, X) |  | Transformer impedance between W3 and W1 in pu on 100 MVA system MBASE.
Xfmr Type |  | 0 is for no control (fixed tap).
1 is for voltage control (variable tap).
WINDV |  | Off-nomimal tap setting of fixed tap transformers or initial tap setting of variable tap
transformers.
Ctrl Bus |  | Enter bus number of the bus for which its voltage is to be controlled by this transformer.
Rmax, Rmin |  | Upper and lower off-nominal turns ratio limits in pu or phase shift angle limits in degrees.
Vmax, Vmin |  | Upper and lower voltage limits at the controlled bus in pu, MVAr flow limits through this
transformer, or MW flow limits through this transformer.
Number of Tap |  | The number of tap positions available.
Table |  | The number of a transformer impedance correction table.
CR, CX |  | The load drop compensation impedance for voltage controlling transformers in pu.
Status |  | Integer (0 through 3).
0 is for out of service.
1 is for in-service all seasons.
2 is for in-service in summer.
3 is for in-service in winter.
VECGRP |  | Transformer vector group based on transformer winding connections and phase angles
Ratings |  | Enter seasonal Normal, LTE and STE ratings in MVA.
Normal is for capacity that may be carried through consecutive twenty-four hour load cycles without
exceeding agreed upon conductor or hottest spot equipment temperatures for this mode of operation.
LTE is for capacity that may be carried through infrequent non-consecutive of approximately four
hour periods. STE is for capacity that may be carried during very infrequent contingencies of
fifteen minutes or less duration.
Assumed PF |  | Assumed line power factor that could be used to convert MVA ratings to
MW ratings.

## Impedance Table
Transformer Impedance Correction Tables
Table Number
| Ratio/Angle | Factor |  | Ratio/Angle | Factor
Point 1 |  |  | Point 7
Point 2 |  |  | Point 8
Point 3 |  |  | Point 9
Point 4 |  |  | Point 10
Point 5 |  |  | Point 11
Point 6
where:
Table Number |  | Impedance correction table number (1 to 96)
Please contact NYISO to obtain the designated number.
Ratio/Angle |  | Either off-nominal turns ratio in pu or phase shift angle in degrees.
Factor |  | Scaling factor by which transformer nominal impedance is to be
multiplied to obtain the actual transformer impedance for the
corresponding point i.

## HVdc
HVdc Transmission Line Data
Name | Ctrl Mode |  | DC Line R | Desired P/I | Schd V | VCMOD | Rcomp
Delt I | Metered Bus |  | DCVMin | CC Limit | CC Acc | In-Service Date | Retired Date
| Rectifier |  | Inverter |  | Rectifier | Inverter
IP |  |  |  | TMX
NB |  |  |  | TMN
ANMX |  |  |  | STP
ANMN |  |  |  | IC
RC |  |  |  | IF
XC |  |  |  | IT
EBAS |  |  |  | ID
TR |  |  |  | XCAP
TAP
where:
Name |  | Unique name (up to 12 characters)
Ctrl Mode |  | Control mode: 0 for blocked, 1 for power, and 2 for current.
DC Line R |  | The dc line resistance in ohms.
Desired P/I |  | Desired dc power in MW or current in A.
Schd V |  | Scheduled compounded dc voltage in kV.
VCMOD |  | Mode switch dc voltage in kV.
Rcomp |  | Compounding resistance in ohms.
Delt I |  | Margin enter in pu of desired dc power or currrent.
Metered Bus |  | Meter location: R for rectifier or I for inverter.
DCVMin |  | Minimum compounded dc voltage in kV.
CC Limit |  | Iteration limit for capacitor commutated two-terminal dc line Newton
solution procedure.
CC Acc |  | Acceleration factor for capacitor commutated two-terminal dc line Newton
solution procedure.
In-service Date |  | Enter in-service date (mm/dd/yyyy).
Retired Date |  | Enter retired date (mm/dd/yyyy).
IP |  | Bus number.
NB |  | Number of bridges in series.
ANMX |  | Maximum steady state firing angle in degrees.
ANMN |  | Minimum steady state firing angle in degrees.
RC |  | Commutating transformer resistance per bridge in ohms.
XC |  | Commutating transformer reactance per bridge in ohms.
EBAS |  | Primary base ac voltage in kV.
TR |  | Transformer ratio.
TAP |  | Tap setting.
TMX |  | Maxmimum tap setting.
TMN |  | Mininum tap setting.
STP |  | Tap step.
IC |  | Firing angle measuring bus number.
IF |  | Winding 1 side from bus number.
IT |  | Winding 2 side to bus number.
ID |  | Circuit identifier.
XCAP |  | Commutating capacitor reactance magnitude per bridge in ohms.

## VSC
Voltage Source Converter (VSC) DC Transmission Line Data
Name | Status |  | DC Line R | In-Service Date | Retired Date
| Owner#1 |  | Owner#2 | Owner#3 | Owner#4
Owner
Fraction
| Convert 1 |  | Convert 2 |  | Convert 1 | Convert 2
IBUS |  |  |  | SMAX
TYPE |  |  |  | IMAX
MODE |  |  |  | PWF
DCSET |  |  |  | MAXQ
ACSET |  |  |  | MINQ
ALOSS |  |  |  | REMOT
BLOSS |  |  |  | RMPCT
MINLOSS
where:
Name |  | Unique name (up to 12 characters)
Status |  | Integer (0 through 3).
0 is for out of service.
1 is for in-service all seasons.
2 is for in-service in summer.
3 is for in-service in winter.
DC Line R |  | The dc line resistance in ohms.
In-service Date |  | Enter in-service date (mm/dd/yyyy).
Retired Date |  | Enter retired date (mm/dd/yyyy).
Owner |  | Enter owner number. Up to four owner can be entered.
Fraction |  | Enter the fraction that each owner owns.
IBUS |  | Convert bus number
TYPE |  | Converter dc control type: 0 for out of service, 1 for dc voltage control, and
2 for MW control.
MOD |  | Converter ac control mode: 1 for ac voltage control and 2 for fixed ac power
factor.
DCSET |  | Converter dc setpoint in kV or MW.
ACSET |  | Converter ac setpoint in pu.
ALOSS, BLOSS |  | Coefficients of the linear equation used to calculate converter losses.
ALOSS is in kW. BLOSS is in kW/amp.
MINLOSS |  | Minimum converter losses in kW.
SMAX |  | Converter MVA rating.
IMAX |  | Converter ac current rating in amps.
PWF |  | Power weighting factor fraction.
MAXQ, MINQ |  | Reactive power upper and lower limits in MVAr.
REMOT |  | Bus number of the remote voltage bus to be controlled.
RMPCT |  | Percent of the total MVAr required to hold the voltage at the controlled bus
by bus IBUS that is to be contributed by this VSC.

## FACTS
Flexible AC Transmission System (FACTS) Device Data
Name | I |  | J | Mode | PDES | QDES | VSET
SHMX | TRMX |  | VTMN | VTMX | VSMX | IMX | LINX
RMPCT | OWNER |  | SET1 | SET2 | VSREF | REMOT | MNAME
In-Service Date | Retired Date
where:
Name |  | Unique name (up to 12 characters)
I |  | Sending end bus number.
J |  | Terminal end bus number
Mode |  | For a STATCON, 0 is for out of service and 1 is for shunt link operating.
For a FACTS device with a series element, 0 is for out of service.
1 is for series and shunt links operating.
2 is for series link bypassed and shunt link operating as a STATCON.
3 is for series and shunt links operating with series link at constant series
impedance.
4 is for series and shunt links operating with series link at constant series
voltage.
5 is for master device of an IPFC with P and Q setpoints specified.
6 is for slave device of an IPFC with P and Q setpoints specified.
7 is for master device of an IPFC with constant series voltage setpoints specified.
8 is for slave device of an IPFC with constant series voltage setpoints specified.
PDES |  | Desired active power flow arriving at the terminal end bus in MW.
QDES |  | Desired reactive power flow arriving at the terminal end bus in MVAr.
VSET |  | Voltage setpoint at the sending end bus in pu.
SHMX |  | Maximum shunt current at the sending end bus in MVA at unity voltage.
TRMX |  | Maximum bridge active power transfer in MW.
VTMN |  | Minimum voltage at the terminal end bus in pu.
VTMX |  | Maximum voltage at the terminal end bus in pu.
VSMX |  | Maximum series voltage in pu.
IMX |  | Maximum series current in MVA at unity voltage.
LINX |  | Reactance of the dummy series element used during power flow solution in pu.
RMPCT |  | Percent of the total MVAr required to hold the voltage at the bus controlled by
the shunt element of this FACTS device that are to be contributed by this
shunt element.
Owner |  | Owner number.
SET1, SET2 |  | If MODE is 3, resistance and reactance of the constant impedance in pu.
If MODE is 4, voltage (pu) and angle (degrees) of the constant series voltage.
If MODE is 7 or 8, the real and imaginary components (pu) of the constant
series voltage.
VSREF |  | Series voltage reference code: 0 for sending end voltage and 1 for series current.
REMOT |  | Bus number of the remote voltage bus to be controlled.
NNAME |  | Name of the master FACTS device when this device is a slave.
In-service Date |  | Enter retired date (mm/dd/yyyy).
Retired Date |  | Enter retired date (mm/dd/yyyy).